## Claude Log
Turn # | Date | User Request | Action Taken | Details | Outcome
1 | 2026-08-20 | Confirm whether ontology definitions for the 5 AHUs (SSC_AHUB0001-0005) match in count, and identify discrepancies; put results on a separate sheet. | Created 'AHU_Comparison' sheet with per-unit triple counts, a discrepancy table, and a full 135-relation matrix. | Normalised each triple in SSC_Ontology_Ver0.5!A128:D773 by replacing the AHU id with {N}, then counted each pattern per unit with COUNTIFS+SUBSTITUTE formulas (live-linked to source). Status flags via MIN/MAX. Conditional formatting highlights non-OK rows. | Counts do NOT match: 129/130/128/132/127 rows. 12 of 135 relation patterns differ - 3 location rows (expected), missing SAP_Setpoint on 0003/0005, missing RF_AutoMan_Status on 0004, duplicated SA_P-Static ref on 0002/0003/0004, extra RA_P-Static_01/_02 on 0004.
2 | 2026-08-20 | Disregard the rec:locatedIn discrepancies. | Removed the 3 location rows from the discrepancy table and flagged them as excluded in the full matrix. | Deleted rows 20:22 (sections below shifted up: matrix header now row 22, data 23:157). Status formula now returns 'Excluded - location varies by unit' when column B = rec:locatedIn; conditional highlight skips excluded rows. Header note in A2/A9 updated. | Discrepancy count now 9 real issues across 135 relations (123 OK, 8 not-on-all-units, 1 duplicated, 3 excluded locations).
3 | 2026-08-20 | Run the same consistency comparison for the newly selected range (A815:E1346) on its own sheet. | Created 'CCU_Comparison' sheet comparing the 14 CCU/CRAC units in SSC_Ontology_Ver0.5!A815:E1346. | Unit ids are non-sequential (CCU3F0301, CCUB0001A/B, ... CCUB0008), so ids were detected by regex rather than assumed. Same method as AHU sheet: normalise unit id to {U}, count each pattern per unit with COUNTIFS+SUBSTITUTE. Also compared the two type columns (B, E) which the AHU range did not have. | Counts MATCH: all 14 units have 38 rows; 37 of 40 relation patterns present exactly once on every unit; 3 rec:locatedIn patterns excluded per user. Type columns consistent. No missing or duplicated rows.
4 | 2026-08-20 | For the CCUs not located in B1_023_Q_TEL or B1_017_MDF-2, do they have a unique rec:locatedIn triple? | Audited rec:locatedIn per CCU and added a 'Location breakdown' table to CCU_Comparison (rows 59-76). | Per-unit triple count via COUNTIFS; room resolved with TEXTJOIN+IF array formula against SSC_Ontology_Ver0.5!A815:D1346; room occupancy via COUNTIFS on predicate+object. Kept as live formulas. | Answer: yes, each of the 14 CCUs has exactly one rec:locatedIn triple - none missing or duplicated. But the rooms are shared, not unique: the 6 units outside Q_TEL/MDF-2 all sit in B1_038_SER-2.
5 | 2026-08-20 | Run the same consistency exercise for the chilled water pumps in SSC_Ontology_Ver0.5!A1347:E1422. | Created 'CHWP_Comparison' sheet comparing the 4 chilled water booster pumps (SSC_CHW_CHWP01-04). | Same method: normalise pump id to {P}, count each of the 19 relation patterns per pump with COUNTIFS+SUBSTITUTE against A1347:D1422; compared subject/object type columns; status flag via MIN/MAX. | Fully consistent: 19 rows per pump, 19/19 patterns present exactly once on every pump, types identical, all 4 in the same room (B1_014_VENT_PLANT) so no location variance either. Flagged one non-error observation: pumps have Speed_Command/Speed_Fbk but no run status or auto-manual point on any of the 4.
6 | 2026-08-20 | Run the same consistency exercise for the heat exchangers in SSC_Ontology_Ver0.5!A1423:E1572. | Created 'HE_Comparison' sheet comparing the 5 chilled water heat exchangers (SSC_CHW_HE01-HE05). | Same method: normalise HE id to {H}, count all 32 relation patterns per unit with COUNTIFS+SUBSTITUTE against A1423:D1572; compared subject/object type columns. Sheet has count summary (rows 5-7), findings (10-14), discrepancy table (17-27) and full matrix (29-61). | Counts DO NOT match: HE01-04 = 32 rows, HE05 = 22 (10 short). All 10 missing rows are on HE05's Supply_Valve (Auto_Command, Manual_Auto_Status, Close_Command, Open_Command, Status + their 5 external references); only Temperature_Sensor remains. Everything else identical, all 5 in same room. Flagged two uniform modelling issues: Open/Close_Command para types look swapped, and Return_Valve has both _Open_Close_Status and _Status with the same class.
7 | 2026-08-20 | Challenged whether the whole worksheet was checked for heat exchanger rows, not just the selected range. | Scanned the entire used range of SSC_Ontology_Ver0.5 (5,120 rows x 27 cols) for heat exchanger references. | Matched on HE0x, HEX, HX, PHE, 'Plate Heat', 'Exchanger' and 'heat exchanger' across all columns of every row. 150 hits found, all within rows 1423-1572. The 25 'Exchanger' hits are the brick:Heat_Exchanger class cells (5 units x 5 rows) inside that same block. | Confirmed: no heat exchanger data exists outside A1423:E1572, so HE_Comparison covers the complete set. Also inspected the user's newly inserted rows 1671-1680 - these are DX unit rec:feeds triples, unrelated to HEs.
8 | 2026-08-20 | Run the same consistency exercise for the DX units in SSC_Ontology_Ver0.5!A1573:E1680. | Created 'DX_Comparison' sheet comparing the 10 DX units (SSC_DXB0001-DXB0010), after first sweeping the whole sheet for stray DX rows. | Whole-sheet scan found one DX row outside the range - row 4988, 'para:DXUnit owl:Class rdfs:subClassOf brick:HVAC_Equipment' - which is a class definition, not instance data, so it was excluded. Same method as prior sheets: normalise id to {D}, COUNTIFS+SUBSTITUTE per unit over A1573:D1680. Both rec:locatedIn and rec:feeds excluded from the pass/fail flag since both legitimately vary by room. Added a location/feeds breakdown table. | Counts DO NOT match: DXB0001-0006 = 10 rows, DXB0007-0010 = 12. Whole difference is the Humidity_Sensor point + its external reference, present only on the 4 units in FM STORAGE rooms - likely intentional, flagged for confirmation. Matrix: 8 OK, 2 not-on-all-units, 10 excluded. Also flagged that all 10 units have rec:feeds pointing at the same room as rec:locatedIn.
9 | 2026-08-20 | Run the same consistency exercise for the FCUs in SSC_Ontology_Ver0.5!A1681:E2208. | Created 'FCU_Comparison' sheet comparing the 11 FCUs (SSC_FCU0001-FCU0011), after sweeping the whole sheet for stray FCU rows. | Whole-sheet scan found zero FCU rows outside A1681:E2208, so the set is complete. Same method: normalise id to {F}, COUNTIFS+SUBSTITUTE per unit; rec:locatedIn and rec:feeds excluded from the pass/fail flag. Sheet: counts (5-7), findings (10-14), 64-pattern matrix (17-81), location/feeds breakdown (83-95). | Fully consistent: 48 rows on every FCU; 46 structural patterns present exactly once on all 11; 18 excluded location/feeds patterns covering 9 distinct rooms, one locatedIn and one feeds per unit. No type inconsistencies. Flagged again that rec:feeds points at the same room as rec:locatedIn on all 11 units.
10 | 2026-08-20 | Run the same consistency exercise for the selected range A2209:E2238. | Found the range held only one unit, widened scope to all 7 brick:Exhaust_Fan entities (rows 2209-2492) and created 'EF_Comparison'. | Selected range contained only GEFB0001, so a whole-sheet scan identified every entity typed brick:Exhaust_Fan: GEFB0001, KEF0103, KEF0303, TEF0101/0102/0301/0302. Rows 2343-2372 (Levels, MV Generator) fall inside the span and were excluded. Matrix uses Presence and Duplication columns instead of a single status because duplication and absence are separate problems here. Distinct-relation row is a SUMPRODUCT over the matrix. | Counts DO NOT match: GEF + 4 TEFs = 30 rows, KEF0103/KEF0303 = 52. KEFs are duplicated end to end (26 distinct relations x2). Three point sets in use - only 24 of 36 patterns shared by all 7. Type inconsistency: Motor_Running_Status is brick:On_Off_Status on GEF/KEFs but brick:Fan_Status on TEFs. Major flag: all 7 fans are locatedIn and feed the same room, entity:Level7_Office0367 - likely placeholder data.
11 | 2026-08-20 | Run the same exercise for the generator (selected range A2347:E2371). | Created 'GEN_Check' sheet - an internal integrity audit rather than a cross-unit comparison, because only one generator exists. | Whole-sheet scan for GEN/Generator returned 71 hits but nearly all were false positives (GENERAL OFFICE rooms, 'General Fault/Alarm' labels, the B1_012_GENERATOR room definition, the para:Generator class row at 4992). Only one generator instance: SSC_MV_Generator. Since there is no peer, the sheet tests each point for exactly one hasPoint declaration and one external reference, and locates every generator triple with an AGGREGATE-based row finder (SUMPRODUCT version returned #N/A because the source columns contain error cells). | 26 generator triples: 25 in the selected block, 1 detached. All 10 points declared once and referenced once - internally clean. Flagged: rec:locatedIn sits alone at row 5013 instead of inside the block; 'Generator_Generator_Running_Status' name stutter; inconsistent _Reading suffixes; no rec:feeds triple.
12 | 2026-08-20 | Run the same consistency exercise for the VAVs (ranges A2493:E4976 and A5014:E5120). | Created 'VAV_Comparison' covering all 108 VAV units, and found 19 corrupted rows that a row-count check alone would miss. | 108 units x 24 rows is too wide for a per-unit column grid, so the sheet tests each structural relation for an expected count of 108 using COUNTIFS with wildcard entity patterns, plus a 108-row per-unit count table. A first pass normalising on exact object values produced 191 meaningless patterns because rated flowrates/rooms are per-unit literals; re-normalised so unit-specific values collapse to one token, giving 27 real structural patterns. Whole-sheet scan confirmed no VAV rows outside the two selected ranges. | Row counts: 107 units have 24 rows, VAV0063 has 23 (missing its rec:feeds triple). Content check found 19 rows where the object column holds a value instead of an entity: VAV0102 (9 rows), VAV0103 (8), VAV0101 (1) all contain the number 130 in place of point/part names, and VAV0063 row 3931 holds #N/A in its locatedIn object. VAV0102 and VAV0103 still total 24 rows each, so only the content check catches them.
13 | 2026-08-20 | VAV0063 can be disregarded as a red flag. | Downgraded VAV0063 from an issue to an accepted exclusion throughout VAV_Comparison. | Applied to both of its findings (23 rows / no rec:feeds, and #N/A in its locatedIn object) since the instruction referred to the unit. Per-unit status formula now returns 'Excluded - reviewed, accepted' for VAV0063; the rec:feeds structural row now passes at 107; its corrupted-table row is greyed rather than deleted so the detail is preserved; conditional formatting no longer flags it. Summary metrics relabelled and a new 'corrupted object cells outstanding' metric added. | Outstanding VAV issues now: 18 corrupted object cells across VAV0101 (1), VAV0102 (9) and VAV0103 (8) - all holding the number 130 instead of an entity name. Row counts: 107 OK, 1 excluded, 0 flagged.
14 | 2026-08-20 | Highlight the section 4 corrupted rows in the source sheet in yellow. | Filled A:E yellow (#FFFF00) on the 18 outstanding corrupted rows in SSC_Ontology_Ver0.5. | Rows highlighted: 4809 (VAV0101), 4816-4823 and 4832 (VAV0102), 4839-4846 (VAV0103). Limited the fill to columns A:E, the populated data columns. Deliberately skipped row 3931 (VAV0063) because that unit was accepted as not a red flag in the previous turn. | All 18 rows verified as #FFFF00 by reading the fill colour back. Row 3931 left unhighlighted pending confirmation.
15 | 2026-08-20 | Pointed out that ref:hasExternalReference rows are also corrupted (object = 130 instead of <blanknode>), not just the 18 structural rows, and asked for these to be shown in the VAV sheet. | Rescanned every VAV row for non-text objects, expanded section 4 from 19 to 37 rows, added a reference-object check to section 3, and highlighted the 18 additional source rows yellow. | My earlier scan only tested hasPart/hasPoint rows - a scoping error on my part. Full rescan of all 2,591 VAV rows found 253 non-text objects, of which 216 are legitimate (para:ratedReheatCapacity and para:ratedSupplyAirFlowrate carry numeric values by design) and 1 is VAV0063's accepted #N/A. Real corruption = 36 rows: 18 structural + 18 reference. Inserted 18 rows at 68 to grow the table, so section 5 moved from row 70 to 88; dependent formulas adjusted automatically and the B10 metric range was repointed manually to D50:D85. | 36 corrupted rows confirmed: VAV0101 = 10 (1 structural + 9 refs), VAV0102 = 18 (9 + 9), VAV0103 = 8 (structural only, refs intact). All 36 source rows verified yellow. New section 3 check row reports 'CORRUPT - 18 rows' for reference objects.

## SSC_Ontology_Ver0.5
Subject | subjectType | predicate | object | objectType | subject_prop_name | subject_prop_val | object_prop_name | object_prop_val | subject_prop_name | subject_prop_val | object_prop_name | object_prop_val | subject_prop_name | subject_prop_val | object_prop_name | object_prop_val | subject_prop_name | subject_prop_val | object_prop_name | object_prop_val | subject_prop_name | subject_prop_val | object_prop_name | object_prop_val | subject_prop_name | subject_prop_val
entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network | ref:hasExternalReference | <blanknode> | ref:IFCReference | [6 empty] | ref:ifcName | CHWS-MAIN-LOOP
entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network | rec:locatedIn | entity:SSC | rec:Building | [8 empty] | brick:aliasOf | CHWS-MAIN-LOOP
entity:CHW-System | brick:Chilled_Water_System | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | Chilled Water System
entity:Electrical_System | brick:System | brick:isPartOf | entity:QF | rec:Site | rdfs:label_en | Electrical System
entity:HVAC | brick:HVAC_System | brick:isPartOf | entity:QF | rec:Site | rdfs:label_en | HVAC System
entity:SSC | rec:Building | rec:isPartOf | entity:QF | rec:Site | rdfs:label_en | SSC Building | rdfs:label_en | Qatar Foundation
entity:SSC_01_001_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.001 CORRIDOR
entity:SSC_01_002_SHELL_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.002 SHELL SPACE
entity:SSC_01_003_OPEN_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.003 OPEN SPACE
entity:SSC_01_004_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.004 CORRIDOR
entity:SSC_01_005_KITCHEN | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.005 KITCHEN
entity:SSC_01_006_MALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.006 MALE TOILET
entity:SSC_01_007_FEMALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.007 FEMALE TOILET
entity:SSC_01_008_AV_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.008 A / V ROOM
entity:SSC_01_009_AUDITORIUM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.009 AUDITORIUM MEETING ROOM
entity:SSC_01_010_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.01 CORRIDOR
entity:SSC_01_011_AIR_LOCK | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.011 AIR LOCK
entity:SSC_01_012_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.012 STORAGE
entity:SSC_01_013_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.013 CORRIDOR
entity:SSC_01_014_SHELL_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.014 SHELL SPACE
entity:SSC_01_015_SHELL_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.015 SHELL SPACE
entity:SSC_01_016_SHELL_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.016 SHELL SPACE
entity:SSC_01_017_FEMALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.017 FEMALE TOILET
entity:SSC_01_018_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.018 CORRIDOR
entity:SSC_01_019_PRAYER_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.019 PRAYER ROOM
entity:SSC_01_020_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.02 CORRIDOR
entity:SSC_01_021_ABLUTION_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.021 ABLUTION ROOM
entity:SSC_01_022_ABLUTION_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.022 ABLUTION ROOM
entity:SSC_01_023_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.023 CORRIDOR
entity:SSC_01_024_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.024 CORRIDOR
entity:SSC_01_025_MALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.025 MALE TOILET
entity:SSC_01_026_STORAGE_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.026 FURNITURE STORAGE
entity:SSC_01_027_IDF_1 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.027 IDF - 1
entity:SSC_01_028_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.028 CORRIDOR
entity:SSC_01_029_ROOM_NO_42 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.029 SHELL SPACE
entity:SSC_01_029_ROOM_NO_43 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.029 SHELL SPACE
entity:SSC_01_029_ROOM_NO_44 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.029 SHELL SPACE
entity:SSC_01_029_SHELL_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.029 SHELL SPACE
entity:SSC_01_030_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.03 STORAGE
entity:SSC_01_031_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.031 TOILET
entity:SSC_01_032_VESTIBULE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.032 VESTIBULE
entity:SSC_01_033_JANITORS_CLOSET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.033 JANITORS CLOSET
entity:SSC_01_034_AIR_LOCK | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.034 AIR LOCK
entity:SSC_01_035_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.035 CORRIDOR
entity:SSC_01_036_OUTDOOR_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.036 OUTDOOR AREA
entity:SSC_01_037_OUTDOOR_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.037 OUTDOOR AREA
entity:SSC_01_038_STORAGE_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.038 STORAGE AREA
entity:SSC_01_039_IDF_2 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.039 IDF - 2
entity:SSC_01_041_STORAGE_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.041 STORAGE
entity:SSC_01_P-1_P-1 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.P-1 LIFT
entity:SSC_01_P-2_P-2 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.P-2 LIFT
entity:SSC_01_ST-1_STAIR-1 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-1 STAIR-1
entity:SSC_01_ST-2_STAIR-2 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-2 STAIR-2
entity:SSC_01_ST-3_STAIR-3 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-3 STAIR-3
entity:SSC_01_ST-4_STAIR_4 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-4 STAIR-4
entity:SSC_01_ST-5_STAIR-5 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-5 STAIR-5
entity:SSC_01_ST-8_STAIR-8 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-8 STAIR-8
entity:SSC_01_ST-9_STAIR-9 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-9 STAIR-9
entity:SSC_02_001_FOYER | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.001 FOYER
entity:SSC_02_002_LOBBY | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.002 LOBBY
entity:SSC_02_003_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.003 CORRIDOR
entity:SSC_02_004_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.004 CORRIDOR
entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.005 EXECUTIVE CONFERENCE ROOM
entity:SSC_02_006_CONFERENCE_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.006 CONFERENCE ROOM
entity:SSC_02_007_MEZZANINE | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.007 MEZZANINE
entity:SSC_02_008_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.008 TOILET
entity:SSC_02_010_VESTIBULE | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.01 VESTIBULE
entity:SSC_02_P-1_LIFT | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 02.P-1 LIFT
entity:SSC_02_P-2_LIFT | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 02.P-2 LIFT
entity:SSC_02_ST-1_STAIR-1 | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 02.ST-1 STAIR-1
entity:SSC_02_ST-2_STAIR-2 | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 02.ST-2 STAIR-2
entity:SSC_02_ST-8_STAIR-8 | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 02.ST-8 STAIR-8
entity:SSC_03_001_DIRECTORS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.001 DIRECTOR'S OFFICE
entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.002 DIRECTOR'S MEETING ROOM
entity:SSC_03_003_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.003 RESEARCHER'S OFFICE
entity:SSC_03_004_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.004 VISITOR'S CUBICLE
entity:SSC_03_005_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.005 RESEARCHER'S OFFICE
entity:SSC_03_006_MEETING_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.006 MEETING ROOM
entity:SSC_03_007_OPERATIONS_MANAGER | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.007 OPERATIONS MANAGER
entity:SSC_03_008_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.008 VISITOR'S CUBICLE
entity:SSC_03_009_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.009 RESEARCHER'S OFFICE
entity:SSC_03_010_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.01 RESEARCHER'S OFFICE
entity:SSC_03_011_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.011 VISITOR'S CUBICLE
entity:SSC_03_012_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.012 RESEARCHER'S OFFICE
entity:SSC_03_013_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.013 RESEARCHER'S OFFICE
entity:SSC_03_014_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.014 VISITOR'S CUBICLE
entity:SSC_03_015_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.015 RESEARCHER'S OFFICE
entity:SSC_03_016_LOUNGE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.016 LOUNGE
entity:SSC_03_017_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.017 RESEARCHER'S OFFICE
entity:SSC_03_018_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.018 VISITOR'S CUBICLE
entity:SSC_03_019_IT_MANAGERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.019 IT MANAGER'S OFFICE
entity:SSC_03_020_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.02 RESEARCHER'S OFFICE
entity:SSC_03_021_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.021 VISITOR'S CUBICLE
entity:SSC_03_022_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.022 RESEARCHER'S OFFICE
entity:SSC_03_023_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.023 RESEARCHER'S OFFICE
entity:SSC_03_024_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.024 VISITOR'S CUBICLE
entity:SSC_03_025_SECRETARIAL_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.025 SECRETARIAL AREA
entity:SSC_03_026_MEETING_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.026 MEETING ROOM
entity:SSC_03_027_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.027 RESEARCHER'S OFFICE
entity:SSC_03_028_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.028 VISITOR'S CUBICLE
entity:SSC_03_029_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.029 RESEARCHER'S OFFICE
entity:SSC_03_030_ASSOC_DIRECTORS_MEETING_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.03 ASSOC. DIRECTOR'S MEETING ROOM
entity:SSC_03_031_ASSOC_DIRECTORS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.031 ASSOC. DIRECTOR'S OFFICE
entity:SSC_03_032_GENERAL_OFFICE_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.032 GENERAL OFFICE AREA
entity:SSC_03_033_PRINTING | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.033 PRINTING
entity:SSC_03_034_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.034 CORRIDOR
entity:SSC_03_035_STUDY_LIBRARY_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.035 STUDY LIBRARY AREA
entity:SSC_03_036_KITCHEN | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.036 KITCHEN
entity:SSC_03_037_MALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.037 MALE TOILET
entity:SSC_03_038_SERVER_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.038 IT SERVER ROOM
entity:SSC_03_039_FEMALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.039 FEMALE TOILET
entity:SSC_03_040_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.04 CORRIDOR
entity:SSC_03_041_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.041 CORRIDOR
entity:SSC_03_042_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.042 CORRIDOR
entity:SSC_03_043_EXTERIOR_COURTYARD | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.043 EXTERIOR COURTYARD
entity:SSC_03_044_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.044 CORRIDOR
entity:SSC_03_045_JANITORS_CLOSET | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.045 JANITOR'S CLOSET
entity:SSC_03_046_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.046 STORAGE
entity:SSC_03_047_BALCONY | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.047 BALCONY
entity:SSC_03_048_BALCONY | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.048 BALCONY
entity:SSC_03_049_IT_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.049 IT OFFICE
entity:SSC_03_F7_1_PODIUM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 03.F7.1 PODIUM
entity:SSC_03_P-1_LIFT | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 03.P-1 LIFT
entity:SSC_03_P-2_LIFT | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 03.P-2 LIFT
entity:SSC_03_ST-1_STAIR-1 | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 03.ST-1 STAIR-1
entity:SSC_03_ST-2_STAIR-2 | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 03.ST-2 STAIR-2
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_Filter | brick:Filter |  |  | rdfs:label_en | Pre Filter and Bag Filter
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_OAD | brick:Outside_Damper |  |  | rdfs:label_en | Outside Air Damper
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_RAD | brick:Return_Damper |  |  | rdfs:label_en | Return Air Damper
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_MAD | brick:Mixed_Damper |  |  | rdfs:label_en | Mixed Air Damper
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_EAD | brick:Exhaust_Damper |  |  | rdfs:label_en | Exhaust Air Damper
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_RF | brick:Return_Fan |  |  | rdfs:label_en | Return Fan
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_Heater | brick:Heater |  |  | rdfs:label_en | Heater
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_OA_RH | brick:Outside_Air_Humidity_Sensor |  |  | rdfs:label_en | Fresh Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_OA_Temperature | brick:Outside_Air_Temperature_Sensor |  |  | rdfs:label_en | Fresh Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_RA_RH | brick:Return_Air_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_RA_Temperature | brick:Return_Air_Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_RA_Flow | brick:Return_Air_Flow_Sensor |  |  | rdfs:label_en | Return Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_MA_Temperature | brick:Mixed_Air_Temperature_Sensor |  |  | rdfs:label_en | Mixed Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_SA_Flow | brick:Supply_Air_Flow_Sensor |  |  | rdfs:label_en | Supply Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_SA_RH | brick:Supply_Air_Humidity_Sensor |  |  | rdfs:label_en | Supply Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_SAT | brick:Supply_Air_Temperature_Sensor |  |  | rdfs:label_en | Supply Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_Occupancy_Mode | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_Dehum_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Dehumidification Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_SAP_Setpoint | brick:Static_Pressure_Setpoint |  |  | rdfs:label_en | Pressure Setpoint |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | UnOccupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_Enable_Disable_Cmd | brick:System_Enable_Command |  |  | rdfs:label_en | AHU Enable Disable Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_Pressure_High_Filter_Dirty_Status | brick:Filter_Status |  |  | rdfs:label_en | Pressure high Filter Dirty Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_High_Pressure_Alarm | brick:Pressure_Alarm |  |  | rdfs:label_en | Pressure Switch High |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_SA_P-Static | brick:Static_Pressure_Sensor |  |  | rdfs:label_en | Supply Air Duct Remote Pressure 01 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_RA_P-Static | para:Return_Air_Static_Pressure_Sensor |  |  | rdfs:label_en | Return Air Duct Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC AHUB0001 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | para:ratedOutsideAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 570 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | para:ratedSupplyAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 3800 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rec:locatedIn | entity:SSC_B1_013_CHILLED_WATER | rec:Room
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_AHUB0001 |  |  | ref:ifcName | SSC_AHUB0001
entity:SSC_AHUB0001_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 29.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0001_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_AHUB0001_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_AHUB0001_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPart | entity:SSC_AHUB0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | Cooling Thermal Power Meter
entity:SSC_AHUB0001_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0001_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command |  |  | rdfs:label_en | Cooling Valve Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0001_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Cooling Valve Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_CoolVlv.PosCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_CoolVlv.PosFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0001_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Load Consumption |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_AHUB0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0001_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Load Demand |  |  | brick:hasUnit | para:KiloWt
entity:SSC_AHUB0001_Dehum_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SP.DehumSP |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0001_EAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Exhaust Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0001_EAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Exhaust Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0001_EAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Exhaust Fan Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_EAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_ExhDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_EAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_ExhDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_EAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001.ExAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Enable_Disable_Cmd | brick:System_Enable_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001.EnableDisableCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Heater | brick:Heater | brick:hasPoint | entity:SSC_AHUB0001_Heater_Command | brick:Heating_Command |  |  | rdfs:label_en | Heater Control |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_Heater_Command | brick:Heating_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupHtr.HtrCtrl |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_High_Pressure_Alarm | brick:Pressure_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SP.PressSWHigh |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_MA_Temperature | brick:Mixed_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_MixAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0001_MAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Mixed Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0001_MAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Mixed Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_MAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_MixDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_MAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_MixDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_OA_RH | brick:Outside_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_FrshAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_OA_Temperature | brick:Outside_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_FrshAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0001_OAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Fresh Air Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0001_OAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Fresh Air Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0001_OAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Fresh Air Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_OAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_FrshDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_OAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_FrshDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_OAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001.FrshAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SP.OccTempSP |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Occupancy_Mode | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001.OccMode |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Pressure_High_Filter_Dirty_Status | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupPreFlt.PressureHigh |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RA_Flow | brick:Return_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RA_P-Static | para:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirDuctPrs.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RA_RH | brick:Return_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RA_Temperature | brick:Return_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 |  |  | rdfs:label_en | Damper Position 100 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 |  |  | rdfs:label_en | Damper Position 70 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 |  |  | rdfs:label_en | Damper Position 77.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 |  |  | rdfs:label_en | Damper Position 85 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 |  |  | rdfs:label_en | Damper Position 92.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0001_MinFALoocupTb.RecDmprPos100 |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0001_MinFALoocupTb.RecDmprPos70 |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0001_MinFALoocupTb.RecDmprPos77.5 |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0001_MinFALoocupTb.RecDmprPos85 |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0001_MinFALoocupTb.RecDmprPos92.5 |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF | brick:Return_Fan | brick:hasPart | entity:SSC_AHUB0001_RF_Motor | brick:Motor |  |  | rdfs:label_en | Return Fan Motor
entity:SSC_AHUB0001_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0001_RF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Return Fan AutoMan_Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0001_RF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Return Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_RF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0001_RF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0001_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0001_RF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Return Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0001_RF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Return Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0001_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0001_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Return Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0001_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0001_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Return Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0001_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.kWh |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.kW |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SA_Flow | brick:Supply_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupAirDuctPrsRmt1.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SA_RH | brick:Supply_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SAP_Setpoint | brick:Static_Pressure_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SP.PressSP |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SAT | brick:Supply_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_AHUB0001_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0001_SF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Supplu Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0001_SF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Supply Fan Auto Man Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0001_SF_FailtoStop | para:Fail_Stop_Alarm |  |  | rdfs:label_en | Supply Fan Fail to Stop |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0001_SF_FailtoStart | para:Fail_Start_Alarm |  |  | rdfs:label_en | Supply Fan FailtoStart |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0001_SF_Status | brick:On_Off_Status |  |  | rdfs:label_en | Supply Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_SF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_FailtoStart | para:Fail_Start_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.FTST |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_FailtoStop | para:Fail_Stop_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.FTSP |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0001_SF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0001_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0001_SF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Supply Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0001_SF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Supply Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0001_SF_Motor | brick:Motor | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value | 50 |  |  | brick:hasUnit | unit:HZ
entity:SSC_AHUB0001_SF_Motor | brick:Motor | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value | 11 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0001_SF_Motor | brick:Motor | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value | 415 |  |  | brick:hasUnit | unit:V
entity:SSC_AHUB0001_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.kWh |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0001_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Supply Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0001_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0001_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Supply Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0001_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.kW |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001.SupFanSts |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SP.UnOccTempSP |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_Filter | brick:Filter |  |  | rdfs:label_en | Pre Filter and Bag Filter
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_OAD | brick:Outside_Damper |  |  | rdfs:label_en | Outside Air Damper
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_RAD | brick:Return_Damper |  |  | rdfs:label_en | Return Air Damper
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_MAD | brick:Mixed_Damper |  |  | rdfs:label_en | Mixed Air Damper
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_EAD | brick:Exhaust_Damper |  |  | rdfs:label_en | Exhaust Air Damper
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_RF | brick:Return_Fan |  |  | rdfs:label_en | Return Fan
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_Heater | brick:Heater |  |  | rdfs:label_en | Heater
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_OA_RH | brick:Outside_Air_Humidity_Sensor |  |  | rdfs:label_en | Fresh Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_OA_Temperature | brick:Outside_Air_Temperature_Sensor |  |  | rdfs:label_en | Fresh Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_RA_RH | brick:Return_Air_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_RA_Temperature | brick:Return_Air_Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_RA_Flow | brick:Return_Air_Flow_Sensor |  |  | rdfs:label_en | Return Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_MA_Temperature | brick:Mixed_Air_Temperature_Sensor |  |  | rdfs:label_en | Mixed Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_SA_Flow | brick:Supply_Air_Flow_Sensor |  |  | rdfs:label_en | Supply Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_SA_RH | brick:Supply_Air_Humidity_Sensor |  |  | rdfs:label_en | Supply Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_SAT | brick:Supply_Air_Temperature_Sensor |  |  | rdfs:label_en | Supply Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_Occupancy_Mode | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_Dehum_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Dehumidification Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_SAP_Setpoint | brick:Static_Pressure_Setpoint |  |  | rdfs:label_en | Pressure Setpoint |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | UnOccupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_Enable_Disable_Cmd | brick:System_Enable_Command |  |  | rdfs:label_en | AHU Enable Disable Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_Pressure_High_Filter_Dirty_Status | brick:Filter_Status |  |  | rdfs:label_en | Pressure high Filter Dirty Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_High_Pressure_Alarm | brick:Pressure_Alarm |  |  | rdfs:label_en | Pressure Switch High |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_SA_P-Static | brick:Static_Pressure_Sensor |  |  | rdfs:label_en | Supply Air Duct Remote Pressure 02 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_RA_P-Static | para:Return_Air_Static_Pressure_Sensor |  |  | rdfs:label_en | Return Air Duct Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC AHUB0002 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | para:ratedOutsideAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 1440 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | para:ratedSupplyAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 9800 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_AHUB0002 |  |  | ref:ifcName | SSC_AHUB0002
entity:SSC_AHUB0002_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 29.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0002_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_AHUB0002_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_AHUB0002_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPart | entity:SSC_AHUB0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | Cooling Thermal Power Meter
entity:SSC_AHUB0002_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0002_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command |  |  | rdfs:label_en | Cooling Valve Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0002_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Cooling Valve Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_CoolVlv.PosCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_CoolVlv.PosFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0002_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Load Consumption |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_AHUB0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0002_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Load Demand |  |  | brick:hasUnit | para:KiloWt
entity:SSC_AHUB0002_Dehum_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SP.DehumSP |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0002_EAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Exhaust Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0002_EAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Exhaust Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0002_EAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Exhaust Fan Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_EAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_ExhDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_EAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_ExhDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_EAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002.ExAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Enable_Disable_Cmd | brick:System_Enable_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002.EnableDisableCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Heater | brick:Heater | brick:hasPoint | entity:SSC_AHUB0002_Heater_Command | brick:Heating_Command |  |  | rdfs:label_en | Heater Control |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_Heater_Command | brick:Heating_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupHtr.HtrCtrl |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_High_Pressure_Alarm | brick:Pressure_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SP.PressSWHigh |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_MA_Temperature | brick:Mixed_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_MixAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0002_MAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Mixed Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0002_MAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Mixed Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_MAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_MixDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_MAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_MixDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_OA_RH | brick:Outside_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_FrshAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_OA_Temperature | brick:Outside_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_FrshAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0002_OAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Fresh Air Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0002_OAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Fresh Air Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0002_OAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Fresh Air Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_OAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_FrshDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_OAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_FrshDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_OAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002.FrshAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SP.OccTempSP |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Occupancy_Mode | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002.OccMode |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Pressure_High_Filter_Dirty_Status | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupPreFlt.PressureHigh |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RA_Flow | brick:Return_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RA_P-Static | para:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirDuctPrs.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RA_RH | brick:Return_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RA_Temperature | brick:Return_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 |  |  | rdfs:label_en | Damper Position 100 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 |  |  | rdfs:label_en | Damper Position 70 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 |  |  | rdfs:label_en | Damper Position 77.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 |  |  | rdfs:label_en | Damper Position 85 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 |  |  | rdfs:label_en | Damper Position 92.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0002_MinFALoocupTb.RecDmprPos100 |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0002_MinFALoocupTb.RecDmprPos70 |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0002_MinFALoocupTb.RecDmprPos77.5 |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0002_MinFALoocupTb.RecDmprPos85 |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0002_MinFALoocupTb.RecDmprPos92.5 |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF | brick:Return_Fan | brick:hasPart | entity:SSC_AHUB0002_RF_Motor | brick:Motor |  |  | rdfs:label_en | Return Fan Motor
entity:SSC_AHUB0002_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0002_RF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Return Fan AutoMan_Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0002_RF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Return Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_RF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0002_RF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0002_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0002_RF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Return Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0002_RF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Return Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0002_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0002_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Return Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0002_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0002_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Return Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0002_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.kWh |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.kW |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SA_Flow | brick:Supply_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupAirDuctPrsRmt2.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupAirDuctPrsRmt1.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SA_RH | brick:Supply_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SAP_Setpoint | brick:Static_Pressure_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SP.PressSP |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SAT | brick:Supply_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_AHUB0002_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0002_SF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Supplu Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0002_SF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Supply Fan Auto Man Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0002_SF_FailtoStop | para:Fail_Stop_Alarm |  |  | rdfs:label_en | Supply Fan Fail to Stop |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0002_SF_FailtoStart | para:Fail_Start_Alarm |  |  | rdfs:label_en | Supply Fan FailtoStart |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0002_SF_Status | brick:On_Off_Status |  |  | rdfs:label_en | Supply Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_SF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_FailtoStart | para:Fail_Start_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.FTST |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_FailtoStop | para:Fail_Stop_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.FTSP |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0002_SF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0002_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0002_SF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Supply Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0002_SF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Supply Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0002_SF_Motor | brick:Motor | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value | 50 |  |  | brick:hasUnit | unit:HZ
entity:SSC_AHUB0002_SF_Motor | brick:Motor | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value | 22 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0002_SF_Motor | brick:Motor | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value | 415 |  |  | brick:hasUnit | unit:V
entity:SSC_AHUB0002_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.kWh |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0002_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Supply Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0002_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0002_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Supply Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0002_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.kW |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002.SupFanSts |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SP.UnOccTempSP |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_Filter | brick:Filter |  |  | rdfs:label_en | Pre Filter and Bag Filter
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_OAD | brick:Outside_Damper |  |  | rdfs:label_en | Outside Air Damper
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_RAD | brick:Return_Damper |  |  | rdfs:label_en | Return Air Damper
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_MAD | brick:Mixed_Damper |  |  | rdfs:label_en | Mixed Air Damper
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_EAD | brick:Exhaust_Damper |  |  | rdfs:label_en | Exhaust Air Damper
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_RF | brick:Return_Fan |  |  | rdfs:label_en | Return Fan
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_Heater | brick:Heater |  |  | rdfs:label_en | Heater
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_OA_RH | brick:Outside_Air_Humidity_Sensor |  |  | rdfs:label_en | Fresh Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_OA_Temperature | brick:Outside_Air_Temperature_Sensor |  |  | rdfs:label_en | Fresh Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_RA_RH | brick:Return_Air_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_RA_Temperature | brick:Return_Air_Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_RA_Flow | brick:Return_Air_Flow_Sensor |  |  | rdfs:label_en | Return Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_MA_Temperature | brick:Mixed_Air_Temperature_Sensor |  |  | rdfs:label_en | Mixed Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_SA_Flow | brick:Supply_Air_Flow_Sensor |  |  | rdfs:label_en | Supply Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_SA_RH | brick:Supply_Air_Humidity_Sensor |  |  | rdfs:label_en | Supply Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_SAT | brick:Supply_Air_Temperature_Sensor |  |  | rdfs:label_en | Supply Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_Occupancy_Mode | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_Dehum_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Dehumidification Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | UnOccupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_Enable_Disable_Cmd | brick:System_Enable_Command |  |  | rdfs:label_en | AHU Enable Disable Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_Pressure_High_Filter_Dirty_Status | brick:Filter_Status |  |  | rdfs:label_en | Pressure high Filter Dirty Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_High_Pressure_Alarm | brick:Pressure_Alarm |  |  | rdfs:label_en | Pressure Switch High |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_SA_P-Static | brick:Static_Pressure_Sensor |  |  | rdfs:label_en | Supply Air Duct Remote Pressure 02 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_RA_P-Static | para:Return_Air_Static_Pressure_Sensor |  |  | rdfs:label_en | Return Air Duct Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC AHUB0003 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | para:ratedOutsideAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 320 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | para:ratedSupplyAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 5700 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_AHUB0003 |  |  | ref:ifcName | SSC_AHUB0003
entity:SSC_AHUB0003_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 29.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0003_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_AHUB0003_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_AHUB0003_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPart | entity:SSC_AHUB0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | Cooling Thermal Power Meter
entity:SSC_AHUB0003_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0003_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command |  |  | rdfs:label_en | Cooling Valve Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0003_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Cooling Valve Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_CoolVlv.PosCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_CoolVlv.PosFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0003_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Load Consumption |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_AHUB0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0003_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Load Demand |  |  | brick:hasUnit | para:KiloWt
entity:SSC_AHUB0003_Dehum_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SP.DehumSP |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0003_EAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Exhaust Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0003_EAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Exhaust Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0003_EAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Exhaust Fan Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_EAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_ExhDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_EAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_ExhDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_EAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003.ExAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Enable_Disable_Cmd | brick:System_Enable_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003.EnableDisableCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Heater | brick:Heater | brick:hasPoint | entity:SSC_AHUB0003_Heater_Command | brick:Heating_Command |  |  | rdfs:label_en | Heater Control |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_Heater_Command | brick:Heating_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupHtr.HtrCtrl |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_High_Pressure_Alarm | brick:Pressure_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SP.PressSWHigh |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_MA_Temperature | brick:Mixed_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_MixAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0003_MAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Mixed Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0003_MAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Mixed Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_MAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_MixDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_MAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_MixDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_OA_RH | brick:Outside_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_FrshAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_OA_Temperature | brick:Outside_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_FrshAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0003_OAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Fresh Air Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0003_OAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Fresh Air Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0003_OAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Fresh Air Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_OAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_FrshDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_OAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_FrshDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_OAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003.FrshAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SP.OccTempSP |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Occupancy_Mode | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003.OccMode |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Pressure_High_Filter_Dirty_Status | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupPreFlt.PressureHigh |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RA_Flow | brick:Return_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RA_P-Static | para:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirDuctPrs.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RA_RH | brick:Return_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RA_Temperature | brick:Return_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 |  |  | rdfs:label_en | Damper Position 100 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 |  |  | rdfs:label_en | Damper Position 70 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 |  |  | rdfs:label_en | Damper Position 77.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 |  |  | rdfs:label_en | Damper Position 85 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 |  |  | rdfs:label_en | Damper Position 92.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0003_MinFALoocupTb.RecDmprPos100 |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0003_MinFALoocupTb.RecDmprPos70 |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0003_MinFALoocupTb.RecDmprPos77.5 |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0003_MinFALoocupTb.RecDmprPos85 |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0003_MinFALoocupTb.RecDmprPos92.5 |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF | brick:Return_Fan | brick:hasPart | entity:SSC_AHUB0003_RF_Motor | brick:Motor |  |  | rdfs:label_en | Return Fan Motor
entity:SSC_AHUB0003_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0003_RF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Return Fan AutoMan_Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0003_RF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Return Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_RF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0003_RF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0003_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0003_RF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Return Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0003_RF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Return Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0003_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0003_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Return Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0003_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0003_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Return Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0003_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.kWh |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.kW |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SA_Flow | brick:Supply_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupAirDuctPrsRmt2.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupAirDuctPrsRmt1.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SA_RH | brick:Supply_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SAT | brick:Supply_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_AHUB0003_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0003_SF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Supplu Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0003_SF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Supply Fan Auto Man Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0003_SF_FailtoStop | para:Fail_Stop_Alarm |  |  | rdfs:label_en | Supply Fan Fail to Stop |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0003_SF_FailtoStart | para:Fail_Start_Alarm |  |  | rdfs:label_en | Supply Fan FailtoStart |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0003_SF_Status | brick:On_Off_Status |  |  | rdfs:label_en | Supply Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_SF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_FailtoStart | para:Fail_Start_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.FTST |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_FailtoStop | para:Fail_Stop_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.FTSP |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0003_SF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0003_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0003_SF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Supply Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0003_SF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Supply Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0003_SF_Motor | brick:Motor | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value | 50 |  |  | brick:hasUnit | unit:HZ
entity:SSC_AHUB0003_SF_Motor | brick:Motor | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value | 15 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0003_SF_Motor | brick:Motor | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value | 415 |  |  | brick:hasUnit | unit:V
entity:SSC_AHUB0003_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.kWh |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0003_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Supply Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0003_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0003_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Supply Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0003_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.kW |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003.SupFanSts |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SP.UnOccTempSP |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_Filter | brick:Filter |  |  | rdfs:label_en | Pre Filter and Bag Filter
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_OAD | brick:Outside_Damper |  |  | rdfs:label_en | Outside Air Damper
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_RAD | brick:Return_Damper |  |  | rdfs:label_en | Return Air Damper
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_MAD | brick:Mixed_Damper |  |  | rdfs:label_en | Mixed Air Damper
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_EAD | brick:Exhaust_Damper |  |  | rdfs:label_en | Exhaust Air Damper
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_RF | brick:Return_Fan |  |  | rdfs:label_en | Return Fan
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_Heater | brick:Heater |  |  | rdfs:label_en | Heater
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_OA_RH | brick:Outside_Air_Humidity_Sensor |  |  | rdfs:label_en | Fresh Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_OA_Temperature | brick:Outside_Air_Temperature_Sensor |  |  | rdfs:label_en | Fresh Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_RH | brick:Return_Air_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_Temperature | brick:Return_Air_Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_Flow | brick:Return_Air_Flow_Sensor |  |  | rdfs:label_en | Return Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_MA_Temperature | brick:Mixed_Air_Temperature_Sensor |  |  | rdfs:label_en | Mixed Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_SA_Flow | brick:Supply_Air_Flow_Sensor |  |  | rdfs:label_en | Supply Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_SA_RH | brick:Supply_Air_Humidity_Sensor |  |  | rdfs:label_en | Supply Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_SAT | brick:Supply_Air_Temperature_Sensor |  |  | rdfs:label_en | Supply Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_Occupancy_Mode | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_Dehum_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Dehumidification Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_SAP_Setpoint | brick:Static_Pressure_Setpoint |  |  | rdfs:label_en | Pressure Setpoint |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | UnOccupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_Enable_Disable_Cmd | brick:System_Enable_Command |  |  | rdfs:label_en | AHU Enable Disable Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_Pressure_High_Filter_Dirty_Status | brick:Filter_Status |  |  | rdfs:label_en | Pressure high Filter Dirty Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_High_Pressure_Alarm | brick:Pressure_Alarm |  |  | rdfs:label_en | Pressure Switch High |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_P-Static_01 | para:Return_Air_Static_Pressure_Sensor_01 |  |  | rdfs:label_en | Return Air Duct Pressure 01 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_P-Static_02 | para:Return_Air_Static_Pressure_Sensor_02 |  |  | rdfs:label_en | Return Air Duct Pressure 02 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_SA_P-Static | brick:Static_Pressure_Sensor |  |  | rdfs:label_en | Supply Air Duct Remote Pressure 02 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_P-Static | para:Return_Air_Static_Pressure_Sensor |  |  | rdfs:label_en | Return Air Duct Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC AHUB0004 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | para:ratedOutsideAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 1070 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | para:ratedSupplyAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 7800 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rec:locatedIn | entity:SSC_B1_008_VENT_PLANT | rec:Room
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_AHUB0004 |  |  | ref:ifcName | SSC_AHUB0004
entity:SSC_AHUB0004_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 29.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0004_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_AHUB0004_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_AHUB0004_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPart | entity:SSC_AHUB0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | Cooling Thermal Power Meter
entity:SSC_AHUB0004_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0004_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command |  |  | rdfs:label_en | Cooling Valve Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0004_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Cooling Valve Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_CoolVlv.PosCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_CoolVlv.PosFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0004_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Load Consumption |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_AHUB0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0004_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Load Demand |  |  | brick:hasUnit | para:KiloWt
entity:SSC_AHUB0004_Dehum_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SP.DehumSP |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0004_EAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Exhaust Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0004_EAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Exhaust Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0004_EAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Exhaust Fan Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_EAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_ExhDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_EAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_ExhDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_EAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004.ExAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Enable_Disable_Cmd | brick:System_Enable_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004.EnableDisableCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Heater | brick:Heater | brick:hasPoint | entity:SSC_AHUB0004_Heater_Command | brick:Heating_Command |  |  | rdfs:label_en | Heater Control |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_Heater_Command | brick:Heating_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupHtr.HtrCtrl |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_High_Pressure_Alarm | brick:Pressure_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SP.PressSWHigh |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_MA_Temperature | brick:Mixed_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_MixAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0004_MAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Mixed Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0004_MAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Mixed Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_MAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_MixDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_MAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_MixDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_OA_RH | brick:Outside_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_FrshAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_OA_Temperature | brick:Outside_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_FrshAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0004_OAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Fresh Air Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0004_OAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Fresh Air Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0004_OAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Fresh Air Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_OAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_FrshDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_OAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_FrshDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_OAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004.FrshAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SP.OccTempSP |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Occupancy_Mode | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004.OccMode |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Pressure_High_Filter_Dirty_Status | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupPreFlt.PressureHigh |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_Flow | brick:Return_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_P-Static | para:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirDuctPrs.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_P-Static_01 | para:Static_Pressure_Sensor_01 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnAirDuctPrs1.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_P-Static_02 | para:Static_Pressure_Sensor_02 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnAirDuctPrs2.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_RH | brick:Return_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_Temperature | brick:Return_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 |  |  | rdfs:label_en | Damper Position 100 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 |  |  | rdfs:label_en | Damper Position 70 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 |  |  | rdfs:label_en | Damper Position 77.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 |  |  | rdfs:label_en | Damper Position 85 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 |  |  | rdfs:label_en | Damper Position 92.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0004_MinFALoocupTb.RecDmprPos100 |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0004_MinFALoocupTb.RecDmprPos70 |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0004_MinFALoocupTb.RecDmprPos77.5 |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0004_MinFALoocupTb.RecDmprPos85 |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0004_MinFALoocupTb.RecDmprPos92.5 |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RF | brick:Return_Fan | brick:hasPart | entity:SSC_AHUB0004_RF_Motor | brick:Motor |  |  | rdfs:label_en | Return Fan Motor
entity:SSC_AHUB0004_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0004_RF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Return Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_RF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0004_RF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0004_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0004_RF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Return Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0004_RF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Return Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0004_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0004_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Return Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0004_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0004_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Return Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0004_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnFanDty.kW |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnFanDty.kWh |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnFanDty.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnFanDty.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnFanDty.TripAlm |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SA_Flow | brick:Supply_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupAirDuctPrsRmt2.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupAirDuctPrsRmt1.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SA_RH | brick:Supply_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SAP_Setpoint | brick:Static_Pressure_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SP.PressSP |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SAT | brick:Supply_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_AHUB0004_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0004_SF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Supplu Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0004_SF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Supply Fan Auto Man Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0004_SF_FailtoStop | para:Fail_Stop_Alarm |  |  | rdfs:label_en | Supply Fan Fail to Stop |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0004_SF_FailtoStart | para:Fail_Start_Alarm |  |  | rdfs:label_en | Supply Fan FailtoStart |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0004_SF_Status | brick:On_Off_Status |  |  | rdfs:label_en | Supply Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_SF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_FailtoStart | para:Fail_Start_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.FTST |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_FailtoStop | para:Fail_Stop_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.FTSP |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0004_SF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0004_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0004_SF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Supply Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0004_SF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Supply Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0004_SF_Motor | brick:Motor | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value | 50 |  |  | brick:hasUnit | unit:HZ
entity:SSC_AHUB0004_SF_Motor | brick:Motor | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value | 18.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0004_SF_Motor | brick:Motor | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value | 415 |  |  | brick:hasUnit | unit:V
entity:SSC_AHUB0004_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.kWh |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0004_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Supply Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0004_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0004_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Supply Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0004_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.kW |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004.SupFanSts |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SP.UnOccTempSP |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_Filter | brick:Filter |  |  | rdfs:label_en | Pre Filter and Bag Filter
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_OAD | brick:Outside_Damper |  |  | rdfs:label_en | Outside Air Damper
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_RAD | brick:Return_Damper |  |  | rdfs:label_en | Return Air Damper
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_MAD | brick:Mixed_Damper |  |  | rdfs:label_en | Mixed Air Damper
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_EAD | brick:Exhaust_Damper |  |  | rdfs:label_en | Exhaust Air Damper
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_RF | brick:Return_Fan |  |  | rdfs:label_en | Return Fan
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_Heater | brick:Heater |  |  | rdfs:label_en | Heater
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_OA_RH | brick:Outside_Air_Humidity_Sensor |  |  | rdfs:label_en | Fresh Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_OA_Temperature | brick:Outside_Air_Temperature_Sensor |  |  | rdfs:label_en | Fresh Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_RA_RH | brick:Return_Air_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_RA_Temperature | brick:Return_Air_Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_RA_Flow | brick:Return_Air_Flow_Sensor |  |  | rdfs:label_en | Return Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_MA_Temperature | brick:Mixed_Air_Temperature_Sensor |  |  | rdfs:label_en | Mixed Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_SA_Flow | brick:Supply_Air_Flow_Sensor |  |  | rdfs:label_en | Supply Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_SA_RH | brick:Supply_Air_Humidity_Sensor |  |  | rdfs:label_en | Supply Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_SAT | brick:Supply_Air_Temperature_Sensor |  |  | rdfs:label_en | Supply Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_Occupancy_Mode | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_Dehum_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Dehumidification Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | UnOccupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_Enable_Disable_Cmd | brick:System_Enable_Command |  |  | rdfs:label_en | AHU Enable Disable Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_Pressure_High_Filter_Dirty_Status | brick:Filter_Status |  |  | rdfs:label_en | Pressure high Filter Dirty Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_High_Pressure_Alarm | brick:Pressure_Alarm |  |  | rdfs:label_en | Pressure Switch High |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_SA_P-Static | brick:Static_Pressure_Sensor |  |  | rdfs:label_en | Supply Air Duct Remote Pressure 01 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_RA_P-Static | para:Return_Air_Static_Pressure_Sensor |  |  | rdfs:label_en | Return Air Duct Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC AHUB0005 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | para:ratedOutsideAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 850 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | para:ratedSupplyAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 2000 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | rec:locatedIn | entity:SSC_B1_013_CHILLED_WATER | rec:Room
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_AHUB0005 |  |  | ref:ifcName | SSC_AHUB0005
entity:SSC_AHUB0005_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 29.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0005_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_AHUB0005_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_AHUB0005_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPart | entity:SSC_AHUB0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | Cooling Thermal Power Meter
entity:SSC_AHUB0005_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0005_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command |  |  | rdfs:label_en | Cooling Valve Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0005_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Cooling Valve Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_CoolVlv.PosCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_CoolVlv.PosFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0005_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Load Consumption |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_AHUB0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0005_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Load Demand |  |  | brick:hasUnit | para:KiloWt
entity:SSC_AHUB0005_Dehum_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SP.DehumSP |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0005_EAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Exhaust Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0005_EAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Exhaust Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0005_EAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Exhaust Fan Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_EAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_ExhDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_EAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_ExhDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_EAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005.ExAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Enable_Disable_Cmd | brick:System_Enable_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005.EnableDisableCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Heater | brick:Heater | brick:hasPoint | entity:SSC_AHUB0005_Heater_Command | brick:Heating_Command |  |  | rdfs:label_en | Heater Control |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_Heater_Command | brick:Heating_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupHtr.HtrCtrl |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_High_Pressure_Alarm | brick:Pressure_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SP.PressSWHigh |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_MA_Temperature | brick:Mixed_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_MixAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0005_MAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Mixed Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0005_MAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Mixed Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_MAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_MixDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_MAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_MixDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_OA_RH | brick:Outside_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_FrshAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_OA_Temperature | brick:Outside_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_FrshAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0005_OAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Fresh Air Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0005_OAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Fresh Air Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0005_OAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Fresh Air Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_OAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_FrshDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_OAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_FrshDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_OAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005.FrshAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SP.OccTempSP |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Occupancy_Mode | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005.OccMode |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Pressure_High_Filter_Dirty_Status | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupPreFlt.PressureHigh |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RA_Flow | brick:Return_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RA_P-Static | para:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirDuctPrs.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RA_RH | brick:Return_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RA_Temperature | brick:Return_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 |  |  | rdfs:label_en | Damper Position 100 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 |  |  | rdfs:label_en | Damper Position 70 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 |  |  | rdfs:label_en | Damper Position 77.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 |  |  | rdfs:label_en | Damper Position 85 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 |  |  | rdfs:label_en | Damper Position 92.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0005_MinFALoocupTb.RecDmprPos100 |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0005_MinFALoocupTb.RecDmprPos70 |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0005_MinFALoocupTb.RecDmprPos77.5 |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0005_MinFALoocupTb.RecDmprPos85 |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0005_MinFALoocupTb.RecDmprPos92.5 |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF | brick:Return_Fan | brick:hasPart | entity:SSC_AHUB0005_RF_Motor | brick:Motor |  |  | rdfs:label_en | Return Fan Motor
entity:SSC_AHUB0005_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0005_RF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Return Fan AutoMan_Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0005_RF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Return Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_RF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0005_RF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0005_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0005_RF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Return Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0005_RF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Return Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0005_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0005_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Return Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0005_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0005_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Return Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0005_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.kWh |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.kW |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SA_Flow | brick:Supply_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupAirDuctPrsRmt1.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SA_RH | brick:Supply_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SAT | brick:Supply_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_AHUB0005_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0005_SF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Supplu Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0005_SF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Supply Fan Auto Man Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0005_SF_FailtoStop | para:Fail_Stop_Alarm |  |  | rdfs:label_en | Supply Fan Fail to Stop |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0005_SF_FailtoStart | para:Fail_Start_Alarm |  |  | rdfs:label_en | Supply Fan FailtoStart |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0005_SF_Status | brick:On_Off_Status |  |  | rdfs:label_en | Supply Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_SF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_FailtoStart | para:Fail_Start_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.FTST |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_FailtoStop | para:Fail_Stop_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.FTSP |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0005_SF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0005_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0005_SF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Supply Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0005_SF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Supply Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0005_SF_Motor | brick:Motor | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value | 50 |  |  | brick:hasUnit | unit:HZ
entity:SSC_AHUB0005_SF_Motor | brick:Motor | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value | 5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0005_SF_Motor | brick:Motor | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value | 415 |  |  | brick:hasUnit | unit:V
entity:SSC_AHUB0005_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.kWh |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0005_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Supply Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0005_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0005_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Supply Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0005_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.kW |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005.SupFanSts |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SP.UnOccTempSP |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_B1_001_FM_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.001 FM STORAGE
entity:SSC_B1_002_HV_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.002 HV
entity:SSC_B1_003_TRANSFORMER | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.003 TRANSFORMER
entity:SSC_B1_004_MV_SWITCH_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.004 MV SWITCH ROOM
entity:SSC_B1_005_UPS | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.005 UPS
entity:SSC_B1_006_SERVICE_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.006 SERVICE AREA
entity:SSC_B1_007_SERVICE_DOCK | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.007 SERVICE DOCK
entity:SSC_B1_008_VENT_PLANT | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.008 VENT PLANT
entity:SSC_B1_009_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.009 TOILET
entity:SSC_B1_010_VESTIBULE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.010 VESTIBULE
entity:SSC_B1_011_JANITORS_CLOSET | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.011 JANITORS CLOSET
entity:SSC_B1_012_GENERATOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.012 GENERATOR
entity:SSC_B1_013_CHILLED_WATER | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.013 CHILLED WATER
entity:SSC_B1_014_VENT_PLANT | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.014 VENT PLANT
entity:SSC_B1_015_ENTRANCE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.015 ENTRANCE
entity:SSC_B1_016_SPRINKLER_&_WATER | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.016 SPRINKLER & WATER
entity:SSC_B1_017_MDF-2 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.017 MDF-2
entity:SSC_B1_018_CONDENSER_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.018 CONDENSER ROOM
entity:SSC_B1_019_FM_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.019 FM STORAGE
entity:SSC_B1_020_FM_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.020 FM STORAGE
entity:SSC_B1_021_FM_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.021 FM STORAGE
entity:SSC_B1_022_SSP | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.022 SSP
entity:SSC_B1_023_Q_TEL | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.023 QTEL
entity:SSC_B1_024_BIN_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.024 BIN STORAGE
entity:SSC_B1_025_MAIN_SEC_CONTROL_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.025 MAIN SEC. CONTROL ROOM
entity:SSC_B1_026_MDF_SER-1 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.026 MDF/SER-1
entity:SSC_B1_027_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.027 CORRIDOR
entity:SSC_B1_028_FILE_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.028 FILE STORAGE
entity:SSC_B1_029_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.029 CORRIDOR
entity:SSC_B1_030_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.030 CORRIDOR
entity:SSC_B1_031_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.031 CORRIDOR
entity:SSC_B1_032_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.032 CORRIDOR
entity:SSC_B1_034_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.034 CORRIDOR
entity:SSC_B1_035_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.035 CORRIDOR
entity:SSC_B1_036_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.036 STORAGE
entity:SSC_B1_038_SER-2 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.038 SER-2
entity:SSC_B1_039_BMS | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.039 BMS
entity:SSC_B1_P-1_P1 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.P-1 LIFT
entity:SSC_B1_P-2_P2 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.P-2 LIFT
entity:SSC_B1_ST-1_STAIR-1 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.ST-1 STAIR-1
entity:SSC_B1_ST-2_STAIR-2 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.ST-2 STAIR-2
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCU3F0301 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCU3F0301 | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCU3F0301 | brick:CRAC | rec:locatedIn | entity:SSC_B1_038_SER-2 | rec:Room
entity:SSC_CCU3F0301 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCU3F0301 |  |  | ref:ifcName | SSC_CCU3F0301
entity:SSC_CCU3F0301_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.CloggedFilter |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.CommAlm |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.CoolSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.DehumSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.ElectHtrSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.FanSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.Alm |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.HumSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.RtnHumidity |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.AirFlwLoss |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.MainFanOvrld |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.State |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.RunSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.SumAlmSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.RtnTemp |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.ActualTempSP |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCU3F0302 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCU3F0302 | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCU3F0302 | brick:CRAC | rec:locatedIn | entity:SSC_B1_038_SER-2 | rec:Room
entity:SSC_CCU3F0302 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCU3F0302 |  |  | ref:ifcName | SSC_CCU3F0302
entity:SSC_CCU3F0302_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.CloggedFilter |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.CommAlm |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.CoolSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.DehumSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.ElectHtrSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.FanSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.Alm |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.HumSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.RtnHumidity |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.AirFlwLoss |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.MainFanOvrld |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.State |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.RunSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.SumAlmSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.RtnTemp |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.ActualTempSP |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0001A |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0001A | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0001A | brick:CRAC | rec:locatedIn | entity:SSC_B1_038_SER-2 | rec:Room
entity:SSC_CCUB0001A | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0001A |  |  | ref:ifcName | SSC_CCUB0001A
entity:SSC_CCUB0001A_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.CommAlm |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.CoolSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.DehumSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.FanSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.Alm |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.HumSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.State |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.RunSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0001B |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0001B | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0001B | brick:CRAC | rec:locatedIn | entity:SSC_B1_038_SER-2 | rec:Room
entity:SSC_CCUB0001B | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0001B |  |  | ref:ifcName | SSC_CCUB0001B
entity:SSC_CCUB0001B_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.CommAlm |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.CoolSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.DehumSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.FanSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.Alm |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.HumSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.State |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.RunSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0002A |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0002A | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0002A | brick:CRAC | rec:locatedIn | entity:SSC_B1_038_SER-2 | rec:Room
entity:SSC_CCUB0002A | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0002A |  |  | ref:ifcName | SSC_CCUB0002A
entity:SSC_CCUB0002A_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.CommAlm |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.CoolSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.DehumSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.FanSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.Alm |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.HumSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.State |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.RunSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0002B |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0002B | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0002B | brick:CRAC | rec:locatedIn | entity:SSC_B1_038_SER-2 | rec:Room
entity:SSC_CCUB0002B | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0002B |  |  | ref:ifcName | SSC_CCUB0002B
entity:SSC_CCUB0002B_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.CommAlm |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.CoolSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.DehumSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.FanSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.Alm |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.HumSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.State |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.RunSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0003 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0003 | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0003 | brick:CRAC | rec:locatedIn | entity:SSC_B1_023_Q_TEL | rec:Room
entity:SSC_CCUB0003 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0003 |  |  | ref:ifcName | SSC_CCUB0003
entity:SSC_CCUB0003_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.CommAlm |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.CoolSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.DehumSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.FanSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.Alm |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.HumSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.State |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.RunSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0004 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0004 | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0004 | brick:CRAC | rec:locatedIn | entity:SSC_B1_023_Q_TEL | rec:Room
entity:SSC_CCUB0004 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0004 |  |  | ref:ifcName | SSC_CCUB0004
entity:SSC_CCUB0004_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.CommAlm |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.CoolSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.DehumSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.FanSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.Alm |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.HumSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.State |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.RunSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0005A |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0005A | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0005A | brick:CRAC | rec:locatedIn | entity:SSC_B1_023_Q_TEL | rec:Room
entity:SSC_CCUB0005A | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0005A |  |  | ref:ifcName | SSC_CCUB0005A
entity:SSC_CCUB0005A_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.CommAlm |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.CoolSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.DehumSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.FanSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.Alm |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.HumSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.State |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.RunSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0005B |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0005B | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0005B | brick:CRAC | rec:locatedIn | entity:SSC_B1_023_Q_TEL | rec:Room
entity:SSC_CCUB0005B | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0005B |  |  | ref:ifcName | SSC_CCUB0005B
entity:SSC_CCUB0005B_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.CommAlm |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.CoolSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.DehumSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.FanSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.Alm |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.HumSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.State |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.RunSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0006A |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0006A | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0006A | brick:CRAC | rec:locatedIn | entity:SSC_B1_023_Q_TEL | rec:Room
entity:SSC_CCUB0006A | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0006A |  |  | ref:ifcName | SSC_CCUB0006A
entity:SSC_CCUB0006A_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.CommAlm |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.CoolSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.DehumSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.FanSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.Alm |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.HumSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.State |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.RunSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0006B |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0006B | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0006B | brick:CRAC | rec:locatedIn | entity:SSC_B1_023_Q_TEL | rec:Room
entity:SSC_CCUB0006B | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0006B |  |  | ref:ifcName | SSC_CCUB0006B
entity:SSC_CCUB0006B_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.CommAlm |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.CoolSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.DehumSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.FanSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.Alm |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.HumSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.State |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.RunSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0007 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0007 | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0007 | brick:CRAC | rec:locatedIn | entity:SSC_B1_017_MDF-2 | rec:Room
entity:SSC_CCUB0007 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0007 |  |  | ref:ifcName | SSC_CCUB0007
entity:SSC_CCUB0007_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.CommAlm |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.CoolSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.DehumSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.FanSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.Alm |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.HumSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.State |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.RunSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | Air Flow Loss Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_General_Fault | brick:Alarm |  |  | rdfs:label_en | General Fault Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | Clogged Filter Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | Cooling Mode Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | Humidification Statu |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | Main Fan Overload |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Run Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | Summary Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CCUB0008 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0008 | brick:CRAC | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0008 | brick:CRAC | rec:locatedIn | entity:SSC_B1_017_MDF-2 | rec:Room
entity:SSC_CCUB0008 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0008 |  |  | ref:ifcName | SSC_CCUB0008
entity:SSC_CCUB0008_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.CommAlm |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.CoolSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.DehumSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.FanSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.Alm |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.HumSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.State |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.RunSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CHW_CHWP01 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP01_Motor | brick:Motor |  |  | rdfs:label_en | SSC_CHW_CHWP01 Motor
entity:SSC_CHW_CHWP01 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP01_Electrical_Meter | brick:Electrical_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP01 Electrical Meter
entity:SSC_CHW_CHWP01 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP01_Thermal_Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP01 Thermal Meter
entity:SSC_CHW_CHWP01 | brick:Chilled_Water_Booster_Pump | brick:hasPoint | entity:SSC_CHW_CHWP01_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration |  |  | rdfs:label_en | ScheduledPM Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP01 | brick:Chilled_Water_Booster_Pump | brick:hasPoint | entity:SSC_CHW_CHWP01_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration |  |  | rdfs:label_en | UnScheduled Outage Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP01 | brick:Chilled_Water_Booster_Pump | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | CHW Pump 01
entity:SSC_CHW_CHWP01 | brick:Chilled_Water_Booster_Pump | rec:feeds | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CHW_CHWP01 | brick:Chilled_Water_Booster_Pump | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_CHW_CHWP01 | brick:Chilled_Water_Booster_Pump | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_CHWP01 |  |  | ref:ifcName | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_Electrical_Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_CHW_CHWP01_Power_Sensor | brick:Power_Sensor |  |  | rdfs:label_en | Power |  |  | brick:hasUnit | unit:KiloW
entity:SSC_CHW_CHWP01_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP01_Speed_Command | brick:Speed_Command |  |  | rdfs:label_en | Speed Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_CHWP01_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP01_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_CHW_CHWP01_Power_Sensor | brick:Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.kW |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_Speed_Command | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.SpeedCmd |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.SpeedFbk |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_Thermal_Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_CHW_CHWP01_Thermal_Power_Sensor | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Thermal Load Fan |  |  | brick:hasUnit | para:KiloWt
entity:SSC_CHW_CHWP01_Thermal_Power_Sensor | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.ThermLoadFan |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP02 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP02_Motor | brick:Motor |  |  | rdfs:label_en | SSC_CHW_CHWP02 Motor
entity:SSC_CHW_CHWP02 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP02_Electrical_Meter | brick:Electrical_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP02 Electrical Meter
entity:SSC_CHW_CHWP02 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP02_Thermal_Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP02 Thermal Meter
entity:SSC_CHW_CHWP02 | brick:Chilled_Water_Booster_Pump | brick:hasPoint | entity:SSC_CHW_CHWP02_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration |  |  | rdfs:label_en | ScheduledPM Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP02 | brick:Chilled_Water_Booster_Pump | brick:hasPoint | entity:SSC_CHW_CHWP02_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration |  |  | rdfs:label_en | UnScheduled Outage Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP02 | brick:Chilled_Water_Booster_Pump | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | CHW Pump 02
entity:SSC_CHW_CHWP02 | brick:Chilled_Water_Booster_Pump | rec:feeds | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CHW_CHWP02 | brick:Chilled_Water_Booster_Pump | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_CHW_CHWP02 | brick:Chilled_Water_Booster_Pump | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_CHWP02 |  |  | ref:ifcName | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_Electrical_Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_CHW_CHWP02_Power_Sensor | brick:Power_Sensor |  |  | rdfs:label_en | Power |  |  | brick:hasUnit | unit:KiloW
entity:SSC_CHW_CHWP02_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP02_Speed_Command | brick:Speed_Command |  |  | rdfs:label_en | Speed Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_CHWP02_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP02_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_CHW_CHWP02_Power_Sensor | brick:Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.kW |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_Speed_Command | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.SpeedCmd |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.SpeedFbk |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_Thermal_Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_CHW_CHWP02_Thermal_Power_Sensor | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Thermal Load Fan |  |  | brick:hasUnit | para:KiloWt
entity:SSC_CHW_CHWP02_Thermal_Power_Sensor | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.ThermLoadFan |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP03 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP03_Motor | brick:Motor |  |  | rdfs:label_en | SSC_CHW_CHWP03 Motor
entity:SSC_CHW_CHWP03 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP03_Electrical_Meter | brick:Electrical_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP03 Electrical Meter
entity:SSC_CHW_CHWP03 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP03_Thermal_Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP03 Thermal Meter
entity:SSC_CHW_CHWP03 | brick:Chilled_Water_Booster_Pump | brick:hasPoint | entity:SSC_CHW_CHWP03_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration |  |  | rdfs:label_en | ScheduledPM Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP03 | brick:Chilled_Water_Booster_Pump | brick:hasPoint | entity:SSC_CHW_CHWP03_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration |  |  | rdfs:label_en | UnScheduled Outage Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP03 | brick:Chilled_Water_Booster_Pump | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | CHW Pump 03
entity:SSC_CHW_CHWP03 | brick:Chilled_Water_Booster_Pump | rec:feeds | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CHW_CHWP03 | brick:Chilled_Water_Booster_Pump | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_CHW_CHWP03 | brick:Chilled_Water_Booster_Pump | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_CHWP03 |  |  | ref:ifcName | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_Electrical_Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_CHW_CHWP03_Power_Sensor | brick:Power_Sensor |  |  | rdfs:label_en | Power |  |  | brick:hasUnit | unit:KiloW
entity:SSC_CHW_CHWP03_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP03_Speed_Command | brick:Speed_Command |  |  | rdfs:label_en | Speed Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_CHWP03_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP03_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_CHW_CHWP03_Power_Sensor | brick:Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.kW |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_Speed_Command | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.SpeedCmd |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.SpeedFbk |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_Thermal_Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_CHW_CHWP03_Thermal_Power_Sensor | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Thermal Load Fan |  |  | brick:hasUnit | para:KiloWt
entity:SSC_CHW_CHWP03_Thermal_Power_Sensor | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.ThermLoadFan |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP04 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP04_Motor | brick:Motor |  |  | rdfs:label_en | SSC_CHW_CHWP04 Motor
entity:SSC_CHW_CHWP04 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP04_Electrical_Meter | brick:Electrical_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP04 Electrical Meter
entity:SSC_CHW_CHWP04 | brick:Chilled_Water_Booster_Pump | brick:hasPart | entity:SSC_CHW_CHWP04_Thermal_Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP04 Thermal Meter
entity:SSC_CHW_CHWP04 | brick:Chilled_Water_Booster_Pump | brick:hasPoint | entity:SSC_CHW_CHWP04_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration |  |  | rdfs:label_en | ScheduledPM Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP04 | brick:Chilled_Water_Booster_Pump | brick:hasPoint | entity:SSC_CHW_CHWP04_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration |  |  | rdfs:label_en | UnScheduled Outage Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP04 | brick:Chilled_Water_Booster_Pump | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | CHW Pump 04
entity:SSC_CHW_CHWP04 | brick:Chilled_Water_Booster_Pump | rec:feeds | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_CHW_CHWP04 | brick:Chilled_Water_Booster_Pump | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_CHW_CHWP04 | brick:Chilled_Water_Booster_Pump | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_CHWP04 |  |  | ref:ifcName | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_Electrical_Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_CHW_CHWP04_Power_Sensor | brick:Power_Sensor |  |  | rdfs:label_en | Power |  |  | brick:hasUnit | unit:KiloW
entity:SSC_CHW_CHWP04_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP04_Speed_Command | brick:Speed_Command |  |  | rdfs:label_en | Speed Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_CHWP04_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP04_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_CHW_CHWP04_Power_Sensor | brick:Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.kW |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_Speed_Command | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.SpeedCmd |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.SpeedFbk |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_Thermal_Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_CHW_CHWP04_Thermal_Power_Sensor | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Thermal Load Fan |  |  | brick:hasUnit | para:KiloWt
entity:SSC_CHW_CHWP04_Thermal_Power_Sensor | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.ThermLoadFan |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_HE01 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE01_Return_Valve | brick:Valve |  |  | rdfs:label_en | Return Valve
entity:SSC_CHW_HE01 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve |  |  | rdfs:label_en | Supply Isolation Valve
entity:SSC_CHW_HE01 | brick:Heat_Exchanger | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | SSC CHW HE01
entity:SSC_CHW_HE01 | brick:Heat_Exchanger | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_CHW_HE01 | brick:Heat_Exchanger | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_HE01 |  |  | ref:ifcName | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPart | entity:SSC_CHW_HE01_Return_Valve_Motor | brick:Motor |  |  | rdfs:label_en | Motor
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Open_Close_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Open Close Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor |  |  | rdfs:label_en | Differential Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Position_Command | brick:Valve_Position_Command |  |  | rdfs:label_en | RTN Valve Position Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | RTN Valve Position |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | RTN Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_DiffPrs.PV |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Open_Close_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.OpenCloseSts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.PosFbk |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Position_Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.PosCmd |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Manual Auto Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Close_Command | para:Open_command |  |  | rdfs:label_en | Close Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Open_Command | para:Close_command |  |  | rdfs:label_en | Open Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Supply Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature Sensor |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CHW_HE01_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupIsoVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve_Close_Command | para:Open_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupIsoVlv.CloseCmd |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupIsoVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve_Open_Command | para:Close_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupIsoVlv.OpenCmd |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupIsoVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupTemp.PV |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE02 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE02_Return_Valve | brick:Valve |  |  | rdfs:label_en | Return Valve
entity:SSC_CHW_HE02 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve |  |  | rdfs:label_en | Supply Isolation Valve
entity:SSC_CHW_HE02 | brick:Heat_Exchanger | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | SSC CHW HE02
entity:SSC_CHW_HE02 | brick:Heat_Exchanger | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_CHW_HE02 | brick:Heat_Exchanger | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_HE02 |  |  | ref:ifcName | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPart | entity:SSC_CHW_HE02_Return_Valve_Motor | brick:Motor |  |  | rdfs:label_en | Motor
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Open_Close_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Open Close Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor |  |  | rdfs:label_en | Differential Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Position_Command | brick:Valve_Position_Command |  |  | rdfs:label_en | RTN Valve Position Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | RTN Valve Position |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | RTN Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_DiffPrs.PV |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Open_Close_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.OpenCloseSts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.PosFbk |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Position_Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.PosCmd |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Manual Auto Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Close_Command | para:Open_command |  |  | rdfs:label_en | Close Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Open_Command | para:Close_command |  |  | rdfs:label_en | Open Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Supply Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature Sensor |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CHW_HE02_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupIsoVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve_Close_Command | para:Open_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupIsoVlv.CloseCmd |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupIsoVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve_Open_Command | para:Close_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupIsoVlv.OpenCmd |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupIsoVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupTemp.PV |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE03 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE03_Return_Valve | brick:Valve |  |  | rdfs:label_en | Return Valve
entity:SSC_CHW_HE03 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve |  |  | rdfs:label_en | Supply Isolation Valve
entity:SSC_CHW_HE03 | brick:Heat_Exchanger | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | SSC CHW HE03
entity:SSC_CHW_HE03 | brick:Heat_Exchanger | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_CHW_HE03 | brick:Heat_Exchanger | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_HE03 |  |  | ref:ifcName | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPart | entity:SSC_CHW_HE03_Return_Valve_Motor | brick:Motor |  |  | rdfs:label_en | Motor
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Open_Close_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Open Close Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor |  |  | rdfs:label_en | Differential Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Position_Command | brick:Valve_Position_Command |  |  | rdfs:label_en | RTN Valve Position Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | RTN Valve Position |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | RTN Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_DiffPrs.PV |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Open_Close_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.OpenCloseSts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.PosFbk |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Position_Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.PosCmd |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Manual Auto Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Close_Command | para:Open_command |  |  | rdfs:label_en | Close Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Open_Command | para:Close_command |  |  | rdfs:label_en | Open Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Supply Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature Sensor |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CHW_HE03_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupIsoVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve_Close_Command | para:Open_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupIsoVlv.CloseCmd |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupIsoVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve_Open_Command | para:Close_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupIsoVlv.OpenCmd |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupIsoVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupTemp.PV |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE04 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE04_Return_Valve | brick:Valve |  |  | rdfs:label_en | Return Valve
entity:SSC_CHW_HE04 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve |  |  | rdfs:label_en | Supply Isolation Valve
entity:SSC_CHW_HE04 | brick:Heat_Exchanger | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | SSC CHW HE04
entity:SSC_CHW_HE04 | brick:Heat_Exchanger | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_CHW_HE04 | brick:Heat_Exchanger | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_HE04 |  |  | ref:ifcName | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPart | entity:SSC_CHW_HE04_Return_Valve_Motor | brick:Motor |  |  | rdfs:label_en | Motor
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Open_Close_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Open Close Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor |  |  | rdfs:label_en | Differential Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Position_Command | brick:Valve_Position_Command |  |  | rdfs:label_en | RTN Valve Position Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | RTN Valve Position |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | RTN Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_DiffPrs.PV |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Open_Close_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.OpenCloseSts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.PosFbk |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Position_Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.PosCmd |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Manual Auto Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Close_Command | para:Open_command |  |  | rdfs:label_en | Close Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Open_Command | para:Close_command |  |  | rdfs:label_en | Open Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Supply Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature Sensor |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CHW_HE04_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupIsoVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve_Close_Command | para:Open_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupIsoVlv.CloseCmd |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupIsoVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve_Open_Command | para:Close_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupIsoVlv.OpenCmd |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupIsoVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupTemp.PV |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE05 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE05_Return_Valve | brick:Valve |  |  | rdfs:label_en | Return Valve
entity:SSC_CHW_HE05 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE05_Supply_Valve | brick:Isolation_Valve |  |  | rdfs:label_en | Supply Isolation Valve
entity:SSC_CHW_HE05 | brick:Heat_Exchanger | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | SSC CHW HE05
entity:SSC_CHW_HE05 | brick:Heat_Exchanger | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_CHW_HE05 | brick:Heat_Exchanger | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_HE05 |  |  | ref:ifcName | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPart | entity:SSC_CHW_HE05_Return_Valve_Motor | brick:Motor |  |  | rdfs:label_en | Motor
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Open_Close_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Open Close Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor |  |  | rdfs:label_en | Differential Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Position_Command | brick:Valve_Position_Command |  |  | rdfs:label_en | RTN Valve Position Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | RTN Valve Position |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | RTN Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_DiffPrs.PV |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Open_Close_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.OpenCloseSts |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.PosFbk |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Position_Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.PosCmd |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE05_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature Sensor |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CHW_HE05_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_SupTemp.PV |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_DXB0001 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0001_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0001 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0001_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0001 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0001_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0001 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC DXB0001 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0001 | para:DXUnit | rec:locatedIn | entity:SSC_B1_005_UPS | rec:Room
entity:SSC_DXB0001 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0001 |  |  | ref:ifcName | SSC_DXB0001
entity:SSC_DXB0001_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0001.Alm |  |  | para:hasEntityId | SSC_DXB0001
entity:SSC_DXB0001_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0001.RunSts |  |  | para:hasEntityId | SSC_DXB0001
entity:SSC_DXB0001_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0001.SpcTemp |  |  | para:hasEntityId | SSC_DXB0001
entity:SSC_DXB0002 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0002_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0002 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0002_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0002 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0002_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0002 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC DXB0002 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0002 | para:DXUnit | rec:locatedIn | entity:SSC_B1_005_UPS | rec:Room
entity:SSC_DXB0002 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0002 |  |  | ref:ifcName | SSC_DXB0002
entity:SSC_DXB0002_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0002.Alm |  |  | para:hasEntityId | SSC_DXB0002
entity:SSC_DXB0002_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0002.RunSts |  |  | para:hasEntityId | SSC_DXB0002
entity:SSC_DXB0002_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0002.SpcTemp |  |  | para:hasEntityId | SSC_DXB0002
entity:SSC_DXB0003 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0003_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0003 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0003_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0003 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0003_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0003 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC DXB0003 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0003 | para:DXUnit | rec:locatedIn | entity:SSC_B1_005_UPS | rec:Room
entity:SSC_DXB0003 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0003 |  |  | ref:ifcName | SSC_DXB0003
entity:SSC_DXB0003_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0003.Alm |  |  | para:hasEntityId | SSC_DXB0003
entity:SSC_DXB0003_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0003.RunSts |  |  | para:hasEntityId | SSC_DXB0003
entity:SSC_DXB0003_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0003.SpcTemp |  |  | para:hasEntityId | SSC_DXB0003
entity:SSC_DXB0004 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0004_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0004 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0004_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0004 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0004_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0004 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC DXB0004 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0004 | para:DXUnit | rec:locatedIn | entity:SSC_B1_005_UPS | rec:Room
entity:SSC_DXB0004 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0004 |  |  | ref:ifcName | SSC_DXB0004
entity:SSC_DXB0004_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0004.Alm |  |  | para:hasEntityId | SSC_DXB0004
entity:SSC_DXB0004_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0004.RunSts |  |  | para:hasEntityId | SSC_DXB0004
entity:SSC_DXB0004_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0004.SpcTemp |  |  | para:hasEntityId | SSC_DXB0004
entity:SSC_DXB0005 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0005_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0005 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0005_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0005 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0005_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0005 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC DXB0005 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0005 | para:DXUnit | rec:locatedIn | entity:SSC_B1_004_MV_SWITCH_ROOM | rec:Room
entity:SSC_DXB0005 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0005 |  |  | ref:ifcName | SSC_DXB0005
entity:SSC_DXB0005_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0005.Alm |  |  | para:hasEntityId | SSC_DXB0005
entity:SSC_DXB0005_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0005.RunSts |  |  | para:hasEntityId | SSC_DXB0005
entity:SSC_DXB0005_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0005.SpcTemp |  |  | para:hasEntityId | SSC_DXB0005
entity:SSC_DXB0006 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0006_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0006 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0006_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0006 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0006_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0006 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC DXB0006 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0006 | para:DXUnit | rec:locatedIn | entity:SSC_B1_004_MV_SWITCH_ROOM | rec:Room
entity:SSC_DXB0006 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0006 |  |  | ref:ifcName | SSC_DXB0006
entity:SSC_DXB0006_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0006.Alm |  |  | para:hasEntityId | SSC_DXB0006
entity:SSC_DXB0006_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0006.RunSts |  |  | para:hasEntityId | SSC_DXB0006
entity:SSC_DXB0006_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0006.SpcTemp |  |  | para:hasEntityId | SSC_DXB0006
entity:SSC_DXB0007 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0007_Humidity_Sensor | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_DXB0007 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0007_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0007 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0007_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0007 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0007_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0007 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC DXB0007 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0007 | para:DXUnit | rec:locatedIn | entity:SSC_B1_019_FM_STORAGE | rec:Room
entity:SSC_DXB0007 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0007 |  |  | ref:ifcName | SSC_DXB0007
entity:SSC_DXB0007_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0007.Alm |  |  | para:hasEntityId | SSC_DXB0007
entity:SSC_DXB0007_Humidity_Sensor | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0007.Humidity |  |  | para:hasEntityId | SSC_DXB0007
entity:SSC_DXB0007_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0007.RunSts |  |  | para:hasEntityId | SSC_DXB0007
entity:SSC_DXB0007_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0007.SpcTemp |  |  | para:hasEntityId | SSC_DXB0007
entity:SSC_DXB0008 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0008_Humidity_Sensor | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_DXB0008 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0008_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0008 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0008_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0008 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0008_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0008 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC DXB0008 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0008 | para:DXUnit | rec:locatedIn | entity:SSC_B1_019_FM_STORAGE | rec:Room
entity:SSC_DXB0008 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0008 |  |  | ref:ifcName | SSC_DXB0008
entity:SSC_DXB0008_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0008.Alm |  |  | para:hasEntityId | SSC_DXB0008
entity:SSC_DXB0008_Humidity_Sensor | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0008.Humidity |  |  | para:hasEntityId | SSC_DXB0008
entity:SSC_DXB0008_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0008.RunSts |  |  | para:hasEntityId | SSC_DXB0008
entity:SSC_DXB0008_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0008.SpcTemp |  |  | para:hasEntityId | SSC_DXB0008
entity:SSC_DXB0009 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0009_Humidity_Sensor | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_DXB0009 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0009_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0009 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0009_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0009 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0009_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0009 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC DXB0009 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0009 | para:DXUnit | rec:locatedIn | entity:SSC_B1_020_FM_STORAGE | rec:Room
entity:SSC_DXB0009 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0009 |  |  | ref:ifcName | SSC_DXB0009
entity:SSC_DXB0009_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0009.Alm |  |  | para:hasEntityId | SSC_DXB0009
entity:SSC_DXB0009_Humidity_Sensor | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0009.Humidity |  |  | para:hasEntityId | SSC_DXB0009
entity:SSC_DXB0009_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0009.RunSts |  |  | para:hasEntityId | SSC_DXB0009
entity:SSC_DXB0009_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0009.SpcTemp |  |  | para:hasEntityId | SSC_DXB0009
entity:SSC_DXB0010 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0010_Humidity_Sensor | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_DXB0010 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0010_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0010 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0010_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0010 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0010_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0010 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC DXB0010 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0010 | para:DXUnit | rec:locatedIn | entity:SSC_B1_021_FM_STORAGE | rec:Room
entity:SSC_DXB0010 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0010 |  |  | ref:ifcName | SSC_DXB0010
entity:SSC_DXB0010_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0010.Alm |  |  | para:hasEntityId | SSC_DXB0010
entity:SSC_DXB0010_Humidity_Sensor | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0010.Humidity |  |  | para:hasEntityId | SSC_DXB0010
entity:SSC_DXB0010_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0010.RunSts |  |  | para:hasEntityId | SSC_DXB0010
entity:SSC_DXB0010_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0010.SpcTemp |  |  | para:hasEntityId | SSC_DXB0010
entity:SSC_DXB0001 | para:DXUnit | rec:feeds | entity:SSC_B1_005_UPS | rec:Room
entity:SSC_DXB0002 | para:DXUnit | rec:feeds | entity:SSC_B1_005_UPS | rec:Room
entity:SSC_DXB0003 | para:DXUnit | rec:feeds | entity:SSC_B1_005_UPS | rec:Room
entity:SSC_DXB0004 | para:DXUnit | rec:feeds | entity:SSC_B1_005_UPS | rec:Room
entity:SSC_DXB0005 | para:DXUnit | rec:feeds | entity:SSC_B1_004_MV_SWITCH_ROOM | rec:Room
entity:SSC_DXB0006 | para:DXUnit | rec:feeds | entity:SSC_B1_004_MV_SWITCH_ROOM | rec:Room
entity:SSC_DXB0007 | para:DXUnit | rec:feeds | entity:SSC_B1_019_FM_STORAGE | rec:Room
entity:SSC_DXB0008 | para:DXUnit | rec:feeds | entity:SSC_B1_019_FM_STORAGE | rec:Room
entity:SSC_DXB0009 | para:DXUnit | rec:feeds | entity:SSC_B1_020_FM_STORAGE | rec:Room
entity:SSC_DXB0010 | para:DXUnit | rec:feeds | entity:SSC_B1_021_FM_STORAGE | rec:Room
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0001_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0001_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0001_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC FCU0001 | rec:modelNumber | CPR173R4
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | rec:feeds | entity:SSC_B1_016_SPRINKLER_&_WATER | rec:Room
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_B1_016_SPRINKLER_&_WATER | rec:Room
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0001 |  |  | ref:ifcName | SSC_FCU0001
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0001_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 11.51 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0001_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0001_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0001_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0001_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0001_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0001_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0001_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0001_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0001_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0001_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.OccSts |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.RmTemp |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0001_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0001_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0001_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0001_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0001_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0001_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.StopCmd |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.TempCtrl |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.StartCmd |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0002_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0002_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0002_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC FCU0002 | rec:modelNumber | CPR173R4
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | rec:feeds | entity:SSC_B1_025_MAIN_SEC_CONTROL_ROOM | rec:Room
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_B1_025_MAIN_SEC_CONTROL_ROOM | rec:Room
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0002 |  |  | ref:ifcName | SSC_FCU0002
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0002_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.01 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0002_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0002_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0002_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0002_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0002_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0002_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0002_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0002_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0002_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0002_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.OccSts |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.RmTemp |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0002_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0002_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0002_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0002_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0002_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0002_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.StopCmd |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.TempCtrl |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.StartCmd |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0003_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0003_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0003_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC FCU0003 | rec:modelNumber | CPR173R4
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | rec:feeds | entity:SSC_B1_039_BMS | rec:Room
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_B1_039_BMS | rec:Room
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0003 |  |  | ref:ifcName | SSC_FCU0003
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0003_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 2 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0003_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0003_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0003_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0003_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0003_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0003_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0003_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0003_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0003_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0003_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.OccSts |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.RmTemp |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0003_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0003_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0003_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0003_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0003_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0003_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.StopCmd |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.TempCtrl |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.StartCmd |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0004_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0004_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0004_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC FCU0004 | rec:modelNumber | CPR173R4
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | rec:feeds | entity:SSC_01_008_AV_ROOM | rec:Room
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_008_AV_ROOM | rec:Room
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0004 |  |  | ref:ifcName | SSC_FCU0004
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0004_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 1.51 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0004_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0004_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0004_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0004_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0004_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0004_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0004_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0004_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0004_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0004_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.OccSts |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.RmTemp |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0004_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0004_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0004_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0004_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0004_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0004_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.StopCmd |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.TempCtrl |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.StartCmd |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0005_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0005_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0005_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC FCU0005 | rec:modelNumber | CPR173R4
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | rec:feeds | entity:SSC_01_027_IDF_1 | rec:Room
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_027_IDF_1 | rec:Room
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0005 |  |  | ref:ifcName | SSC_FCU0005
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0005_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 4.21 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0005_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0005_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0005_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0005_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0005_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0005_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0005_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0005_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0005_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0005_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.OccSts |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.RmTemp |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0005_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0005_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0005_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0005_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0005_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0005_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.StopCmd |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.TempCtrl |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.StartCmd |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0006_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0006_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0006_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0006_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC FCU0006 | rec:modelNumber | CPR173R4
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | rec:feeds | entity:SSC_01_027_IDF_1 | rec:Room
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_027_IDF_1 | rec:Room
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0006 |  |  | ref:ifcName | SSC_FCU0006
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0006_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 4.21 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0006_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0006_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0006_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0006_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0006_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0006_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0006_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0006_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0006_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0006_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0006_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.OccSts |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.RmTemp |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0006_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0006_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0006_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0006_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0006_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0006_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.StopCmd |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.TempCtrl |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.StartCmd |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0007_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0007_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0007_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0007_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC FCU0007 | rec:modelNumber | CPR173R4
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | rec:feeds | entity:SSC_01_039_IDF_2 | rec:Room
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_039_IDF_2 | rec:Room
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0007 |  |  | ref:ifcName | SSC_FCU0007
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0007_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 4.21 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0007_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0007_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0007_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0007_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0007_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0007_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0007_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0007_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0007_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0007_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0007_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.OccSts |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.RmTemp |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0007_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0007_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0007_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0007_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0007_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0007_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.StopCmd |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.TempCtrl |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.StartCmd |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0008_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0008_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0008_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0008_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC FCU0008 | rec:modelNumber | CPR173R4
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | rec:feeds | entity:SSC_01_039_IDF_2 | rec:Room
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_039_IDF_2 | rec:Room
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0008 |  |  | ref:ifcName | SSC_FCU0008
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0008_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 4.21 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0008_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0008_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0008_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0008_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0008_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0008_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0008_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0008_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0008_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0008_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0008_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.OccSts |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.RmTemp |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0008_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0008_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0008_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0008_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0008_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0008_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.StopCmd |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.TempCtrl |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.StartCmd |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0009_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0009_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0009_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0009_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC FCU0009 | rec:modelNumber | CPR173R4
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | rec:feeds | entity:SSC_01_028_CORRIDOR | rec:Room
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_028_CORRIDOR | rec:Room
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0009 |  |  | ref:ifcName | SSC_FCU0009
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0009_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 0.73 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0009_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0009_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0009_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0009_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0009_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0009_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0009_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0009_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0009_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0009_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0009_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.OccSts |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.RmTemp |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0009_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0009_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0009_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0009_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0009_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0009_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.StopCmd |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.TempCtrl |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.StartCmd |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0010_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0010_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0010_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0010_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC FCU0010 | rec:modelNumber | CPR173R4
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | rec:feeds | entity:SSC_01_010_CORRIDOR | rec:Room
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_010_CORRIDOR | rec:Room
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0010 |  |  | ref:ifcName | SSC_FCU0010
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0010_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 0.73 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0010_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0010_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0010_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0010_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0010_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0010_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0010_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0010_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0010_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0010_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0010_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.OccSts |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.RmTemp |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0010_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0010_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0010_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0010_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0010_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0010_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.StopCmd |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.TempCtrl |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.StartCmd |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0011_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0011_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0011_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0011_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC FCU0011 | rec:modelNumber | CPR173R4
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | rec:feeds | entity:SSC_03_033_PRINTING | rec:Room
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | rec:isFedBy | entity:CHWS-MAIN-LOOP | para:Chilled_Water_Loop_Network
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_03_033_PRINTING | rec:Room
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0011 |  |  | ref:ifcName | SSC_FCU0011
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0011_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 2.01 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0011_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0011_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0011_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0011_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0011_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0011_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0011_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0011_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0011_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0011_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0011_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.OccSts |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.RmTemp |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0011_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0011_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0011_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0011_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0011_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0011_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.StopCmd |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.TempCtrl |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.StartCmd |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_GEFB0001 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_GEFB0001_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_GEFB0001 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_GEFB0001_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_GEFB0001 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_GEFB0001_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_GEFB0001 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC GEFB0001 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_GEFB0001 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_GEFB0001 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_GEFB0001 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_GEFB0001 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_GEFB0001 |  |  | ref:ifcName | SSC_GEFB0001
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Auto_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Exhaust_Fan_in_Auto_Mode | brick:Mode_Command |  |  | rdfs:label_en | Exhaust Fan in Auto Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Exhaust_Fan_Healthy | brick:Status |  |  | rdfs:label_en | Exhaust Fan Healthy (For Internal Use Only) |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Running_Status | brick:On_Off_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.AutoCmd |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Auto_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.AutoManCmdSts |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.AutoManSts |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Exhaust_Fan_Healthy | brick:Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.iEFSts |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Exhaust_Fan_in_Auto_Mode | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.EFAutoMode |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.ManCmd |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Running_Status | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.RunSts |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.StartCmd |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.StopCmd |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.TripAlm |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_KEF0103_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_KEF0103_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0103_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0103_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0103_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0103_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC KEF0103 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC KEF0103 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_KEF0103 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_KEF0103 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_KEF0103 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_KEF0103 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_KEF0103 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_KEF0103 |  |  | ref:ifcName | SSC_KEF0103
entity:SSC_KEF0103 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_KEF0103 |  |  | ref:ifcName | SSC_KEF0103
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Running_Status | brick:On_Off_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Running_Status | brick:On_Off_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.AutoCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.AutoCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.AutoManSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.AutoManSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.LocSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.LocSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.ManCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.ManCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Running_Status | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.RunSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Running_Status | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.RunSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.StartCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.StartCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.StopCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.StopCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.TripAlm |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.TripAlm |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_KEF0303_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_KEF0303_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0303_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0303_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0303_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0303_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC KEF0303 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC KEF0303 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_KEF0303 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_KEF0303 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_KEF0303 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_KEF0303 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_KEF0303 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_KEF0303 |  |  | ref:ifcName | SSC_KEF0303
entity:SSC_KEF0303 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_KEF0303 |  |  | ref:ifcName | SSC_KEF0303
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Running_Status | brick:On_Off_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Running_Status | brick:On_Off_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.AutoCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.AutoCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.AutoManSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.AutoManSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.LocSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.LocSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.ManCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.ManCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Running_Status | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.RunSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Running_Status | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.RunSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.StartCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.StartCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.StopCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.StopCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.TripAlm |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.TripAlm |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_Level-01 | rec:Level | rec:isPartOf | entity:SSC | rec:Building | rdfs:label_en | Level 01
entity:SSC_Level-02 | rec:Level | rec:isPartOf | entity:SSC | rec:Building | rdfs:label_en | Level 02
entity:SSC_Level-03 | rec:Level | rec:isPartOf | entity:SSC | rec:Building | rdfs:label_en | Level 03
entity:SSC_Level-B1 | rec:BasementLevel | rec:isPartOf | entity:SSC | rec:Building | rdfs:label_en | Basement 01
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Battery_Voltage | brick:Battery_Voltage_Sensor |  |  | rdfs:label_en | Battery Voltage |  |  | brick:hasUnit | unit:V
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Current_Reading | brick:Current_Sensor |  |  | rdfs:label_en | Current Reading |  |  | brick:hasUnit | unit:A
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Engine_Oil_Pressure_Reading | brick:Pressure_Sensor |  |  | rdfs:label_en | Engine Oil Pressure Reading |  |  | brick:hasUnit | unit:PA
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Frequency_Reading | brick:Frequency_Sensor |  |  | rdfs:label_en | Frequency Reading |  |  | brick:hasUnit | unit:HZ
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Apparent_Power | brick:Apparent_Power_Sensor |  |  | rdfs:label_en | Apparent Power |  |  | brick:hasUnit | unit:KVA
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Active_Power | brick:Active_Power_Sensor |  |  | rdfs:label_en | Active Power |  |  | brick:hasUnit | unit:KiloW
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Energy | brick:Energy_Sensor |  |  | rdfs:label_en | Energy |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Generator_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Generator Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Runtime_Meter | brick:Duration_Sensor |  |  | rdfs:label_en | Runtime Meter |  |  | brick:hasUnit | unit:HR
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Voltage | brick:Voltage_Sensor |  |  | rdfs:label_en | Voltage |  |  | brick:hasUnit | unit:V
entity:SSC_MV_Generator | para:Generator | brick:isPartOf | entity:Electrical_System | brick:System | rdfs:label_en | SSC_MV_Generator
entity:SSC_MV_Generator | para:Generator | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value |  |  |  | brick:hasUnit | unit:HZ
entity:SSC_MV_Generator | para:Generator | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value |  |  |  | brick:hasUnit | unit:KVA
entity:SSC_MV_Generator | para:Generator | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value |  |  |  | brick:hasUnit | unit:V
entity:SSC_MV_Generator | para:Generator | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_MV_Generator |  |  | ref:ifcName | SSC_MV_Generator
entity:SSC_MV_Generator_Active_Power | brick:Active_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.kW |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Apparent_Power | brick:Apparent_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.kVA |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Battery_Voltage | brick:Battery_Voltage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.BattVoltage |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Current_Reading | brick:Current_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.Current |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Energy | brick:Energy_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.kWh |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Engine_Oil_Pressure_Reading | brick:Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.EngOilPrs |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Frequency_Reading | brick:Frequency_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.Frequency |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Generator_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.RunSts |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Runtime_Meter | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.RuntimeMtr |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Voltage | brick:Voltage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.Voltage |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_ST-10_STAIR-10 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | ST-10 STAIR-10
entity:SSC_TEF0101 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_TEF0101_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_TEF0101 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0101_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0101 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0101_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0101 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC TEF0101 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_TEF0101 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_TEF0101 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_TEF0101 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_TEF0101 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_TEF0101 |  |  | ref:ifcName | SSC_TEF0101
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_PDSL_OnOff_Status | brick:Status |  |  | rdfs:label_en | PDSL On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Running_Status | brick:Fan_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.AutoCmd |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.AutoManSts |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.LocSts |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.ManCmd |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_PDSL_OnOff_Status | brick:Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101_PDSL.OnOffSts |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101_RtnAirPrsSW.Alm |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Running_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.RunSts |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.StartCmd |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.StopCmd |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.TripAlm |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0102 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_TEF0102_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_TEF0102 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0102_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0102 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0102_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0102 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC TEF0102 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_TEF0102 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_TEF0102 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_TEF0102 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_TEF0102 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_TEF0102 |  |  | ref:ifcName | SSC_TEF0102
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_PDSL_OnOff_Status | brick:Status |  |  | rdfs:label_en | PDSL On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Running_Status | brick:Fan_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.AutoCmd |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.AutoManSts |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.LocSts |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.ManCmd |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_PDSL_OnOff_Status | brick:Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102_PDSL.OnOffSts |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102_RtnAirPrsSW.Alm |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Running_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.RunSts |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.StartCmd |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.StopCmd |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.TripAlm |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0301 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_TEF0301_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_TEF0301 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0301_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0301 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0301_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0301 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC TEF0301 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_TEF0301 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_TEF0301 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_TEF0301 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_TEF0301 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_TEF0301 |  |  | ref:ifcName | SSC_TEF0301
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_PDSL_OnOff_Status | brick:Status |  |  | rdfs:label_en | PDSL On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Running_Status | brick:Fan_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.AutoCmd |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.AutoManSts |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.LocSts |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.ManCmd |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_PDSL_OnOff_Status | brick:Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301_PDSL.OnOffSts |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301_RtnAirPrsSW.Alm |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Running_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.RunSts |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.StartCmd |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.StopCmd |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.TripAlm |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0302 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_TEF0302_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_TEF0302 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0302_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0302 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0302_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0302 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC TEF0302 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_TEF0302 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_TEF0302 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_TEF0302 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_TEF0302 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_TEF0302 |  |  | ref:ifcName | SSC_TEF0302
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_PDSL_OnOff_Status | brick:Status |  |  | rdfs:label_en | PDSL On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Running_Status | brick:Fan_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.AutoCmd |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.AutoManSts |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.LocSts |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.ManCmd |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_PDSL_OnOff_Status | brick:Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302_PDSL.OnOffSts |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302_RtnAirPrsSW.Alm |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Running_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.RunSts |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.StartCmd |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.StopCmd |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.TripAlm |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0001_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 140 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0001 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_B1_015_ENTRANCE | rec:Room
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0001 |  |  | ref:ifcName | SSC_VAV0001
entity:SSC_VAV0001_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.AirFlow |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0001_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0001_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.DmprPos |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.OccSts |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.RmTemp |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.SP |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0002_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0002 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_014_SHELL_SPACE | rec:Room
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0002 |  |  | ref:ifcName | SSC_VAV0002
entity:SSC_VAV0002_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.AirFlow |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0002_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0002_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.DmprPos |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.OccSts |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.RmTemp |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.SP |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0003_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0003 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_014_SHELL_SPACE | rec:Room
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0003 |  |  | ref:ifcName | SSC_VAV0003
entity:SSC_VAV0003_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.AirFlow |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0003_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0003_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.DmprPos |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.OccSts |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.RmTemp |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.SP |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0004_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0004 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_014_SHELL_SPACE | rec:Room
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0004 |  |  | ref:ifcName | SSC_VAV0004
entity:SSC_VAV0004_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.AirFlow |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0004_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0004_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.DmprPos |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.OccSts |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.RmTemp |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.SP |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0005_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 205 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0005 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_015_SHELL_SPACE | rec:Room
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0005 |  |  | ref:ifcName | SSC_VAV0005
entity:SSC_VAV0005_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.AirFlow |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0005_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0005_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.DmprPos |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.OccSts |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.RmTemp |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.SP |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0006_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 205 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0006 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_015_SHELL_SPACE | rec:Room
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0006 |  |  | ref:ifcName | SSC_VAV0006
entity:SSC_VAV0006_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.AirFlow |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0006_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0006_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.DmprPos |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.OccSts |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.RmTemp |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.SP |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0007_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 205 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0007 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_015_SHELL_SPACE | rec:Room
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0007 |  |  | ref:ifcName | SSC_VAV0007
entity:SSC_VAV0007_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.AirFlow |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0007_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0007_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.DmprPos |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.OccSts |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.RmTemp |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.SP |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0008_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 30 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0008 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 3 |  |  | para:inletSize | 198 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_024_CORRIDOR | rec:Room
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0008 |  |  | ref:ifcName | SSC_VAV0008
entity:SSC_VAV0008_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.AirFlow |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0008_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0008_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.DmprPos |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.OccSts |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.RmTemp |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.SP |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0009_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0009 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 3 |  |  | para:inletSize | 198 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0009 |  |  | ref:ifcName | SSC_VAV0009
entity:SSC_VAV0009_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.AirFlow |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0009_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0009_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.DmprPos |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.OccSts |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.RmTemp |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.SP |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0010_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0010 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 3 |  |  | para:inletSize | 198 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0010 |  |  | ref:ifcName | SSC_VAV0010
entity:SSC_VAV0010_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.AirFlow |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0010_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0010_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.DmprPos |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.OccSts |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.RmTemp |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.SP |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0011_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0011 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 3 |  |  | para:inletSize | 198 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0011 |  |  | ref:ifcName | SSC_VAV0011
entity:SSC_VAV0011_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.AirFlow |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0011_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0011_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.DmprPos |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.OccSts |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.RmTemp |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.SP |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0012_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0012 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 3 |  |  | para:inletSize | 198 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0012 |  |  | ref:ifcName | SSC_VAV0012
entity:SSC_VAV0012_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.AirFlow |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0012_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0012_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.DmprPos |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.OccSts |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.RmTemp |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.SP |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0013_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0013 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 3 |  |  | para:inletSize | 198 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0013 |  |  | ref:ifcName | SSC_VAV0013
entity:SSC_VAV0013_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.AirFlow |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0013_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0013_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.DmprPos |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.OccSts |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.RmTemp |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.SP |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0014_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0014 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0014 |  |  | ref:ifcName | SSC_VAV0014
entity:SSC_VAV0014_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.AirFlow |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0014_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0014_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.DmprPos |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.OccSts |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.RmTemp |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.SP |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0015_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 185 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0015 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_ROOM_NO_42 | rec:Room
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0015 |  |  | ref:ifcName | SSC_VAV0015
entity:SSC_VAV0015_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.AirFlow |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0015_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0015_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.DmprPos |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.OccSts |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.RmTemp |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.SP |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0016_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 185 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0016 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_ROOM_NO_43 | rec:Room
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0016 |  |  | ref:ifcName | SSC_VAV0016
entity:SSC_VAV0016_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.AirFlow |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0016_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0016_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.DmprPos |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.OccSts |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.RmTemp |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.SP |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0017_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 185 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0017 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_ROOM_NO_44 | rec:Room
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0017 |  |  | ref:ifcName | SSC_VAV0017
entity:SSC_VAV0017_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.AirFlow |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0017_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0017_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.DmprPos |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.OccSts |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.RmTemp |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.SP |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0018_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 185 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0018 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_SHELL_SPACE | rec:Room
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0018 |  |  | ref:ifcName | SSC_VAV0018
entity:SSC_VAV0018_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.AirFlow |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0018_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0018_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.DmprPos |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.OccSts |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.RmTemp |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.SP |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0019_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 185 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0019 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_SHELL_SPACE | rec:Room
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0019 |  |  | ref:ifcName | SSC_VAV0019
entity:SSC_VAV0019_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.AirFlow |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0019_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0019_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.DmprPos |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.OccSts |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.RmTemp |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.SP |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0020_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 185 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0020 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_SHELL_SPACE | rec:Room
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0020 |  |  | ref:ifcName | SSC_VAV0020
entity:SSC_VAV0020_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.AirFlow |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0020_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0020_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.DmprPos |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.OccSts |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.RmTemp |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.SP |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0021_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 3 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 110 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0021 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 5 |  |  | para:inletSize | 313 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_013_CORRIDOR | rec:Room
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0021 |  |  | ref:ifcName | SSC_VAV0021
entity:SSC_VAV0021_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.AirFlow |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0021_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0021_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.DmprPos |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.OccSts |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.RmTemp |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.SP |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0022_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 3 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 540 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0022 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 5 |  |  | para:inletSize | 313 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_003_OPEN_SPACE | rec:Room
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0022 |  |  | ref:ifcName | SSC_VAV0022
entity:SSC_VAV0022_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.AirFlow |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0022_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0022_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.DmprPos |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.OccSts |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.RmTemp |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.SP |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0023_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 540 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0023 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_003_OPEN_SPACE | rec:Room
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0023 |  |  | ref:ifcName | SSC_VAV0023
entity:SSC_VAV0023_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.AirFlow |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0023_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0023_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.DmprPos |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.OccSts |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.RmTemp |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.SP |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0024_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 3 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 55 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0024 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 5 |  |  | para:inletSize | 313 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_001_CORRIDOR | rec:Room
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0024 |  |  | ref:ifcName | SSC_VAV0024
entity:SSC_VAV0024_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.AirFlow |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0024_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0024_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.DmprPos |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.OccSts |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.RmTemp |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.SP |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0025_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0025 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_002_SHELL_SPACE | rec:Room
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0025 |  |  | ref:ifcName | SSC_VAV0025
entity:SSC_VAV0025_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.AirFlow |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0025_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0025_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.DmprPos |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.OccSts |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.RmTemp |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.SP |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0026_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0026 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_002_SHELL_SPACE | rec:Room
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0026 |  |  | ref:ifcName | SSC_VAV0026
entity:SSC_VAV0026_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.AirFlow |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0026_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0026_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.DmprPos |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.OccSts |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.RmTemp |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.SP |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0027_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 3 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0027 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 5 |  |  | para:inletSize | 313 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_002_SHELL_SPACE | rec:Room
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0027 |  |  | ref:ifcName | SSC_VAV0027
entity:SSC_VAV0027_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.AirFlow |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0027_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0027_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.DmprPos |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.OccSts |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.RmTemp |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.SP |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0028_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0028 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_002_SHELL_SPACE | rec:Room
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0028 |  |  | ref:ifcName | SSC_VAV0028
entity:SSC_VAV0028_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.AirFlow |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0028_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0028_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.DmprPos |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.OccSts |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.RmTemp |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.SP |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0029_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 55 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0029 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_001_CORRIDOR | rec:Room
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0029 |  |  | ref:ifcName | SSC_VAV0029
entity:SSC_VAV0029_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.AirFlow |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0029_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0029_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.DmprPos |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.OccSts |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.RmTemp |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.SP |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0030_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 95 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0030 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_016_SHELL_SPACE | rec:Room
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0030 |  |  | ref:ifcName | SSC_VAV0030
entity:SSC_VAV0030_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.AirFlow |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0030_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0030_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.DmprPos |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.OccSts |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.RmTemp |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.SP |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0031_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 55 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0031 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_001_CORRIDOR | rec:Room
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0031 |  |  | ref:ifcName | SSC_VAV0031
entity:SSC_VAV0031_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.AirFlow |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0031_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0031_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.DmprPos |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.OccSts |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.RmTemp |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.SP |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0032_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 30 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0032 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_018_CORRIDOR | rec:Room
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0032 |  |  | ref:ifcName | SSC_VAV0032
entity:SSC_VAV0032_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.AirFlow |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0032_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0032_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.DmprPos |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.OccSts |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.RmTemp |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.SP |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0033_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 110 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0033 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_028_CORRIDOR | rec:Room
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0033 |  |  | ref:ifcName | SSC_VAV0033
entity:SSC_VAV0033_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.AirFlow |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0033_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0033_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.DmprPos |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.OccSts |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.RmTemp |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.SP |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0034_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 540 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0034 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_003_OPEN_SPACE | rec:Room
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0034 |  |  | ref:ifcName | SSC_VAV0034
entity:SSC_VAV0034_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.AirFlow |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0034_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0034_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.DmprPos |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.OccSts |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.RmTemp |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.SP |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0035_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 60 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0035 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_010_CORRIDOR | rec:Room
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0035 |  |  | ref:ifcName | SSC_VAV0035
entity:SSC_VAV0035_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.AirFlow |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0035_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0035_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.DmprPos |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.OccSts |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.RmTemp |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.SP |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0036_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 125 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0036 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_022_ABLUTION_ROOM | rec:Room
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0036 |  |  | ref:ifcName | SSC_VAV0036
entity:SSC_VAV0036_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.AirFlow |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0036_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0036_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.DmprPos |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.OccSts |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.RmTemp |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.SP |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0037_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 25 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0037 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_008_AV_ROOM | rec:Room
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0037 |  |  | ref:ifcName | SSC_VAV0037
entity:SSC_VAV0037_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.AirFlow |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0037_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0037_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.DmprPos |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.OccSts |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.RmTemp |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.SP |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0038_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 330 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0038 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_ST-4_STAIR_4 | rec:Room
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0038 |  |  | ref:ifcName | SSC_VAV0038
entity:SSC_VAV0038_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.AirFlow |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0038_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0038_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.DmprPos |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.OccSts |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.RmTemp |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.SP |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0039_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 3 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 540 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0039 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 5 |  |  | para:inletSize | 313 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_003_OPEN_SPACE | rec:Room
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0039 |  |  | ref:ifcName | SSC_VAV0039
entity:SSC_VAV0039_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.AirFlow |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0039_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0039_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.DmprPos |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.OccSts |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.RmTemp |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.SP |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0040_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 325 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0040 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_006_CONFERENCE_ROOM | rec:Room
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0040 |  |  | ref:ifcName | SSC_VAV0040
entity:SSC_VAV0040_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.AirFlow |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0040_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0040_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.DmprPos |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.OccSts |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.RmTemp |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.SP |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0041_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 300 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0041 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | rec:Room
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0041 |  |  | ref:ifcName | SSC_VAV0041
entity:SSC_VAV0041_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.AirFlow |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0041_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0041_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.DmprPos |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.OccSts |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.RmTemp |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.SP |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0042_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 300 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0042 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | rec:Room
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0042 |  |  | ref:ifcName | SSC_VAV0042
entity:SSC_VAV0042_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.AirFlow |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0042_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0042_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.DmprPos |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.OccSts |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.RmTemp |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.SP |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0043_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 3 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 385 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0043 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 5 |  |  | para:inletSize | 313 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_004_CORRIDOR | rec:Room
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0043 |  |  | ref:ifcName | SSC_VAV0043
entity:SSC_VAV0043_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.AirFlow |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0043_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0043_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.DmprPos |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.OccSts |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.RmTemp |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.SP |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0044_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 3 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 505 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0044 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 5 |  |  | para:inletSize | 313 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_001_FOYER | rec:Room
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0044 |  |  | ref:ifcName | SSC_VAV0044
entity:SSC_VAV0044_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.AirFlow |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0044_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0044_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.DmprPos |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.OccSts |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.RmTemp |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.SP |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0045_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 505 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0045 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_001_FOYER | rec:Room
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0045 |  |  | ref:ifcName | SSC_VAV0045
entity:SSC_VAV0045_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.AirFlow |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0045_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0045_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.DmprPos |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.OccSts |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.RmTemp |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.SP |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0046_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 320 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0046 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_002_LOBBY | rec:Room
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0046 |  |  | ref:ifcName | SSC_VAV0046
entity:SSC_VAV0046_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.AirFlow |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0046_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0046_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.DmprPos |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.OccSts |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.RmTemp |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.SP |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0047_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 320 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0047 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_002_LOBBY | rec:Room
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0047 |  |  | ref:ifcName | SSC_VAV0047
entity:SSC_VAV0047_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.AirFlow |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0047_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0047_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.DmprPos |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.OccSts |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.RmTemp |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.SP |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0048_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 320 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0048 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_002_LOBBY | rec:Room
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0048 |  |  | ref:ifcName | SSC_VAV0048
entity:SSC_VAV0048_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.AirFlow |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0048_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0048_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.DmprPos |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.OccSts |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.RmTemp |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.SP |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0049_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 320 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0049 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_002_LOBBY | rec:Room
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0049 |  |  | ref:ifcName | SSC_VAV0049
entity:SSC_VAV0049_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.AirFlow |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0049_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0049_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.DmprPos |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.OccSts |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.RmTemp |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.SP |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0050_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 320 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0050 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_003_CORRIDOR | rec:Room
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0050 |  |  | ref:ifcName | SSC_VAV0050
entity:SSC_VAV0050_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.AirFlow |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0050_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0050_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.DmprPos |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.OccSts |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.RmTemp |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.SP |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0051_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 3 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 300 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0051 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 5 |  |  | para:inletSize | 313 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | rec:Room
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0051 |  |  | ref:ifcName | SSC_VAV0051
entity:SSC_VAV0051_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.AirFlow |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0051_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0051_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.DmprPos |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.OccSts |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.RmTemp |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.SP |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0052_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 325 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0052 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_006_CONFERENCE_ROOM | rec:Room
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0052 |  |  | ref:ifcName | SSC_VAV0052
entity:SSC_VAV0052_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.AirFlow |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0052_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0052_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.DmprPos |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.OccSts |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.RmTemp |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.SP |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0053_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 225 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0053 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_015_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0053 |  |  | ref:ifcName | SSC_VAV0053
entity:SSC_VAV0053_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.AirFlow |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0053_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0053_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.DmprPos |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.OccSts |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.RmTemp |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.SP |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0054_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 105 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0054 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_014_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0054 |  |  | ref:ifcName | SSC_VAV0054
entity:SSC_VAV0054_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.AirFlow |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0054_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0054_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.DmprPos |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.OccSts |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.RmTemp |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.SP |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0055_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 135 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0055 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_013_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0055 |  |  | ref:ifcName | SSC_VAV0055
entity:SSC_VAV0055_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.AirFlow |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0055_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0055_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.DmprPos |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.OccSts |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.RmTemp |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.SP |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0056_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 135 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0056 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_012_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0056 |  |  | ref:ifcName | SSC_VAV0056
entity:SSC_VAV0056_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.AirFlow |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0056_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0056_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.DmprPos |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.OccSts |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.RmTemp |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.SP |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0057_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 105 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0057 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_011_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0057 |  |  | ref:ifcName | SSC_VAV0057
entity:SSC_VAV0057_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.AirFlow |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0057_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0057_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.DmprPos |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.OccSts |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.RmTemp |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.SP |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0058_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 135 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0058 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_010_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0058 |  |  | ref:ifcName | SSC_VAV0058
entity:SSC_VAV0058_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.AirFlow |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0058_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0058_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.DmprPos |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.OccSts |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.RmTemp |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.SP |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0059_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 135 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0059 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_009_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0059 |  |  | ref:ifcName | SSC_VAV0059
entity:SSC_VAV0059_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.AirFlow |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0059_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0059_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.DmprPos |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.OccSts |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.RmTemp |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.SP |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0060_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 105 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0060 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_008_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0060 |  |  | ref:ifcName | SSC_VAV0060
entity:SSC_VAV0060_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.AirFlow |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0060_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0060_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.DmprPos |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.OccSts |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.RmTemp |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.SP |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0061_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 135 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0061 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_007_OPERATIONS_MANAGER | rec:Room
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0061 |  |  | ref:ifcName | SSC_VAV0061
entity:SSC_VAV0061_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.AirFlow |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0061_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0061_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.DmprPos |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.OccSts |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.RmTemp |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.SP |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0062_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 335 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0062 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_006_MEETING_ROOM | rec:Room
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0062 |  |  | ref:ifcName | SSC_VAV0062
entity:SSC_VAV0062_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.AirFlow |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0062_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0062_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.DmprPos |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.OccSts |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.RmTemp |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.SP |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0063_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 335 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0063 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | rec:locatedIn | #N/A | rec:Room
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0063 |  |  | ref:ifcName | SSC_VAV0063
entity:SSC_VAV0063_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.AirFlow |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0063_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0063_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.DmprPos |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.OccSts |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.RmTemp |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.SP |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0064_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 335 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0064 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_006_MEETING_ROOM | rec:Room
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0064 |  |  | ref:ifcName | SSC_VAV0064
entity:SSC_VAV0064_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.AirFlow |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0064_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0064_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.DmprPos |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.OccSts |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.RmTemp |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.SP |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0065_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 130 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0065 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_005_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0065 |  |  | ref:ifcName | SSC_VAV0065
entity:SSC_VAV0065_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.AirFlow |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0065_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0065_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.DmprPos |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.OccSts |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.RmTemp |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.SP |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0066_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 130 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0066 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_004_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0066 |  |  | ref:ifcName | SSC_VAV0066
entity:SSC_VAV0066_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.AirFlow |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0066_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0066_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.DmprPos |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.OccSts |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.RmTemp |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.SP |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0067_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 130 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0067 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_003_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0067 |  |  | ref:ifcName | SSC_VAV0067
entity:SSC_VAV0067_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.AirFlow |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0067_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0067_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.DmprPos |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.OccSts |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.RmTemp |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.SP |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0068_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0068 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0068 |  |  | ref:ifcName | SSC_VAV0068
entity:SSC_VAV0068_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.AirFlow |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0068_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0068_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.DmprPos |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.OccSts |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.RmTemp |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.SP |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0069_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0069 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 3 |  |  | para:inletSize | 198 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0069 |  |  | ref:ifcName | SSC_VAV0069
entity:SSC_VAV0069_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.AirFlow |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0069_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0069_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.DmprPos |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.OccSts |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.RmTemp |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.SP |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0070_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 330 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0070 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_001_DIRECTORS_OFFICE | rec:Room
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0070 |  |  | ref:ifcName | SSC_VAV0070
entity:SSC_VAV0070_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.AirFlow |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0070_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0070_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.DmprPos |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.OccSts |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.RmTemp |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.SP |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0071_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0071 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0071 |  |  | ref:ifcName | SSC_VAV0071
entity:SSC_VAV0071_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.AirFlow |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0071_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0071_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.DmprPos |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.OccSts |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.RmTemp |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.SP |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0072_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0072 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0072 |  |  | ref:ifcName | SSC_VAV0072
entity:SSC_VAV0072_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.AirFlow |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0072_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0072_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.DmprPos |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.OccSts |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.RmTemp |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.SP |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0073_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0073 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0073 |  |  | ref:ifcName | SSC_VAV0073
entity:SSC_VAV0073_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.AirFlow |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0073_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0073_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.DmprPos |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.OccSts |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.RmTemp |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.SP |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0074_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0074 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0074 |  |  | ref:ifcName | SSC_VAV0074
entity:SSC_VAV0074_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.AirFlow |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0074_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0074_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.DmprPos |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.OccSts |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.RmTemp |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.SP |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0075_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0075 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0075 |  |  | ref:ifcName | SSC_VAV0075
entity:SSC_VAV0075_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.AirFlow |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0075_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0075_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.DmprPos |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.OccSts |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.RmTemp |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.SP |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0076_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0076 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0076 |  |  | ref:ifcName | SSC_VAV0076
entity:SSC_VAV0076_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.AirFlow |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0076_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0076_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.DmprPos |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.OccSts |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.RmTemp |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.SP |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0077_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0077 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 3 |  |  | para:inletSize | 198 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0077 |  |  | ref:ifcName | SSC_VAV0077
entity:SSC_VAV0077_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.AirFlow |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0077_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0077_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.DmprPos |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.OccSts |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.RmTemp |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.SP |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0078_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 320 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0078 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_031_ASSOC_DIRECTORS_OFFICE | rec:Room
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0078 |  |  | ref:ifcName | SSC_VAV0078
entity:SSC_VAV0078_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.AirFlow |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0078_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0078_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.DmprPos |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.OccSts |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.RmTemp |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.SP |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0079_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0079 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_030_ASSOC_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0079 |  |  | ref:ifcName | SSC_VAV0079
entity:SSC_VAV0079_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.AirFlow |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0079_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0079_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.DmprPos |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.OccSts |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.RmTemp |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.SP |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0080_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 170 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0080 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_030_ASSOC_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0080 |  |  | ref:ifcName | SSC_VAV0080
entity:SSC_VAV0080_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.AirFlow |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0080_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0080_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.DmprPos |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.OccSts |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.RmTemp |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.SP |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0081_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 140 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0081 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_029_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0081 |  |  | ref:ifcName | SSC_VAV0081
entity:SSC_VAV0081_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.AirFlow |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0081_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0081_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.DmprPos |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.OccSts |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.RmTemp |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.SP |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0082_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 110 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0082 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_028_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0082 |  |  | ref:ifcName | SSC_VAV0082
entity:SSC_VAV0082_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.AirFlow |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0082_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0082_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.DmprPos |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.OccSts |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.RmTemp |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.SP |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0083_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 140 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0083 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_027_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0083 |  |  | ref:ifcName | SSC_VAV0083
entity:SSC_VAV0083_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.AirFlow |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0083_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0083_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.DmprPos |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.OccSts |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.RmTemp |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.SP |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0084_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 265 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0084 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_026_MEETING_ROOM | rec:Room
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0084 |  |  | ref:ifcName | SSC_VAV0084
entity:SSC_VAV0084_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.AirFlow |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0084_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0084_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.DmprPos |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.OccSts |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.RmTemp |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.SP |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0085_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 265 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0085 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_026_MEETING_ROOM | rec:Room
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0085 |  |  | ref:ifcName | SSC_VAV0085
entity:SSC_VAV0085_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.AirFlow |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0085_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0085_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.DmprPos |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.OccSts |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.RmTemp |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.SP |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0086_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 265 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0086 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_026_MEETING_ROOM | rec:Room
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0086 |  |  | ref:ifcName | SSC_VAV0086
entity:SSC_VAV0086_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.AirFlow |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0086_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0086_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.DmprPos |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.OccSts |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.RmTemp |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.SP |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0087_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 140 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0087 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_025_SECRETARIAL_AREA | rec:Room
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0087 |  |  | ref:ifcName | SSC_VAV0087
entity:SSC_VAV0087_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.AirFlow |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0087_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0087_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.DmprPos |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.OccSts |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.RmTemp |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.SP |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0088_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 120 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0088 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_024_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0088 |  |  | ref:ifcName | SSC_VAV0088
entity:SSC_VAV0088_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.AirFlow |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0088_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0088_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.DmprPos |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.OccSts |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.RmTemp |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.SP |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0089_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 140 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0089 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_023_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0089 |  |  | ref:ifcName | SSC_VAV0089
entity:SSC_VAV0089_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.AirFlow |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0089_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0089_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.DmprPos |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.OccSts |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.RmTemp |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.SP |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0090_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 140 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0090 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_022_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0090 |  |  | ref:ifcName | SSC_VAV0090
entity:SSC_VAV0090_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.AirFlow |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0090_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0090_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.DmprPos |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.OccSts |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.RmTemp |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.SP |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0091_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 120 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0091 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_021_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0091 |  |  | ref:ifcName | SSC_VAV0091
entity:SSC_VAV0091_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.AirFlow |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0091_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0091_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.DmprPos |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.OccSts |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.RmTemp |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.SP |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0092_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 140 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0092 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_020_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0092 |  |  | ref:ifcName | SSC_VAV0092
entity:SSC_VAV0092_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.AirFlow |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0092_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0092_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.DmprPos |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.OccSts |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.RmTemp |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.SP |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0093_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 125 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0093 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_019_IT_MANAGERS_OFFICE | rec:Room
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0093 |  |  | ref:ifcName | SSC_VAV0093
entity:SSC_VAV0093_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.AirFlow |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0093_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0093_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.DmprPos |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.OccSts |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.RmTemp |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.SP |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0094_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 120 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0094 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_018_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0094 |  |  | ref:ifcName | SSC_VAV0094
entity:SSC_VAV0094_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.AirFlow |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0094_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0094_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.DmprPos |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.OccSts |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.RmTemp |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.SP |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0095_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 225 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0095 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_017_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0095 |  |  | ref:ifcName | SSC_VAV0095
entity:SSC_VAV0095_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.AirFlow |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0095_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0095_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.DmprPos |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.OccSts |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.RmTemp |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.SP |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0096_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 2 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 420 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0096 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 4 |  |  | para:inletSize | 248 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_016_LOUNGE | rec:Room
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0096 |  |  | ref:ifcName | SSC_VAV0096
entity:SSC_VAV0096_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.AirFlow |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0096_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0096_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.DmprPos |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.OccSts |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.RmTemp |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.SP |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0097_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 420 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0097 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_016_LOUNGE | rec:Room
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0097 |  |  | ref:ifcName | SSC_VAV0097
entity:SSC_VAV0097_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.AirFlow |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0097_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0097_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.DmprPos |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.OccSts |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.RmTemp |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.SP |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0098_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 130 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0098 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_049_IT_OFFICE | rec:Room
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0098 |  |  | ref:ifcName | SSC_VAV0098
entity:SSC_VAV0098_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.AirFlow |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0098_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0098_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.DmprPos |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.OccSts |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.RmTemp |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.SP |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0099_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 105 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0099 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_042_CORRIDOR | rec:Room
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0099 |  |  | ref:ifcName | SSC_VAV0099
entity:SSC_VAV0099_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.AirFlow |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0099_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0099_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.DmprPos |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.OccSts |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.RmTemp |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.SP |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0100_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 45 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0100 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_041_CORRIDOR | rec:Room
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0100 |  |  | ref:ifcName | SSC_VAV0100
entity:SSC_VAV0100_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.AirFlow |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0100_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0100_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.DmprPos |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.OccSts |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.RmTemp |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.SP |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0101_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 130 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0101 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_044_CORRIDOR | rec:Room
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | 130 | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0101 |  |  | ref:ifcName | SSC_VAV0101
entity:SSC_VAV0101_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.AirFlow |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Damper_Controller | brick:Controller | brick:hasPoint | 130 | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0101_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.DmprPos |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.OccSts |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.RmTemp |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.SP |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPart | 130 | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 130 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0102 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_034_CORRIDOR | rec:Room
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | 130 | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0102 |  |  | ref:ifcName | SSC_VAV0102
entity:SSC_VAV0102_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.AirFlow |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Damper_Controller | brick:Controller | brick:hasPoint | 130 | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0102_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.DmprPos |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.OccSts |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.RmTemp |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.SP |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | 130 | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPart | 130 | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | 130 | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 130 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0103 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_034_CORRIDOR | rec:Room
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0103 |  |  | ref:ifcName | SSC_VAV0103
entity:SSC_VAV0103_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.AirFlow |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0103_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0103_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.DmprPos |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.OccSts |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.RmTemp |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.SP |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0104_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 105 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0104 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_034_CORRIDOR | rec:Room
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0104 |  |  | ref:ifcName | SSC_VAV0104
entity:SSC_VAV0104_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.AirFlow |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0104_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0104_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.DmprPos |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.OccSts |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.RmTemp |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.SP |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0105_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 105 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0105 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_034_CORRIDOR | rec:Room
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0105 |  |  | ref:ifcName | SSC_VAV0105
entity:SSC_VAV0105_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.AirFlow |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0105_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0105_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.DmprPos |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.OccSts |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.RmTemp |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.SP |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0106_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 105 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0106 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 2 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_042_CORRIDOR | rec:Room
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0106 |  |  | ref:ifcName | SSC_VAV0106
entity:SSC_VAV0106_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.AirFlow |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0106_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0106_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.DmprPos |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.OccSts |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.RmTemp |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.SP |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0107_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 105 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0107 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 1 |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0107 |  |  | ref:ifcName | SSC_VAV0107
entity:SSC_VAV0107_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.AirFlow |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0107_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0107_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.DmprPos |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.OccSts |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.RmTemp |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.SP |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0108_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 105 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rdfs:label_en | SSC VAV0108 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType | 0 |  |  | para:inletSize | 0 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0108 |  |  | ref:ifcName | SSC_VAV0108
entity:SSC_VAV0108_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.AirFlow |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0108_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0108_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.DmprPos |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.OccSts |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.RmTemp |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.SP |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0108
para:Chilled_Water_Loop_Network | owl:Class | rdfs:subClassOf | brick:HVAC_Equipment |  | rdfs:label_en | Chilled Water Loop Network
para:Chilled_Water_Loop_Network | owl:Class | rdfs:subClassOf | brick:HVAC_Equipment |  | rdfs:label_en | Chilled Water Loop Network
para:Close_command | owl:Class | rdfs:subClassOf | brick:Open_Close_Command |  | rdfs:label_en | Close Command
para:Command_Status | owl:Class | rdfs:subClassOf | brick:Manual_Auto_Status |  | rdfs:label_en | Auto Manual Command Status
para:Cooling_Mode_Operation_Hours | owl:Class | rdfs:subClassOf | para:Operation_Hours |  | rdfs:label_en | Cooling Mode Operating Duration
para:Damper_Position_100 | owl:Class | rdfs:subClassOf | brick:Valve_Position_Command |  | rdfs:comment | Damper Position 100%
para:Damper_Position_70 | owl:Class | rdfs:subClassOf | brick:Valve_Position_Command |  | rdfs:comment | Damper Position 70%
para:Damper_Position_77.5 | owl:Class | rdfs:subClassOf | brick:Valve_Position_Command |  | rdfs:comment | Damper Position 77.5%
para:Damper_Position_85 | owl:Class | rdfs:subClassOf | brick:Valve_Position_Command |  | rdfs:comment | Damper Position 85%
para:Damper_Position_92.5 | owl:Class | rdfs:subClassOf | brick:Valve_Position_Command |  | rdfs:comment | Damper Position 92.5%
para:Dehumidification_On_Status | owl:Class | rdfs:subClassOf | brick:Operating_Mode_Status |  | rdfs:label_en | Dehumidification On Status
para:DXUnit | owl:Class | rdfs:subClassOf | brick:HVAC_Equipment |  | rdfs:label_en | DX Unit
para:Fail_Start_Alarm | owl:Class | rdfs:subClassOf | brick:Alarm |  | rdfs:label_en | Fail to Start Alarm
para:Fail_Stop_Alarm | owl:Class | rdfs:subClassOf | brick:Alarm |  | rdfs:label_en | Fail to Stop Alarm
para:Fan_Mode_Operation_Hours | owl:Class | rdfs:subClassOf | para:Operation_Hours |  | rdfs:label_en | Fan Mode Operating Duration
para:Generator | owl:Class | rdfs:subClassOf | brick:Electrical_Equipment |  | rdfs:label_en | Generator
para:Heater_On_Status | owl:Class | rdfs:subClassOf | brick:Operating_Mode_Status |  | rdfs:label_en | Heater On Status
para:Humidification_On_Status | owl:Class | rdfs:subClassOf | brick:Operating_Mode_Status |  | rdfs:label_en | Humidification On Status
para:Open_command | owl:Class | rdfs:subClassOf | brick:Open_Close_Command |  | rdfs:label_en | Open Command
para:Operation_Hours | owl:Class | rdfs:subClassOf | brick:Duration_Sensor |  | rdfs:label_en | Operating Duration
para:Return_Air_Static_Pressure_Sensor | owl:Class | rdfs:subClassOf | brick:Air_Static_Pressure_Sensor |  | rdfs:label_en | Return Air Static Pressure
para:Return_Air_Static_Pressure_Sensor_01 | owl:Class | rdfs:subClassOf | brick:Air_Static_Pressure_Sensor |  | rdfs:label_en | Return Air Static Pressure 01
para:Return_Air_Static_Pressure_Sensor_02 | owl:Class | rdfs:subClassOf | brick:Air_Static_Pressure_Sensor |  | rdfs:label_en | Return Air Static Pressure 02
para:Scheduled_Hrs_Duration | owl:Class | rdfs:subClassOf | brick:Duration_Sensor |  | rdfs:label_en | Scheduled Hours of Operation
para:Start_Command | owl:Class | rdfs:subClassOf | brick:Start_Stop_Command |  | rdfs:label_en | Start Command
para:Start_Time | owl:Class | rdfs:subClassOf | brick:Duration_Sensor |  | rdfs:label_en | Start Time
para:Static_Pressure_Sensor | owl:Class | rdfs:subClassOf | brick:Supply_Air_Static_Pressure_Sensor |  | rdfs:label_en | Static Pressure Sensor
para:Static_Pressure_Sensor_01 | owl:Class | rdfs:subClassOf | brick:Supply_Air_Static_Pressure_Sensor |  | rdfs:label_en | Static Pressure Sensor 01
para:Static_Pressure_Sensor_02 | owl:Class | rdfs:subClassOf | brick:Supply_Air_Static_Pressure_Sensor |  | rdfs:label_en | Static Pressure Sensor 02
para:Static_Pressure_Sensor_Remote_01 | owl:Class | rdfs:subClassOf | brick:Supply_Air_Static_Pressure_Sensor |  | rdfs:label_en | Static Pressure Remote Sensor 01
para:Static_Pressure_Sensor_Remote_02 | owl:Class | rdfs:subClassOf | brick:Supply_Air_Static_Pressure_Sensor |  | rdfs:label_en | Static Pressure Remote Sensor 02
para:Stop_Command | owl:Class | rdfs:subClassOf | brick:Start_Stop_Command |  | rdfs:label_en | Stop Command
para:Stop_Time | owl:Class | rdfs:subClassOf | brick:Duration_Sensor |  | rdfs:label_en | Stop Time
para:Summary_Alarm | owl:Class | rdfs:subClassOf | brick:Alarm |  | rdfs:label_en | Summary Alarm
para:UnScheduled_Hrs_Duration | owl:Class | rdfs:subClassOf | brick:Duration_Sensor |  | rdfs:label_en | UnScheduled Hours of Operation
unit:EPOCH | qudt:Unit | rdf:type | qudt:Unit |  | qudt:symbol | <blanknode>
entity:SSC_MV_Generator | para:Generator | rec:locatedIn | entity:SSC_B1_012_GENERATOR | rec:Room
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_B1_015_ENTRANCE | rec:Room
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_014_SHELL_SPACE | rec:Room
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_014_SHELL_SPACE | rec:Room
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_014_SHELL_SPACE | rec:Room
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_015_SHELL_SPACE | rec:Room
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_015_SHELL_SPACE | rec:Room
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_015_SHELL_SPACE | rec:Room
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_024_CORRIDOR | rec:Room
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_019_PRAYER_ROOM | rec:Room
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_029_ROOM_NO_42 | rec:Room
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_029_ROOM_NO_43 | rec:Room
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_029_ROOM_NO_44 | rec:Room
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_029_SHELL_SPACE | rec:Room
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_029_SHELL_SPACE | rec:Room
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_029_SHELL_SPACE | rec:Room
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_013_CORRIDOR | rec:Room
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_003_OPEN_SPACE | rec:Room
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_003_OPEN_SPACE | rec:Room
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_001_CORRIDOR | rec:Room
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_002_SHELL_SPACE | rec:Room
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_002_SHELL_SPACE | rec:Room
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_002_SHELL_SPACE | rec:Room
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_002_SHELL_SPACE | rec:Room
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_001_CORRIDOR | rec:Room
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_016_SHELL_SPACE | rec:Room
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_001_CORRIDOR | rec:Room
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_018_CORRIDOR | rec:Room
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_028_CORRIDOR | rec:Room
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_003_OPEN_SPACE | rec:Room
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_010_CORRIDOR | rec:Room
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_022_ABLUTION_ROOM | rec:Room
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_008_AV_ROOM | rec:Room
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_ST-4_STAIR_4 | rec:Room
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_01_003_OPEN_SPACE | rec:Room
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_006_CONFERENCE_ROOM | rec:Room
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | rec:Room
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | rec:Room
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_004_CORRIDOR | rec:Room
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_001_FOYER | rec:Room
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_001_FOYER | rec:Room
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_002_LOBBY | rec:Room
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_002_LOBBY | rec:Room
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_002_LOBBY | rec:Room
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_002_LOBBY | rec:Room
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_003_CORRIDOR | rec:Room
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | rec:Room
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_02_006_CONFERENCE_ROOM | rec:Room
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_015_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_014_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_013_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_012_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_011_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_010_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_009_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_008_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_007_OPERATIONS_MANAGER | rec:Room
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_006_MEETING_ROOM | rec:Room
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_006_MEETING_ROOM | rec:Room
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_005_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_004_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_003_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_001_DIRECTORS_OFFICE | rec:Room
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_031_ASSOC_DIRECTORS_OFFICE | rec:Room
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_030_ASSOC_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_030_ASSOC_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_029_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_028_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_027_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_026_MEETING_ROOM | rec:Room
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_026_MEETING_ROOM | rec:Room
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_026_MEETING_ROOM | rec:Room
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_025_SECRETARIAL_AREA | rec:Room
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_024_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_023_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_022_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_021_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_020_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_019_IT_MANAGERS_OFFICE | rec:Room
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_018_VISITORS_CUBICLE | rec:Room
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_017_RESEARCHERS_OFFICE | rec:Room
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_016_LOUNGE | rec:Room
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_016_LOUNGE | rec:Room
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_049_IT_OFFICE | rec:Room
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_042_CORRIDOR | rec:Room
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_041_CORRIDOR | rec:Room
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_044_CORRIDOR | rec:Room
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_034_CORRIDOR | rec:Room
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_034_CORRIDOR | rec:Room
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_034_CORRIDOR | rec:Room
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_034_CORRIDOR | rec:Room
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_042_CORRIDOR | rec:Room
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | rec:feeds | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room

## CCU_Comparison
CCU / CRAC Ontology Consistency Check — 14 units
Source: SSC_Ontology_Ver0.5!A815:E1346 (532 triples). Relations normalised by replacing the unit id with {U}, then counted per unit. rec:locatedIn relations are excluded - location legitimately differs by unit.
1. Triple count per unit
Metric | CCU3F0301 | CCU3F0302 | CCUB0001A | CCUB0001B | CCUB0002A | CCUB0002B | CCUB0003 | CCUB0004 | CCUB0005A | CCUB0005B | CCUB0006A | CCUB0006B | CCUB0007 | CCUB0008 | Check
Rows in source | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | All equal (38 rows)
Difference vs CCU3F0301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2. Findings
Triple count: IDENTICAL — all 14 units have exactly 38 rows.
Relation patterns: 40 unique patterns; 37 present exactly once on every unit. No missing points, no duplicated rows.
The only variation is rec:locatedIn (3 distinct rooms: B1_038_SER-2, B1_023_Q_TEL, B1_017_MDF-2) — excluded as agreed.
Type columns (subject type, object type): consistent — every pattern uses the same brick/para class on all 14 units.
3. Full relation matrix — every unique CCU relation pattern and its count per unit
Subject pattern | Predicate | Object pattern | CCU3F0301 | CCU3F0302 | CCUB0001A | CCUB0001B | CCUB0002A | CCUB0002B | CCUB0003 | CCUB0004 | CCUB0005A | CCUB0005B | CCUB0006A | CCUB0006B | CCUB0007 | CCUB0008 | Status
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Humidity | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Temperature | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Humidity_Setpoint | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Temperature_Setpoint | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Communication_Alarm | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Loss_of_Airflow | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_General_Fault | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Clogged_Filter | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Cool_On_Status | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Dehumidifcation_On_Status | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Electric_Heater_On_Status | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Fan_On_Status | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Humidification_On_Status | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Main_Fan_Overload | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Running_Status | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Operating_State | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:hasPoint | entity:SSC_{U}_Summary_Alarm_Status | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | brick:isPartOf | entity:HVAC | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | rec:isFedBy | entity:CHWS-MAIN-LOOP | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | rec:locatedIn | entity:SSC_B1_038_SER-2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Excluded - location varies by unit
entity:SSC_{U} | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Clogged_Filter | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Communication_Alarm | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Cool_On_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Dehumidifcation_On_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Electric_Heater_On_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Fan_On_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_General_Fault | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Humidification_On_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Humidity | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Humidity_Setpoint | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Loss_of_Airflow | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Main_Fan_Overload | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Operating_State | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Running_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Summary_Alarm_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Temperature | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U}_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{U} | rec:locatedIn | entity:SSC_B1_023_Q_TEL | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | Excluded - location varies by unit
entity:SSC_{U} | rec:locatedIn | entity:SSC_B1_017_MDF-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | Excluded - location varies by unit
4. Location breakdown — rec:locatedIn triple per unit
Unit | # of rec:locatedIn triples | Room (object of the triple) | Units sharing that room
CCU3F0301 | 1 | entity:SSC_B1_038_SER-2 | 6
CCU3F0302 | 1 | entity:SSC_B1_038_SER-2 | 6
CCUB0001A | 1 | entity:SSC_B1_038_SER-2 | 6
CCUB0001B | 1 | entity:SSC_B1_038_SER-2 | 6
CCUB0002A | 1 | entity:SSC_B1_038_SER-2 | 6
CCUB0002B | 1 | entity:SSC_B1_038_SER-2 | 6
CCUB0003 | 1 | entity:SSC_B1_023_Q_TEL | 6
CCUB0004 | 1 | entity:SSC_B1_023_Q_TEL | 6
CCUB0005A | 1 | entity:SSC_B1_023_Q_TEL | 6
CCUB0005B | 1 | entity:SSC_B1_023_Q_TEL | 6
CCUB0006A | 1 | entity:SSC_B1_023_Q_TEL | 6
CCUB0006B | 1 | entity:SSC_B1_023_Q_TEL | 6
CCUB0007 | 1 | entity:SSC_B1_017_MDF-2 | 2
CCUB0008 | 1 | entity:SSC_B1_017_MDF-2 | 2
Conclusion: every CCU has exactly one rec:locatedIn triple, so none is missing or duplicated. The rooms themselves are NOT unique per unit — 6 units share B1_038_SER-2, 6 share B1_023_Q_TEL, and 2 share B1_017_MDF-2.

## AHU_Comparison
AHU Ontology Consistency Check — SSC_AHUB0001 to SSC_AHUB0005
Source: SSC_Ontology_Ver0.5!A128:D773 (646 triples). Relations normalised by replacing the AHU id with {N}, then counted per unit. rec:locatedIn relations are excluded - location legitimately differs by unit.
1. Triple count per AHU
Metric | AHUB0001 | AHUB0002 | AHUB0003 | AHUB0004 | AHUB0005
Rows in source | 129 | 130 | 128 | 132 | 127
Difference vs AHUB0001 | 0 | 1 | -1 | 3 | -2
2. Discrepancies (relations whose count is not identical across the 5 AHUs — location relations excluded)
Subject pattern | Predicate | Object pattern | AHUB0001 | AHUB0002 | AHUB0003 | AHUB0004 | AHUB0005 | Finding
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_SAP_Setpoint | 1 | 1 | 0 | 1 | 0 | MISSING: SAP_Setpoint point not declared on AHUB0003 and AHUB0005 | Missing or doesn’t exist?
entity:SSC_AHUB{N}_SAP_Setpoint | ref:hasExternalReference | <blanknode> | 1 | 1 | 0 | 1 | 0 | MISSING: no external reference for SAP_Setpoint on AHUB0003 and AHUB0005 (entity absent) | based on above
entity:SSC_AHUB{N}_RF | brick:hasPoint | entity:SSC_AHUB{N}_RF_AutoMan_Status | 1 | 1 | 1 | 0 | 1 | MISSING: Return Fan Auto/Manual status not declared on AHUB0004 | Missing or doesn’t exist?
entity:SSC_AHUB{N}_RF_AutoMan_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 0 | 1 | MISSING: no external reference for RF_AutoMan_Status on AHUB0004 (entity absent) | based on above
entity:SSC_AHUB{N}_SA_P-Static | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 2 | 1 | DUPLICATE: row repeated twice on AHUB0002, AHUB0003 and AHUB0004 | 2 sets of data for each
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_RA_P-Static_01 | 0 | 0 | 0 | 1 | 0 | EXTRA: only AHUB0004 has additional RA static points _01/_02 (all units already have RA_P-Static) | 2 extra sets of data
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_RA_P-Static_02 | 0 | 0 | 0 | 1 | 0 | EXTRA: only AHUB0004 | 2 extra sets of data
entity:SSC_AHUB{N}_RA_P-Static_01 | ref:hasExternalReference | <blanknode> | 0 | 0 | 0 | 1 | 0 | EXTRA: only AHUB0004 | based on above
entity:SSC_AHUB{N}_RA_P-Static_02 | ref:hasExternalReference | <blanknode> | 0 | 0 | 0 | 1 | 0 | EXTRA: only AHUB0004 | based on above
3. Full relation matrix — every unique AHU relation pattern and its count per unit
Subject pattern | Predicate | Object pattern | AHUB0001 | AHUB0002 | AHUB0003 | AHUB0004 | AHUB0005 | Status
entity:SSC_AHUB{N} | brick:hasPart | entity:SSC_AHUB{N}_CHW-Coil | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPart | entity:SSC_AHUB{N}_Filter | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPart | entity:SSC_AHUB{N}_OAD | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPart | entity:SSC_AHUB{N}_RAD | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPart | entity:SSC_AHUB{N}_MAD | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPart | entity:SSC_AHUB{N}_EAD | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPart | entity:SSC_AHUB{N}_RF | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPart | entity:SSC_AHUB{N}_SF | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPart | entity:SSC_AHUB{N}_Heater | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_OA_RH | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_OA_Temperature | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_RA_RH | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_RA_Temperature | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_RA_Flow | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_MA_Temperature | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_SA_Flow | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_SA_RH | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_SAT | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_Occupancy_Mode | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_Dehum_Setpoint | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_Occ_Temp_Setpoint | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_SAP_Setpoint | 1 | 1 | 0 | 1 | 0 | Not on all units
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_UnOcc_Temp_Setpoint | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_Enable_Disable_Cmd | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_Pressure_High_Filter_Dirty_Status | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_High_Pressure_Alarm | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_SA_P-Static | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_RA_P-Static | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | brick:isPartOf | entity:HVAC | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | para:ratedOutsideAirFlowrate | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | para:ratedSupplyAirFlowrate | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | rec:isFedBy | entity:CHWS-MAIN-LOOP | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | rec:locatedIn | entity:SSC_B1_013_CHILLED_WATER | 1 | 0 | 0 | 0 | 1 | Excluded - location varies by unit
entity:SSC_AHUB{N} | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_CHW-Coil | brick:coolingCapacity | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_CHW-Coil | brick:hasPart | entity:SSC_AHUB{N}_CHW-Coil_Valve | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_CHW-Coil_Cooling-Load-Consumption | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_CHW-Coil_Cooling-Load-Demand | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_CHW-Coil_Valve | brick:hasPart | entity:SSC_AHUB{N}_Cooling-Thermal-Virtual-Meter | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_CHW-Coil_Valve | brick:hasPoint | entity:SSC_AHUB{N}_CHW-Coil_Valve_Pos-Command | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_CHW-Coil_Valve | brick:hasPoint | entity:SSC_AHUB{N}_CHW-Coil_Valve_Pos-Feedback | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_CHW-Coil_Valve_Pos-Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_CHW-Coil_Valve_Pos-Feedback | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_Cooling-Thermal-Virtual-Meter | brick:hasPoint | entity:SSC_AHUB{N}_CHW-Coil_Cooling-Load-Consumption | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_Cooling-Thermal-Virtual-Meter | brick:hasPoint | entity:SSC_AHUB{N}_CHW-Coil_Cooling-Load-Demand | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_Dehum_Setpoint | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_EAD | brick:hasPoint | entity:SSC_AHUB{N}_EAD_Pos_Cmd | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_EAD | brick:hasPoint | entity:SSC_AHUB{N}_EAD_Pos_Fbk | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_EAD | brick:hasPoint | entity:SSC_AHUB{N}_EAD_Pos-Status | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_EAD_Pos_Cmd | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_EAD_Pos_Fbk | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_EAD_Pos-Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_Enable_Disable_Cmd | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_Heater | brick:hasPoint | entity:SSC_AHUB{N}_Heater_Command | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_Heater_Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_High_Pressure_Alarm | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_MA_Temperature | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_MAD | brick:hasPoint | entity:SSC_AHUB{N}_MAD_Pos_Cmd | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_MAD | brick:hasPoint | entity:SSC_AHUB{N}_MAD_Pos_Fbk | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_MAD_Pos_Cmd | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_MAD_Pos_Fbk | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_OA_RH | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_OA_Temperature | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_OAD | brick:hasPoint | entity:SSC_AHUB{N}_OAD_Pos_Cmd | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_OAD | brick:hasPoint | entity:SSC_AHUB{N}_OAD_Pos_Fbk | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_OAD | brick:hasPoint | entity:SSC_AHUB{N}_OAD_Pos-Status | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_OAD_Pos_Cmd | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_OAD_Pos_Fbk | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_OAD_Pos-Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_Occ_Temp_Setpoint | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_Occupancy_Mode | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_Pressure_High_Filter_Dirty_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RA_Flow | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RA_P-Static | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RA_RH | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RA_Temperature | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RAD | brick:hasPoint | entity:SSC_AHUB{N}_RAD_ReCr_Damper_Pos_100 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RAD | brick:hasPoint | entity:SSC_AHUB{N}_RAD_ReCr_Damper_Pos_70 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RAD | brick:hasPoint | entity:SSC_AHUB{N}_RAD_ReCr_Damper_Pos_77.5 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RAD | brick:hasPoint | entity:SSC_AHUB{N}_RAD_ReCr_Damper_Pos_85 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RAD | brick:hasPoint | entity:SSC_AHUB{N}_RAD_ReCr_Damper_Pos_92.5 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RAD_ReCr_Damper_Pos_100 | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RAD_ReCr_Damper_Pos_70 | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RAD_ReCr_Damper_Pos_77.5 | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RAD_ReCr_Damper_Pos_85 | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RAD_ReCr_Damper_Pos_92.5 | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF | brick:hasPart | entity:SSC_AHUB{N}_RF_Motor | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF | brick:hasPoint | entity:SSC_AHUB{N}_RF_AutoMan_Status | 1 | 1 | 1 | 0 | 1 | Not on all units
entity:SSC_AHUB{N}_RF | brick:hasPoint | entity:SSC_AHUB{N}_RF_TripAlm | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF_AutoMan_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 0 | 1 | Not on all units
entity:SSC_AHUB{N}_RF_Motor | brick:hasPart | entity:SSC_AHUB{N}_RF_Motor_Electrical-Meter | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF_Motor | brick:hasPoint | entity:SSC_AHUB{N}_RF_Motor_Speed_Cmd | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF_Motor | brick:hasPoint | entity:SSC_AHUB{N}_RF_Motor_Speed_Fbk | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF_Motor_Electrical-Meter | brick:hasPoint | entity:SSC_AHUB{N}_RF_Motor_Electrical-Meter_Power-Demand | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF_Motor_Electrical-Meter | brick:hasPoint | entity:SSC_AHUB{N}_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF_Motor_Electrical-Meter_Power-Demand | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF_Motor_Speed_Cmd | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF_Motor_Speed_Fbk | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_RF_TripAlm | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SA_Flow | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SA_P-Static | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 2 | 1 | Duplicated
entity:SSC_AHUB{N}_SA_RH | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SAP_Setpoint | ref:hasExternalReference | <blanknode> | 1 | 1 | 0 | 1 | 0 | Not on all units
entity:SSC_AHUB{N}_SAT | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF | brick:hasPart | entity:SSC_AHUB{N}_SF_Motor | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF | brick:hasPoint | entity:SSC_AHUB{N}_SF_TripAlm | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF | brick:hasPoint | entity:SSC_AHUB{N}_SF_AutoMan_Status | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF | brick:hasPoint | entity:SSC_AHUB{N}_SF_FailtoStop | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF | brick:hasPoint | entity:SSC_AHUB{N}_SF_FailtoStart | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF | brick:hasPoint | entity:SSC_AHUB{N}_SF_Status | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_AutoMan_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_FailtoStart | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_FailtoStop | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor | brick:hasPart | entity:SSC_AHUB{N}_SF_Motor_Electrical-Meter | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor | brick:hasPoint | entity:SSC_AHUB{N}_SF_Motor_Speed_Cmd | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor | brick:hasPoint | entity:SSC_AHUB{N}_SF_Motor_Speed_Fbk | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor | para:ratedFrequency | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor | para:ratedPower | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor | para:ratedVoltage | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor_Electrical_Energy_Consumption | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor_Electrical-Meter | brick:hasPoint | entity:SSC_AHUB{N}_SF_Motor_Electrical-Meter_Power-Demand | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor_Electrical-Meter | brick:hasPoint | entity:SSC_AHUB{N}_SF_Motor_Electrical_Energy_Consumption | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor_Electrical-Meter_Power-Demand | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor_Speed_Cmd | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Motor_Speed_Fbk | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_SF_TripAlm | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N}_UnOcc_Temp_Setpoint | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_AHUB{N} | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | 0 | 1 | 1 | 0 | 0 | Excluded - location varies by unit
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_RA_P-Static_01 | 0 | 0 | 0 | 1 | 0 | Not on all units
entity:SSC_AHUB{N} | brick:hasPoint | entity:SSC_AHUB{N}_RA_P-Static_02 | 0 | 0 | 0 | 1 | 0 | Not on all units
entity:SSC_AHUB{N} | rec:locatedIn | entity:SSC_B1_008_VENT_PLANT | 0 | 0 | 0 | 1 | 0 | Excluded - location varies by unit
entity:SSC_AHUB{N}_RA_P-Static_01 | ref:hasExternalReference | <blanknode> | 0 | 0 | 0 | 1 | 0 | Not on all units
entity:SSC_AHUB{N}_RA_P-Static_02 | ref:hasExternalReference | <blanknode> | 0 | 0 | 0 | 1 | 0 | Not on all units

## CHWP_Comparison
Chilled Water Pump Ontology Consistency Check — SSC_CHW_CHWP01 to CHWP04
Source: SSC_Ontology_Ver0.5!A1347:E1422 (76 triples). Relations normalised by replacing the pump id with {P}, then counted per pump. Type columns (B, E) also compared.
1. Triple count per pump
Metric | CHWP01 | CHWP02 | CHWP03 | CHWP04 | All equal?
Rows in source | 19 | 19 | 19 | 19 | YES
Difference vs CHWP01 | 0 | 0 | 0 | 0
2. Findings
Triple count: IDENTICAL — all 4 pumps have exactly 19 rows.
Relation patterns: 19 unique patterns, each present exactly once on every pump. No missing points, no duplicated rows, no extra points.
Location: unlike the AHUs and CCUs, all 4 pumps share the same room (SSC_B1_014_VENT_PLANT), so even rec:locatedIn is identical.
Type columns (subject type, object type): consistent — every pattern uses the same brick/para class on all 4 pumps.
Observation (not a discrepancy): the pumps carry Speed_Command and Speed_Fbk but no run/stop status or auto-manual point. This is uniform across all 4, so it is a modelling choice rather than an inconsistency — worth confirming it is intended.
3. Full relation matrix — every unique pump relation pattern and its count per pump
Subject pattern | Predicate | Object pattern | CHWP01 | CHWP02 | CHWP03 | CHWP04 | Status
entity:SSC_CHW_{P} | brick:hasPart | entity:SSC_CHW_{P}_Motor | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P} | brick:hasPart | entity:SSC_CHW_{P}_Electrical_Meter | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P} | brick:hasPart | entity:SSC_CHW_{P}_Thermal_Meter | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P} | brick:hasPoint | entity:SSC_CHW_{P}_Scheduled_PM_Hours | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P} | brick:hasPoint | entity:SSC_CHW_{P}_UNScheduled_Outage_Hours | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P} | brick:isPartOf | entity:CHW-System | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P} | rec:feeds | entity:CHWS-MAIN-LOOP | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P} | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P} | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P}_Electrical_Meter | brick:hasPoint | entity:SSC_CHW_{P}_Power_Sensor | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P}_Motor | brick:hasPoint | entity:SSC_CHW_{P}_Speed_Command | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P}_Motor | brick:hasPoint | entity:SSC_CHW_{P}_Speed_Fbk | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P}_Power_Sensor | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P}_Scheduled_PM_Hours | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P}_Speed_Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P}_Speed_Fbk | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P}_Thermal_Meter | brick:hasPoint | entity:SSC_CHW_{P}_Thermal_Power_Sensor | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P}_Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{P}_UNScheduled_Outage_Hours | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | OK

## HE_Comparison
Heat Exchanger Ontology Consistency Check — SSC_CHW_HE01 to HE05
Source: SSC_Ontology_Ver0.5!A1423:E1572 (150 triples). Relations normalised by replacing the HE id with {H}, then counted per unit. Type columns (B, E) also compared.
1. Triple count per heat exchanger
Metric | HE01 | HE02 | HE03 | HE04 | HE05 | All equal?
Rows in source | 32 | 32 | 32 | 32 | 22 | NO
Difference vs HE01 | 0 | 0 | 0 | 0 | -10
2. Findings
Counts DO NOT match: HE01-HE04 have 32 rows each, HE05 has only 22 — 10 rows short.
All 10 missing rows sit on HE05's Supply_Valve: the points Auto_Command, Manual_Auto_Status, Close_Command, Open_Command and Status are absent, together with their 5 ref:hasExternalReference rows. HE05's Supply_Valve keeps only its Temperature_Sensor.
Everything else is consistent: the Return_Valve branch, Motor, isPartOf, locatedIn and IFC reference are identical on all 5. All 5 are in the same room (SSC_B1_014_VENT_PLANT), so there is no location variance.
Type columns: no inconsistencies between units — every shared pattern carries the same subject/object class on all 5.
Observation (affects all 5, so not a count discrepancy): Supply_Valve_Close_Command is typed para:Open_command and Supply_Valve_Open_Command is typed para:Close_command — the two classes look swapped. Also Return_Valve carries both _Open_Close_Status and _Status, both typed brick:Open_Close_Status, which looks like a duplicated point under two names.
3. Discrepancies — relations not present on every heat exchanger
Subject pattern | Predicate | Object pattern | HE01 | HE02 | HE03 | HE04 | HE05 | Finding
entity:SSC_CHW_{H}_Supply_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Supply_Valve_Auto_Command | 1 | 1 | 1 | 1 | 0 | MISSING on HE05
entity:SSC_CHW_{H}_Supply_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Supply_Valve_Manual_Auto_Status | 1 | 1 | 1 | 1 | 0 | MISSING on HE05
entity:SSC_CHW_{H}_Supply_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Supply_Valve_Close_Command | 1 | 1 | 1 | 1 | 0 | MISSING on HE05
entity:SSC_CHW_{H}_Supply_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Supply_Valve_Open_Command | 1 | 1 | 1 | 1 | 0 | MISSING on HE05
entity:SSC_CHW_{H}_Supply_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Supply_Valve_Status | 1 | 1 | 1 | 1 | 0 | MISSING on HE05
entity:SSC_CHW_{H}_Supply_Valve_Auto_Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 0 | MISSING on HE05
entity:SSC_CHW_{H}_Supply_Valve_Close_Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 0 | MISSING on HE05
entity:SSC_CHW_{H}_Supply_Valve_Manual_Auto_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 0 | MISSING on HE05
entity:SSC_CHW_{H}_Supply_Valve_Open_Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 0 | MISSING on HE05
entity:SSC_CHW_{H}_Supply_Valve_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 0 | MISSING on HE05
4. Full relation matrix — every unique heat exchanger relation pattern and its count per unit
Subject pattern | Predicate | Object pattern | HE01 | HE02 | HE03 | HE04 | HE05 | Status
entity:SSC_CHW_{H} | brick:hasPart | entity:SSC_CHW_{H}_Return_Valve | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H} | brick:hasPart | entity:SSC_CHW_{H}_Supply_Valve | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H} | brick:isPartOf | entity:CHW-System | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H} | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H} | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve | brick:hasPart | entity:SSC_CHW_{H}_Return_Valve_Motor | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Return_Valve_Open_Close_Status | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Return_Valve_Diff_Prs | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Return_Valve_Position_Command | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Return_Valve_Position | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Return_Valve_Status | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve_Diff_Prs | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve_Motor | brick:hasPoint | entity:SSC_CHW_{H}_Return_Valve_Motor_Auto_Manual_Command_Status | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve_Motor | brick:hasPoint | entity:SSC_CHW_{H}_Return_Valve_Motor_Auto_Manual_Status | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve_Motor_Auto_Manual_Command_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve_Motor_Auto_Manual_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve_Open_Close_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve_Position | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve_Position_Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Return_Valve_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Supply_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Supply_Valve_Auto_Command | 1 | 1 | 1 | 1 | 0 | Not on all units
entity:SSC_CHW_{H}_Supply_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Supply_Valve_Manual_Auto_Status | 1 | 1 | 1 | 1 | 0 | Not on all units
entity:SSC_CHW_{H}_Supply_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Supply_Valve_Close_Command | 1 | 1 | 1 | 1 | 0 | Not on all units
entity:SSC_CHW_{H}_Supply_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Supply_Valve_Open_Command | 1 | 1 | 1 | 1 | 0 | Not on all units
entity:SSC_CHW_{H}_Supply_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Supply_Valve_Status | 1 | 1 | 1 | 1 | 0 | Not on all units
entity:SSC_CHW_{H}_Supply_Valve | brick:hasPoint | entity:SSC_CHW_{H}_Supply_Valve_Temperature_Sensor | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_CHW_{H}_Supply_Valve_Auto_Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 0 | Not on all units
entity:SSC_CHW_{H}_Supply_Valve_Close_Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 0 | Not on all units
entity:SSC_CHW_{H}_Supply_Valve_Manual_Auto_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 0 | Not on all units
entity:SSC_CHW_{H}_Supply_Valve_Open_Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 0 | Not on all units
entity:SSC_CHW_{H}_Supply_Valve_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 0 | Not on all units
entity:SSC_CHW_{H}_Supply_Valve_Temperature_Sensor | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | OK

## DX_Comparison
DX Unit Ontology Consistency Check — SSC_DXB0001 to DXB0010
Source: SSC_Ontology_Ver0.5!A1573:E1680 (108 triples). Relations normalised by replacing the DX id with {D}, then counted per unit. rec:locatedIn and rec:feeds are excluded from the pass/fail flag because both legitimately vary by room.
1. Triple count per DX unit
Metric | DXB0001 | DXB0002 | DXB0003 | DXB0004 | DXB0005 | DXB0006 | DXB0007 | DXB0008 | DXB0009 | DXB0010 | All equal?
Rows in source | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 12 | NO
Difference vs DXB0001 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2
2. Findings
Counts DO NOT match: DXB0001-DXB0006 have 10 rows each, DXB0007-DXB0010 have 12 — a 2-row difference.
The entire difference is one point: DXB0007-DXB0010 carry a Humidity_Sensor (hasPoint + its ref:hasExternalReference). DXB0001-DXB0006 have no humidity point at all.
This looks intentional rather than a defect: the four units with humidity sensing are the ones in FM STORAGE rooms (B1_019/020/021), while the six without are in the UPS and MV switch rooms. Worth confirming that storage rooms are meant to be humidity-monitored and the electrical rooms are not.
Everything else is consistent: Temperature_Sensor, Alarm, Running_Status, isPartOf HVAC and the IFC external reference are present exactly once on all 10 units. Type columns show no inconsistencies.
Observation: every unit's rec:feeds target is the SAME room as its rec:locatedIn target. If rec:feeds is meant to express which space the unit serves that is fine, but a unit feeding the room it sits in is worth a second look — see the breakdown in section 5.
3. Discrepancies — structural relations not present on every DX unit (location/feeds excluded)
Subject pattern | Predicate | Object pattern | DXB0001 | DXB0002 | DXB0003 | DXB0004 | DXB0005 | DXB0006 | DXB0007 | DXB0008 | DXB0009 | DXB0010 | Finding
entity:SSC_{D} | brick:hasPoint | entity:SSC_{D}_Humidity_Sensor | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | MISSING on DXB0001-DXB0006 (likely intentional - see findings)
entity:SSC_{D}_Humidity_Sensor | ref:hasExternalReference | <blanknode> | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | MISSING on DXB0001-DXB0006 (entity absent)
4. Full relation matrix — every unique DX relation pattern and its count per unit
Subject pattern | Predicate | Object pattern | DXB0001 | DXB0002 | DXB0003 | DXB0004 | DXB0005 | DXB0006 | DXB0007 | DXB0008 | DXB0009 | DXB0010 | Status
entity:SSC_{D} | brick:hasPoint | entity:SSC_{D}_Temperature_Sensor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{D} | brick:hasPoint | entity:SSC_{D}_Alarm | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{D} | brick:hasPoint | entity:SSC_{D}_Running_Status | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{D} | brick:hasPoint | entity:SSC_{D}_Humidity_Sensor | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | Not on all units
entity:SSC_{D} | brick:isPartOf | entity:HVAC | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{D} | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{D}_Alarm | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{D}_Running_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{D}_Temperature_Sensor | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{D}_Humidity_Sensor | ref:hasExternalReference | <blanknode> | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | Not on all units
entity:SSC_{D} | rec:locatedIn | entity:SSC_B1_005_UPS | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{D} | rec:locatedIn | entity:SSC_B1_004_MV_SWITCH_ROOM | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{D} | rec:locatedIn | entity:SSC_B1_019_FM_STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | Excluded - varies by room
entity:SSC_{D} | rec:locatedIn | entity:SSC_B1_020_FM_STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Excluded - varies by room
entity:SSC_{D} | rec:locatedIn | entity:SSC_B1_021_FM_STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Excluded - varies by room
entity:SSC_{D} | rec:feeds | entity:SSC_B1_005_UPS | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{D} | rec:feeds | entity:SSC_B1_004_MV_SWITCH_ROOM | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{D} | rec:feeds | entity:SSC_B1_019_FM_STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | Excluded - varies by room
entity:SSC_{D} | rec:feeds | entity:SSC_B1_020_FM_STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Excluded - varies by room
entity:SSC_{D} | rec:feeds | entity:SSC_B1_021_FM_STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Excluded - varies by room
5. Location and feeds breakdown per unit
Unit | # locatedIn | Room (locatedIn) | Target (rec:feeds) | feeds = locatedIn?
DXB0001 | 1 | entity:SSC_B1_005_UPS | entity:SSC_B1_005_UPS | same
DXB0002 | 1 | entity:SSC_B1_005_UPS | entity:SSC_B1_005_UPS | same
DXB0003 | 1 | entity:SSC_B1_005_UPS | entity:SSC_B1_005_UPS | same
DXB0004 | 1 | entity:SSC_B1_005_UPS | entity:SSC_B1_005_UPS | same
DXB0005 | 1 | entity:SSC_B1_004_MV_SWITCH_ROOM | entity:SSC_B1_004_MV_SWITCH_ROOM | same
DXB0006 | 1 | entity:SSC_B1_004_MV_SWITCH_ROOM | entity:SSC_B1_004_MV_SWITCH_ROOM | same
DXB0007 | 1 | entity:SSC_B1_019_FM_STORAGE | entity:SSC_B1_019_FM_STORAGE | same
DXB0008 | 1 | entity:SSC_B1_019_FM_STORAGE | entity:SSC_B1_019_FM_STORAGE | same
DXB0009 | 1 | entity:SSC_B1_020_FM_STORAGE | entity:SSC_B1_020_FM_STORAGE | same
DXB0010 | 1 | entity:SSC_B1_021_FM_STORAGE | entity:SSC_B1_021_FM_STORAGE | same

## FCU_Comparison
FCU Ontology Consistency Check — SSC_FCU0001 to FCU0011
Source: SSC_Ontology_Ver0.5!A1681:E2208 (528 triples). Relations normalised by replacing the FCU id with {F}, then counted per unit. rec:locatedIn and rec:feeds are excluded from the pass/fail flag because both legitimately vary by room.
1. Triple count per FCU
Metric | FCU0001 | FCU0002 | FCU0003 | FCU0004 | FCU0005 | FCU0006 | FCU0007 | FCU0008 | FCU0009 | FCU0010 | FCU0011 | All equal?
Rows in source | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | YES
Difference vs FCU0001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2. Findings
Triple count: IDENTICAL — all 11 FCUs have exactly 48 rows.
Relation patterns: 64 unique patterns. 46 are structural and present exactly once on every FCU — no missing points, no duplicates, no extras.
The remaining 18 patterns are the rec:locatedIn and rec:feeds rows, which differ only in which room they point at (9 distinct rooms across the 11 units). Every FCU has exactly one of each, so this is room variance, not a gap.
Type columns (subject type, object type): consistent — every shared pattern uses the same brick/para class on all 11 units.
Observation: as with the DX units, each FCU's rec:feeds target is the SAME room as its rec:locatedIn target on all 11 units — see the breakdown in section 4.
3. Full relation matrix — every unique FCU relation pattern and its count per unit
Subject pattern | Predicate | Object pattern | FCU0001 | FCU0002 | FCU0003 | FCU0004 | FCU0005 | FCU0006 | FCU0007 | FCU0008 | FCU0009 | FCU0010 | FCU0011 | Status
entity:SSC_{F} | brick:hasPart | entity:SSC_{F}_CHW-Coil | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPart | entity:SSC_{F}_Cooling-Thermal-Virtual-Meter | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPart | entity:SSC_{F}_ElectricalVirtualMeter | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPart | entity:SSC_{F}_SF | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_Schedule_Hrs | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_UnScheduled_Hrs | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_Temp_Setpoint | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_Occupied_Temp_Setpoint | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_Room_Temperature | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_CoolingMode_OperationDuration | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_FanMode_OperationDuration | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_TotalOperationDuration | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_Starttime | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_Stoptime | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:isPartOf | entity:HVAC | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | rec:feeds | entity:SSC_B1_016_SPRINKLER_&_WATER | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:isFedBy | entity:CHWS-MAIN-LOOP | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | rec:locatedIn | entity:SSC_B1_016_SPRINKLER_&_WATER | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_Occupancy_Status | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | brick:hasPoint | entity:SSC_{F}_Temp_Cntrl_SCADA_or_Thermostat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_CHW-Coil | brick:coolingCapacity | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_CHW-Coil | brick:hasPart | entity:SSC_{F}_CHW-Coil_Valve | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Cooling-Load-Consumption | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Cooling-Load-Demand | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_CoolingMode_OperationDuration | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Cooling-Thermal-Virtual-Meter | brick:hasPoint | entity:SSC_{F}_Cooling-Load-Consumption | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Cooling-Thermal-Virtual-Meter | brick:hasPoint | entity:SSC_{F}_Cooling-Load-Demand | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_ElectricalConsumption | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_ElectricalDemand | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_ElectricalVirtualMeter | brick:hasPoint | entity:SSC_{F}_ElectricalConsumption | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_ElectricalVirtualMeter | brick:hasPoint | entity:SSC_{F}_ElectricalDemand | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_FanMode_OperationDuration | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Occupancy_Status | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Occupied_Temp_Setpoint | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Room_Temperature | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Schedule_Hrs | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_SF | brick:hasPart | entity:SSC_{F}_SF_Motor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_SF_Motor | brick:hasPoint | entity:SSC_{F}_Start_Command | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_SF_Motor | brick:hasPoint | entity:SSC_{F}_Stop_Command | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Start_Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Starttime | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Stop_Command | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Stoptime | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Temp_Cntrl_SCADA_or_Thermostat | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_Temp_Setpoint | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_TotalOperationDuration | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F}_UnScheduled_Hrs | ref:hasExternalReference | <blanknode> | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | OK
entity:SSC_{F} | rec:feeds | entity:SSC_B1_025_MAIN_SEC_CONTROL_ROOM | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:locatedIn | entity:SSC_B1_025_MAIN_SEC_CONTROL_ROOM | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:feeds | entity:SSC_B1_039_BMS | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:locatedIn | entity:SSC_B1_039_BMS | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:feeds | entity:SSC_01_008_AV_ROOM | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:locatedIn | entity:SSC_01_008_AV_ROOM | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:feeds | entity:SSC_01_027_IDF_1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:locatedIn | entity:SSC_01_027_IDF_1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:feeds | entity:SSC_01_039_IDF_2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:locatedIn | entity:SSC_01_039_IDF_2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:feeds | entity:SSC_01_028_CORRIDOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:locatedIn | entity:SSC_01_028_CORRIDOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:feeds | entity:SSC_01_010_CORRIDOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:locatedIn | entity:SSC_01_010_CORRIDOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Excluded - varies by room
entity:SSC_{F} | rec:feeds | entity:SSC_03_033_PRINTING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Excluded - varies by room
entity:SSC_{F} | rec:locatedIn | entity:SSC_03_033_PRINTING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Excluded - varies by room
4. Location and feeds breakdown per unit
Unit | # locatedIn | Room (locatedIn) | Target (rec:feeds) | feeds = locatedIn?
FCU0001 | 1 | entity:SSC_B1_016_SPRINKLER_&_WATER | entity:SSC_B1_016_SPRINKLER_&_WATER | same
FCU0002 | 1 | entity:SSC_B1_025_MAIN_SEC_CONTROL_ROOM | entity:SSC_B1_025_MAIN_SEC_CONTROL_ROOM | same
FCU0003 | 1 | entity:SSC_B1_039_BMS | entity:SSC_B1_039_BMS | same
FCU0004 | 1 | entity:SSC_01_008_AV_ROOM | entity:SSC_01_008_AV_ROOM | same
FCU0005 | 1 | entity:SSC_01_027_IDF_1 | entity:SSC_01_027_IDF_1 | same
FCU0006 | 1 | entity:SSC_01_027_IDF_1 | entity:SSC_01_027_IDF_1 | same
FCU0007 | 1 | entity:SSC_01_039_IDF_2 | entity:SSC_01_039_IDF_2 | same
FCU0008 | 1 | entity:SSC_01_039_IDF_2 | entity:SSC_01_039_IDF_2 | same
FCU0009 | 1 | entity:SSC_01_028_CORRIDOR | entity:SSC_01_028_CORRIDOR | same
FCU0010 | 1 | entity:SSC_01_010_CORRIDOR | entity:SSC_01_010_CORRIDOR | same
FCU0011 | 1 | entity:SSC_03_033_PRINTING | entity:SSC_03_033_PRINTING | same

## EF_Comparison
Exhaust Fan Ontology Consistency Check — GEFB0001, KEF0103/0303, TEF0101/0102/0301/0302
Source: SSC_Ontology_Ver0.5!A2209:E2492. The selected range A2209:E2238 held only ONE unit (GEFB0001), so the scope was widened to every entity typed brick:Exhaust_Fan — 7 units in total. Rows 2343-2372 inside that span belong to Levels and the MV Generator and are ignored.
1. Triple count per fan
Metric | GEFB0001 | KEF0103 | KEF0303 | TEF0101 | TEF0102 | TEF0301 | TEF0302 | All equal?
Rows in source | 30 | 52 | 52 | 30 | 30 | 30 | 30 | NO
Distinct relations (rows / duplication) | 30 | 26 | 26 | 30 | 30 | 30 | 30
Difference vs GEFB0001 | 0 | 22 | 22 | 0 | 0 | 0 | 0
2. Findings
Counts DO NOT match: GEFB0001 and the four TEFs have 30 rows each; KEF0103 and KEF0303 have 52.
KEF0103 and KEF0303 are DUPLICATED end to end: each has 26 distinct relations and every single one of them appears exactly twice (26 x 2 = 52). This is a data-entry duplication, not extra content — see the Duplication column in section 3.
Three different point sets are in use. GEFB0001 alone has Auto_Command_Status, Exhaust_Fan_in_Auto_Mode and Exhaust_Fan_Healthy (plus their references). The KEFs and TEFs have LOC_On_Off_Status, which GEFB0001 lacks. The four TEFs alone have PDSL_OnOff_Status and Rtn_Air_Prs_Sw_Alarm. Of 36 relation patterns, only 24 are shared by all 7 fans; the other 12 are sub-type specific.
Type inconsistency: Motor_Running_Status is typed brick:On_Off_Status on GEFB0001, KEF0103 and KEF0303, but brick:Fan_Status on all four TEFs. The same concept carries two different classes.
Location: ALL 7 fans are locatedIn AND feed the same room, entity:Level7_Office0367 — including units named for basement and level 01/03. This looks like placeholder data copied across every fan and should be corrected.
Note: rows 2343-2372 sit inside the scanned span but belong to Levels and the MV Generator, so they are excluded from this comparison.
3. Full relation matrix — count per fan (1 = present once, 2 = duplicated, 0 = absent)
Subject pattern | Predicate | Object pattern | GEFB0001 | KEF0103 | KEF0303 | TEF0101 | TEF0102 | TEF0301 | TEF0302 | Presence | Duplication
entity:SSC_{X} | brick:hasPart | entity:SSC_{X}_Motor | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X} | brick:hasPoint | entity:SSC_{X}_Starttime | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X} | brick:hasPoint | entity:SSC_{X}_Stoptime | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X} | brick:isPartOf | entity:HVAC | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X} | brick:ratedPowerInput | <blanknode> | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X} | rec:feeds | entity:Level7_Office0367 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X} | rec:locatedIn | entity:Level7_Office0367 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X} | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_Auto_Command | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_Auto_Command_Status | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Missing on 6 of 7 | -
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_Auto_Manual_Status | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_Exhaust_Fan_in_Auto_Mode | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Missing on 6 of 7 | -
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_Exhaust_Fan_Healthy | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Missing on 6 of 7 | -
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_Manual_Command | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_Running_Status | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_Start_Command | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_Stop_Command | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_Trip_Alarm | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor_Auto_Command | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor_Auto_Command_Status | ref:hasExternalReference | <blanknode> | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Missing on 6 of 7 | -
entity:SSC_{X}_Motor_Auto_Manual_Status | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor_Exhaust_Fan_Healthy | ref:hasExternalReference | <blanknode> | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Missing on 6 of 7 | -
entity:SSC_{X}_Motor_Exhaust_Fan_in_Auto_Mode | ref:hasExternalReference | <blanknode> | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Missing on 6 of 7 | -
entity:SSC_{X}_Motor_Manual_Command | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor_Running_Status | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor_Start_Command | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor_Stop_Command | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor_Trip_Alarm | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Starttime | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Stoptime | ref:hasExternalReference | <blanknode> | 1 | 2 | 2 | 1 | 1 | 1 | 1 | On all 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_LOC_On_Off_Status | 0 | 2 | 2 | 1 | 1 | 1 | 1 | Missing on 1 of 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor_LOC_On_Off_Status | ref:hasExternalReference | <blanknode> | 0 | 2 | 2 | 1 | 1 | 1 | 1 | Missing on 1 of 7 | Duplicated on 2 unit(s)
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_PDSL_OnOff_Status | 0 | 0 | 0 | 1 | 1 | 1 | 1 | Missing on 3 of 7 | -
entity:SSC_{X}_Motor | brick:hasPoint | entity:SSC_{X}_Motor_Rtn_Air_Prs_Sw_Alarm | 0 | 0 | 0 | 1 | 1 | 1 | 1 | Missing on 3 of 7 | -
entity:SSC_{X}_Motor_PDSL_OnOff_Status | ref:hasExternalReference | <blanknode> | 0 | 0 | 0 | 1 | 1 | 1 | 1 | Missing on 3 of 7 | -
entity:SSC_{X}_Motor_Rtn_Air_Prs_Sw_Alarm | ref:hasExternalReference | <blanknode> | 0 | 0 | 0 | 1 | 1 | 1 | 1 | Missing on 3 of 7 | -
4. Location and feeds breakdown per fan
Fan | # locatedIn triples | Room (locatedIn) | Target (rec:feeds) | feeds = locatedIn?
GEFB0001 | 1 | entity:Level7_Office0367 | entity:Level7_Office0367 | same
KEF0103 | 2 | entity:Level7_Office0367 ; entity:Level7_Office0367 | entity:Level7_Office0367 ; entity:Level7_Office0367 | same
KEF0303 | 2 | entity:Level7_Office0367 ; entity:Level7_Office0367 | entity:Level7_Office0367 ; entity:Level7_Office0367 | same
TEF0101 | 1 | entity:Level7_Office0367 | entity:Level7_Office0367 | same
TEF0102 | 1 | entity:Level7_Office0367 | entity:Level7_Office0367 | same
TEF0301 | 1 | entity:Level7_Office0367 | entity:Level7_Office0367 | same
TEF0302 | 1 | entity:Level7_Office0367 | entity:Level7_Office0367 | same
Every fan points at the same room, and the KEFs show it twice because their whole block is duplicated. A basement GEF, two kitchen EFs and four toilet EFs all located in one Level 7 office is almost certainly placeholder data.

## GEN_Check
Generator Ontology Check — SSC_MV_Generator
There is only ONE generator instance in the model, so a cross-unit count comparison is not possible. This sheet is an internal integrity check instead: every point is tested for exactly one declaration and exactly one external reference, and all generator triples are located.
1. Row inventory
Metric | Count
Triples with the generator itself as subject | 16
Triples with a generator point as subject | 10
Total generator triples in the workbook | 26
Of those, inside the selected block (rows 2347-2371) | 25
Of those, located elsewhere in the sheet | 1
2. Point inventory — each point should be declared once and referenced once
Point entity | Class | hasPoint declarations | ref:hasExternalReference rows | Status
entity:SSC_MV_Generator_Battery_Voltage | brick:Battery_Voltage_Sensor | 1 | 1 | OK
entity:SSC_MV_Generator_Current_Reading | brick:Current_Sensor | 1 | 1 | OK
entity:SSC_MV_Generator_Engine_Oil_Pressure_Reading | brick:Pressure_Sensor | 1 | 1 | OK
entity:SSC_MV_Generator_Frequency_Reading | brick:Frequency_Sensor | 1 | 1 | OK
entity:SSC_MV_Generator_Apparent_Power | brick:Apparent_Power_Sensor | 1 | 1 | OK
entity:SSC_MV_Generator_Active_Power | brick:Active_Power_Sensor | 1 | 1 | OK
entity:SSC_MV_Generator_Energy | brick:Energy_Sensor | 1 | 1 | OK
entity:SSC_MV_Generator_Generator_Running_Status | brick:Run_Status | 1 | 1 | OK
entity:SSC_MV_Generator_Runtime_Meter | brick:Duration_Sensor | 1 | 1 | OK
entity:SSC_MV_Generator_Voltage | brick:Voltage_Sensor | 1 | 1 | OK
3. Non-point triples on the generator, and where they sit in the sheet
Predicate | Object | Occurrences | Sheet row
brick:isPartOf | entity:Electrical_System | 1 | 2357
para:ratedFrequency | <blanknode> | 1 | 2358
para:ratedPower | <blanknode> | 1 | 2359
para:ratedVoltage | <blanknode> | 1 | 2360
ref:hasExternalReference | <blanknode> | 1 | 2361
rec:locatedIn | entity:SSC_B1_012_GENERATOR | 1 | 5013
4. Findings
Only one generator instance exists in the model (SSC_MV_Generator), so there is no peer to compare counts against — unlike the AHUs, CCUs, pumps, HEs, DX units, FCUs and exhaust fans.
Internal integrity is clean: all 10 points are declared exactly once and each has exactly one external reference. No duplicates, no orphaned reference rows, no undeclared points.
Rated parameters (ratedFrequency, ratedPower, ratedVoltage), brick:isPartOf Electrical_System and the IFC reference are all present exactly once.
SPLIT DATA: the generator's rec:locatedIn triple is not in the equipment block (rows 2347-2371) — it sits alone at row 5013. Every other equipment family keeps locatedIn inside its own block. Worth moving so the generator's definition is contiguous.
Naming: entity:SSC_MV_Generator_Generator_Running_Status repeats the word Generator. Comparable points elsewhere are named <equipment>_Running_Status.
Naming: sensor suffixes are inconsistent — Current_Reading, Frequency_Reading and Engine_Oil_Pressure_Reading carry a _Reading suffix while Voltage, Energy, Active_Power and Apparent_Power do not.
Unlike the DX units and FCUs, the generator has no rec:feeds triple. Its location (SSC_B1_012_GENERATOR) is a real room, which is correct — contrast with the exhaust fans, which all point at the Level7_Office0367 placeholder.

## VAV_Comparison
VAV Ontology Consistency Check — SSC_VAV0001 to VAV0108
Source: SSC_Ontology_Ver0.5!A2493:E4976 and A5014:E5120 (2,591 triples, 108 units). With 108 units a per-unit column grid is unreadable, so each structural relation is tested for the expected count of 108 instead.
1. Row count summary
Metric | Value
VAV units found | 108
Total VAV triples | 2591
Units with the expected 24 rows | 107
Units with an unexpected row count (VAV0063 excluded) | 0
Corrupted cells outstanding (rows) | 36
2. Findings
VAV0063 has been reviewed and accepted — it is NOT counted as a red flag. It has 23 rows (no rec:feeds triple) and #N/A in the object of its rec:locatedIn row; both are excluded below by decision, not by evidence.
Excluding VAV0063, all remaining 107 VAVs have exactly 24 rows and the same predicate profile: 1 hasPart, 8 hasPoint, 1 isPartOf, 1 ratedReheatCapacity, 1 ratedSupplyAirFlowrate, 1 isFedBy, 1 locatedIn, 1 feeds, 9 external references.
DATA CORRUPTION — 36 rows have the number 130 in the object column. 18 are structural (hasPart/hasPoint objects that should name an entity) and 18 are reference triples whose object should be <blanknode>. See section 4.
VAV0101: 10 corrupted rows (1 structural + 9 references). VAV0102: 18 corrupted rows (9 structural + 9 references). VAV0103: 8 corrupted rows (all structural; its reference triples are intact). 130 is a supply-air-flowrate value, so a parameter column appears to have been pasted over the object column.
These three units are the outstanding issue: 3 of 108 VAVs carry broken references.
Row counts alone hide all of this — VAV0101, VAV0102 and VAV0103 each still total 24 rows, so only a content check catches them.
3. Structural completeness — each relation should appear exactly 108 times, once per unit
Relation | Predicate | Matched on | Actual count | Status
Damper_Controller part | brick:hasPart | entity:SSC_VAV*_Damper_Controller | 106 | MISSING 2 of 108
Air_Flow_Sensor point | brick:hasPoint | entity:SSC_VAV*_Air_Flow_Sensor | 106 | MISSING 2 of 108
ActiveState_CALC point | brick:hasPoint | entity:SSC_VAV*_ActiveState_CALC | 106 | MISSING 2 of 108
TotalOperationDuration point | brick:hasPoint | entity:SSC_VAV*_TotalOperationDuration | 106 | MISSING 2 of 108
Effective_Temp_Setpoint point | brick:hasPoint | entity:SSC_VAV*_Effective_Temp_Setpoint | 106 | MISSING 2 of 108
Room_Temperature point | brick:hasPoint | entity:SSC_VAV*_Room_Temperature | 106 | MISSING 2 of 108
Temperature_Setpoint point | brick:hasPoint | entity:SSC_VAV*_Temperature_Setpoint | 106 | MISSING 2 of 108
Occupancy_Status point | brick:hasPoint | entity:SSC_VAV*_Occupancy_Status | 106 | MISSING 2 of 108
Damper_Position under controller | brick:hasPoint | entity:SSC_VAV*_Damper_Position | 106 | MISSING 2 of 108
isPartOf (system) | brick:isPartOf | predicate only | 108 | OK
ratedReheatCapacity | para:ratedReheatCapacity | predicate only | 108 | OK
ratedSupplyAirFlowrate | para:ratedSupplyAirFlowrate | predicate only | 108 | OK
rec:isFedBy (parent AHU) | rec:isFedBy | predicate only | 108 | OK
rec:locatedIn (room) | rec:locatedIn | predicate only | 108 | OK
rec:feeds (served space) | rec:feeds | predicate only | 107 | OK (107 + VAV0063 excluded)
Ref — VAV itself | ref:hasExternalReference | entity:SSC_VAV0??? | 108 | OK
Ref — Air_Flow_Sensor | ref:hasExternalReference | entity:SSC_VAV*_Air_Flow_Sensor | 108 | OK
Ref — ActiveState_CALC | ref:hasExternalReference | entity:SSC_VAV*_ActiveState_CALC | 108 | OK
Ref — TotalOperationDuration | ref:hasExternalReference | entity:SSC_VAV*_TotalOperationDuration | 108 | OK
Ref — Effective_Temp_Setpoint | ref:hasExternalReference | entity:SSC_VAV*_Effective_Temp_Setpoint | 108 | OK
Ref — Room_Temperature | ref:hasExternalReference | entity:SSC_VAV*_Room_Temperature | 108 | OK
Ref — Temperature_Setpoint | ref:hasExternalReference | entity:SSC_VAV*_Temperature_Setpoint | 108 | OK
Ref — Occupancy_Status | ref:hasExternalReference | entity:SSC_VAV*_Occupancy_Status | 108 | OK
Ref — Damper_Position | ref:hasExternalReference | entity:SSC_VAV*_Damper_Position | 108 | OK
Reference triples with a corrupted object | ref:hasExternalReference | object should be <blanknode> | 18 | CORRUPT — 18 rows
4. Corrupted rows — object column holds the number 130 instead of an entity name or <blanknode> (VAV0063 row greyed out as accepted)
Sheet row | Subject | Predicate | Object cell (live) | What it should be
3931 | entity:SSC_VAV0063 | rec:locatedIn | #N/A in source | #N/A in source — excluded, VAV0063 reviewed and accepted
4806 | entity:SSC_VAV0101 | ref:hasExternalReference | 130 | should be <blanknode> (IFC reference)
4807 | entity:SSC_VAV0101_ActiveState_CALC | ref:hasExternalReference | 130 | should be <blanknode>
4808 | entity:SSC_VAV0101_Air_Flow_Sensor | ref:hasExternalReference | 130 | should be <blanknode>
4809 | entity:SSC_VAV0101_Damper_Controller | brick:hasPoint | 130 | should be entity:SSC_VAV0101_Damper_Position
4810 | entity:SSC_VAV0101_Damper_Position | ref:hasExternalReference | 130 | should be <blanknode>
4811 | entity:SSC_VAV0101_Effective_Temp_Setpoint | ref:hasExternalReference | 130 | should be <blanknode>
4812 | entity:SSC_VAV0101_Occupancy_Status | ref:hasExternalReference | 130 | should be <blanknode>
4813 | entity:SSC_VAV0101_Room_Temperature | ref:hasExternalReference | 130 | should be <blanknode>
4814 | entity:SSC_VAV0101_Temperature_Setpoint | ref:hasExternalReference | 130 | should be <blanknode>
4815 | entity:SSC_VAV0101_TotalOperationDuration | ref:hasExternalReference | 130 | should be <blanknode>
4816 | entity:SSC_VAV0102 | brick:hasPart | 130 | should be entity:SSC_VAV0102_Damper_Controller
4817 | entity:SSC_VAV0102 | brick:hasPoint | 130 | should be entity:SSC_VAV0102_Air_Flow_Sensor
4818 | entity:SSC_VAV0102 | brick:hasPoint | 130 | should be entity:SSC_VAV0102_ActiveState_CALC
4819 | entity:SSC_VAV0102 | brick:hasPoint | 130 | should be entity:SSC_VAV0102_TotalOperationDuration
4820 | entity:SSC_VAV0102 | brick:hasPoint | 130 | should be entity:SSC_VAV0102_Effective_Temp_Setpoint
4821 | entity:SSC_VAV0102 | brick:hasPoint | 130 | should be entity:SSC_VAV0102_Room_Temperature
4822 | entity:SSC_VAV0102 | brick:hasPoint | 130 | should be entity:SSC_VAV0102_Temperature_Setpoint
4823 | entity:SSC_VAV0102 | brick:hasPoint | 130 | should be entity:SSC_VAV0102_Occupancy_Status
4829 | entity:SSC_VAV0102 | ref:hasExternalReference | 130 | should be <blanknode> (IFC reference)
4830 | entity:SSC_VAV0102_ActiveState_CALC | ref:hasExternalReference | 130 | should be <blanknode>
4831 | entity:SSC_VAV0102_Air_Flow_Sensor | ref:hasExternalReference | 130 | should be <blanknode>
4832 | entity:SSC_VAV0102_Damper_Controller | brick:hasPoint | 130 | should be entity:SSC_VAV0102_Damper_Position
4833 | entity:SSC_VAV0102_Damper_Position | ref:hasExternalReference | 130 | should be <blanknode>
4834 | entity:SSC_VAV0102_Effective_Temp_Setpoint | ref:hasExternalReference | 130 | should be <blanknode>
4835 | entity:SSC_VAV0102_Occupancy_Status | ref:hasExternalReference | 130 | should be <blanknode>
4836 | entity:SSC_VAV0102_Room_Temperature | ref:hasExternalReference | 130 | should be <blanknode>
4837 | entity:SSC_VAV0102_Temperature_Setpoint | ref:hasExternalReference | 130 | should be <blanknode>
4838 | entity:SSC_VAV0102_TotalOperationDuration | ref:hasExternalReference | 130 | should be <blanknode>
4839 | entity:SSC_VAV0103 | brick:hasPart | 130 | should be entity:SSC_VAV0103_Damper_Controller
4840 | entity:SSC_VAV0103 | brick:hasPoint | 130 | should be entity:SSC_VAV0103_Air_Flow_Sensor
4841 | entity:SSC_VAV0103 | brick:hasPoint | 130 | should be entity:SSC_VAV0103_ActiveState_CALC
4842 | entity:SSC_VAV0103 | brick:hasPoint | 130 | should be entity:SSC_VAV0103_TotalOperationDuration
4843 | entity:SSC_VAV0103 | brick:hasPoint | 130 | should be entity:SSC_VAV0103_Effective_Temp_Setpoint
4844 | entity:SSC_VAV0103 | brick:hasPoint | 130 | should be entity:SSC_VAV0103_Room_Temperature
4845 | entity:SSC_VAV0103 | brick:hasPoint | 130 | should be entity:SSC_VAV0103_Temperature_Setpoint
4846 | entity:SSC_VAV0103 | brick:hasPoint | 130 | should be entity:SSC_VAV0103_Occupancy_Status
5. Row count per unit (expected 24)
Unit | Rows | Status
VAV0001 | 24 | OK
VAV0002 | 24 | OK
VAV0003 | 24 | OK
VAV0004 | 24 | OK
VAV0005 | 24 | OK
VAV0006 | 24 | OK
VAV0007 | 24 | OK
VAV0008 | 24 | OK
VAV0009 | 24 | OK
VAV0010 | 24 | OK
VAV0011 | 24 | OK
VAV0012 | 24 | OK
VAV0013 | 24 | OK
VAV0014 | 24 | OK
VAV0015 | 24 | OK
VAV0016 | 24 | OK
VAV0017 | 24 | OK
VAV0018 | 24 | OK
VAV0019 | 24 | OK
VAV0020 | 24 | OK
VAV0021 | 24 | OK
VAV0022 | 24 | OK
VAV0023 | 24 | OK
VAV0024 | 24 | OK
VAV0025 | 24 | OK
VAV0026 | 24 | OK
VAV0027 | 24 | OK
VAV0028 | 24 | OK
VAV0029 | 24 | OK
VAV0030 | 24 | OK
VAV0031 | 24 | OK
VAV0032 | 24 | OK
VAV0033 | 24 | OK
VAV0034 | 24 | OK
VAV0035 | 24 | OK
VAV0036 | 24 | OK
VAV0037 | 24 | OK
VAV0038 | 24 | OK
VAV0039 | 24 | OK
VAV0040 | 24 | OK
VAV0041 | 24 | OK
VAV0042 | 24 | OK
VAV0043 | 24 | OK
VAV0044 | 24 | OK
VAV0045 | 24 | OK
VAV0046 | 24 | OK
VAV0047 | 24 | OK
VAV0048 | 24 | OK
VAV0049 | 24 | OK
VAV0050 | 24 | OK
VAV0051 | 24 | OK
VAV0052 | 24 | OK
VAV0053 | 24 | OK
VAV0054 | 24 | OK
VAV0055 | 24 | OK
VAV0056 | 24 | OK
VAV0057 | 24 | OK
VAV0058 | 24 | OK
VAV0059 | 24 | OK
VAV0060 | 24 | OK
VAV0061 | 24 | OK
VAV0062 | 24 | OK
VAV0063 | 23 | Excluded — reviewed, accepted
VAV0064 | 24 | OK
VAV0065 | 24 | OK
VAV0066 | 24 | OK
VAV0067 | 24 | OK
VAV0068 | 24 | OK
VAV0069 | 24 | OK
VAV0070 | 24 | OK
VAV0071 | 24 | OK
VAV0072 | 24 | OK
VAV0073 | 24 | OK
VAV0074 | 24 | OK
VAV0075 | 24 | OK
VAV0076 | 24 | OK
VAV0077 | 24 | OK
VAV0078 | 24 | OK
VAV0079 | 24 | OK
VAV0080 | 24 | OK
VAV0081 | 24 | OK
VAV0082 | 24 | OK
VAV0083 | 24 | OK
VAV0084 | 24 | OK
VAV0085 | 24 | OK
VAV0086 | 24 | OK
VAV0087 | 24 | OK
VAV0088 | 24 | OK
VAV0089 | 24 | OK
VAV0090 | 24 | OK
VAV0091 | 24 | OK
VAV0092 | 24 | OK
VAV0093 | 24 | OK
VAV0094 | 24 | OK
VAV0095 | 24 | OK
VAV0096 | 24 | OK
VAV0097 | 24 | OK
VAV0098 | 24 | OK
VAV0099 | 24 | OK
VAV0100 | 24 | OK
VAV0101 | 24 | OK
VAV0102 | 24 | OK
VAV0103 | 24 | OK
VAV0104 | 24 | OK
VAV0105 | 24 | OK
VAV0106 | 24 | OK
VAV0107 | 24 | OK
VAV0108 | 24 | OK