## SSC_Ontology_Ver0.4
Subject | subjectType | predicate | object | objectType | subject_prop_name | subject_prop_val | object_prop_name | object_prop_val | subject_prop_name | subject_prop_val | object_prop_name | object_prop_val | subject_prop_name | subject_prop_val | object_prop_name | object_prop_val | subject_prop_name | subject_prop_val | object_prop_name | object_prop_val | subject_prop_name | subject_prop_val | object_prop_name | object_prop_val | subject_prop_name | subject_prop_val
entity:SSC_01_001_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.001_CORRIDOR
entity:SSC_01_002_SHELL_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.002_SHELL SPACE
entity:SSC_01_003_OPEN_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.003_OPEN SPACE
entity:SSC_01_004_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.004_CORRIDOR
entity:SSC_01_005_KITCHEN | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.005_KITCHEN
entity:SSC_01_006_MALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.006_MALE TOILET
entity:SSC_01_007_FEMALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.007_FEMALE TOILET
entity:SSC_01_008_AV_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.008_A / V ROOM
entity:SSC_01_009_AUDITORIUM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.009_AUDITORIUM MEETING ROOM
entity:SSC_01_010_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.01_CORRIDOR
entity:SSC_01_011_AIR_LOCK | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.011_AIR LOCK
entity:SSC_01_012_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.012_STORAGE
entity:SSC_01_013_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.013_CORRIDOR
entity:SSC_01_014_SHELL_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.014_SHELL SPACE
entity:SSC_01_015_SHELL_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.015_SHELL SPACE
entity:SSC_01_016_SHELL_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.016_SHELL SPACE
entity:SSC_01_017_FEMALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.017_FEMALE TOILET
entity:SSC_01_018_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.018_CORRIDOR
entity:SSC_01_019_PRAYER_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.019_PRAYER ROOM
entity:SSC_01_020_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.02_CORRIDOR
entity:SSC_01_021_ABLUTION_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.021_ABLUTION ROOM
entity:SSC_01_022_ABLUTION_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.022_ABLUTION ROOM
entity:SSC_01_023_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.023_CORRIDOR
entity:SSC_01_024_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.024_CORRIDOR
entity:SSC_01_025_MALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.025_MALE TOILET
entity:SSC_01_026_STORAGE_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.026_FURNITURE STORAGE
entity:SSC_01_027_IDF_1 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.027_IDF - 1
entity:SSC_01_028_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.028_CORRIDOR
entity:SSC_01_029_ROOM_NO_42 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.029_SHELL SPACE
entity:SSC_01_029_ROOM_NO_43 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.029_SHELL SPACE
entity:SSC_01_029_ROOM_NO_44 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.029_SHELL SPACE
entity:SSC_01_029_SHELL_SPACE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.029_SHELL SPACE
entity:SSC_01_030_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.03_STORAGE
entity:SSC_01_031_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.031_TOILET
entity:SSC_01_032_VESTIBULE | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.032_VESTIBULE
entity:SSC_01_033_JANITORS_CLOSET | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.033_JANITORS CLOSET
entity:SSC_01_034_AIR_LOCK | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.034_AIR LOCK
entity:SSC_01_035_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.035_CORRIDOR
entity:SSC_01_036_OUTDOOR_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.036_OUTDOOR AREA
entity:SSC_01_037_OUTDOOR_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.037_OUTDOOR AREA
entity:SSC_01_038_STORAGE_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.038_STORAGE AREA
entity:SSC_01_039_IDF_2 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.039_IDF - 2
entity:SSC_01_041_STORAGE_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 1.041_STORAGE
entity:SSC_01_P-1_P-1 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.P-1_LIFT
entity:SSC_01_P-2_P-2 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.P-2_LIFT
entity:SSC_01_ST-1_STAIR-1 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-1_STAIR-1
entity:SSC_01_ST-2_STAIR-2 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-2_STAIR-2
entity:SSC_01_ST-3_STAIR-3 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-3_STAIR-3
entity:SSC_01_ST-4_STAIR_4 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-4_STAIR-4
entity:SSC_01_ST-5_STAIR-5 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-5_STAIR-5
entity:SSC_01_ST-8_STAIR-8 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-8_STAIR-8
entity:SSC_01_ST-9_STAIR-9 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | 01.ST-9_STAIR-9
entity:SSC_02_001_FOYER | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.001_FOYER
entity:SSC_02_002_LOBBY | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.002_LOBBY
entity:SSC_02_003_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.003_CORRIDOR
entity:SSC_02_004_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.004_CORRIDOR
entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.005_EXECUTIVE CONFERENCE ROOM
entity:SSC_02_006_CONFERENCE_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.006_CONFERENCE ROOM
entity:SSC_02_007_MEZZANINE | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.007_MEZZANINE
entity:SSC_02_008_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.008_TOILET
entity:SSC_02_010_VESTIBULE | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 2.01_VESTIBULE
entity:SSC_02_P-1_LIFT | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 02.P-1_LIFT
entity:SSC_02_P-2_LIFT | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 02.P-2_LIFT
entity:SSC_02_ST-1_STAIR-1 | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 02.ST-1_STAIR-1
entity:SSC_02_ST-2_STAIR-2 | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 02.ST-2_STAIR-2
entity:SSC_02_ST-8_STAIR-8 | rec:Room | rec:isPartOf | entity:SSC_Level-02 | rec:Level | rdfs:label_en | 02.ST-8_STAIR-8
entity:SSC_03_001_DIRECTORS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.001_DIRECTOR'S OFFICE
entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.002_DIRECTOR'S MEETING ROOM
entity:SSC_03_003_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.003_RESEARCHER'S OFFICE
entity:SSC_03_004_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.004_VISITOR'S CUBICLE
entity:SSC_03_005_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.005_RESEARCHER'S OFFICE
entity:SSC_03_006_MEETING_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.006_MEETING ROOM
entity:SSC_03_007_OPERATIONS_MANAGER | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.007_OPERATIONS MANAGER
entity:SSC_03_008_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.008_VISITOR'S CUBICLE
entity:SSC_03_009_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.009_RESEARCHER'S OFFICE
entity:SSC_03_010_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.01_RESEARCHER'S OFFICE
entity:SSC_03_011_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.011_VISITOR'S CUBICLE
entity:SSC_03_012_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.012_RESEARCHER'S OFFICE
entity:SSC_03_013_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.013_RESEARCHER'S OFFICE
entity:SSC_03_014_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.014_VISITOR'S CUBICLE
entity:SSC_03_015_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.015_RESEARCHER'S OFFICE
entity:SSC_03_016_LOUNGE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.016_LOUNGE
entity:SSC_03_017_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.017_RESEARCHER'S OFFICE
entity:SSC_03_018_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.018_VISITOR'S CUBICLE
entity:SSC_03_019_IT_MANAGERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.019_IT MANAGER'S OFFICE
entity:SSC_03_020_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.02_RESEARCHER'S OFFICE
entity:SSC_03_021_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.021_VISITOR'S CUBICLE
entity:SSC_03_022_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.022_RESEARCHER'S OFFICE
entity:SSC_03_023_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.023_RESEARCHER'S OFFICE
entity:SSC_03_024_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.024_VISITOR'S CUBICLE
entity:SSC_03_025_SECRETARIAL_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.025_SECRETARIAL AREA
entity:SSC_03_026_MEETING_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.026_MEETING ROOM
entity:SSC_03_027_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.027_RESEARCHER'S OFFICE
entity:SSC_03_028_VISITORS_CUBICLE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.028_VISITOR'S CUBICLE
entity:SSC_03_029_RESEARCHERS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.029_RESEARCHER'S OFFICE
entity:SSC_03_030_ASSOC_DIRECTORS_MEETING_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.03_ASSOC. DIRECTOR'S MEETING ROOM
entity:SSC_03_031_ASSOC_DIRECTORS_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.031_ASSOC. DIRECTOR'S OFFICE
entity:SSC_03_032_GENERAL_OFFICE_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.032_GENERAL OFFICE AREA
entity:SSC_03_033_PRINTING | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.033_PRINTING
entity:SSC_03_034_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.034_CORRIDOR
entity:SSC_03_035_STUDY_LIBRARY_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.035_STUDY LIBRARY AREA
entity:SSC_03_036_KITCHEN | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.036_KITCHEN
entity:SSC_03_037_MALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.037_MALE TOILET
entity:SSC_03_038_SERVER_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.038_IT SERVER ROOM
entity:SSC_03_039_FEMALE_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.039_FEMALE TOILET
entity:SSC_03_040_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.04_CORRIDOR
entity:SSC_03_041_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.041_CORRIDOR
entity:SSC_03_042_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.042_CORRIDOR
entity:SSC_03_043_EXTERIOR_COURTYARD | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.043_EXTERIOR COURTYARD
entity:SSC_03_044_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.044_CORRIDOR
entity:SSC_03_045_JANITORS_CLOSET | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.045_JANITOR'S CLOSET
entity:SSC_03_046_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.046_STORAGE
entity:SSC_03_047_BALCONY | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.047_BALCONY
entity:SSC_03_048_BALCONY | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.048_BALCONY
entity:SSC_03_049_IT_OFFICE | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 3.049_IT OFFICE
entity:SSC_03_F7_1_PODIUM | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 03.F7.1_PODIUM
entity:SSC_03_P-1_LIFT | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 03.P-1_LIFT
entity:SSC_03_P-2_LIFT | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 03.P-2_LIFT
entity:SSC_03_ST-1_STAIR-1 | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 03.ST-1_STAIR-1
entity:SSC_03_ST-2_STAIR-2 | rec:Room | rec:isPartOf | entity:SSC_Level-03 | rec:Level | rdfs:label_en | 03.ST-2_STAIR-2
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_Filter | brick:Filter |  |  | rdfs:label_en | Pre Filter and Bag Filter
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_OAD | brick:Outside_Damper |  |  | rdfs:label_en | Outside Air Damper
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_RAD | brick:Return_Damper |  |  | rdfs:label_en | Return Air Damper
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_MAD | brick:Mixed_Damper |  |  | rdfs:label_en | Mixed Air Damper
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_EAD | brick:Exhaust_Damper |  |  | rdfs:label_en | Exhaust Air Damper
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_RF | brick:Return_Fan |  |  | rdfs:label_en | Return Fan
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0001_Heater | brick:Heater |  |  | rdfs:label_en | Heater
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_OA_RH | brick:Outside_Air_Humidity_Sensor |  |  | rdfs:label_en | Fresh Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_OA_Temperature | brick:Outside_Air_Temperature_Sensor |  |  | rdfs:label_en | Fresh Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_RA_RH | brick:Return_Air_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_RA_Temperature | brick:Return_Air_Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_RA_Flow | brick:Return_Air_Flow_Sensor |  |  | rdfs:label_en | Return Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_MA_Temperature | brick:Mixed_Air_Temperature_Sensor |  |  | rdfs:label_en | Mixed Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_SA_Flow | brick:Supply_Air_Flow_Sensor |  |  | rdfs:label_en | Supply Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_SA_RH | brick:Supply_Air_Humidity_Sensor |  |  | rdfs:label_en | Supply Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_SAT | brick:Supply_Air_Temperature_Sensor |  |  | rdfs:label_en | Supply Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_Occupancy_Mode | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_Dehum_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Dehumidification Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_Occ_Temp_Setpoint | brick:Occupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_SAP_Setpoint | brick:Static_Pressure_Setpoint |  |  | rdfs:label_en | Pressure Setpoint |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Unoccupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_Enable_Disable_Cmd | brick:System_Enable_Command |  |  | rdfs:label_en | AHU Enable Disable Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_Pressure_High_Filter_Dirty_Status | brick:Filter_Status |  |  | rdfs:label_en | Pressure high Filter Dirty Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_High_Pressure_Alarm | brick:Pressure_Alarm |  |  | rdfs:label_en | Pressure Switch High |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_SA_P-Static | brick:Static_Pressure_Sensor |  |  | rdfs:label_en | Supply Air Duct Remote Pressure 01 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0001_RA_P-Static | para:Return_Air_Static_Pressure_Sensor |  |  | rdfs:label_en | Return Air Duct Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_AHUB0001 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | para:ratedOutsideAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 570 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | para:ratedSupplyAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 3800 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rec:isFedBy | <FedByASSET> | para:Chilled_Water_Loop_Network
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rec:locatedIn | entity:SSC_B1_013_CHILLED_WATER | rec:Room
entity:SSC_AHUB0001 | brick:Air_Handling_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_AHUB0001 |  |  | ref:ifcName | SSC_AHUB0001
entity:SSC_AHUB0001_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 29.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0001_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_AHUB0001_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_AHUB0001_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPart | entity:SSC_AHUB0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | Cooling Thermal Power Meter
entity:SSC_AHUB0001_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0001_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command |  |  | rdfs:label_en | Cooling Valve Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0001_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Cooling Valve Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_CoolVlv.PosCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_CoolVlv.PosFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0001_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Load Consumption |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_AHUB0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0001_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Load Demand |  |  | brick:hasUnit | para:KiloWt
entity:SSC_AHUB0001_Dehum_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SP.DehumSP |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0001_EAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Exhaust Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0001_EAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Exhaust Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0001_EAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Exhaust Fan Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_EAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_ExhDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_EAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_ExhDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_EAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001.ExAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Enable_Disable_Cmd | brick:System_Enable_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001.EnableDisableCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Heater | brick:Heater | brick:hasPoint | entity:SSC_AHUB0001_Heater_Command | brick:Heating_Command |  |  | rdfs:label_en | Heater Control |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_Heater_Command | brick:Heating_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupHtr.HtrCtrl |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_High_Pressure_Alarm | brick:Pressure_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SP.PressSWHigh |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_MA_Temperature | brick:Mixed_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_MixAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0001_MAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Mixed Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0001_MAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Mixed Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_MAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_MixDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_MAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_MixDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_OA_RH | brick:Outside_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_FrshAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_OA_Temperature | brick:Outside_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_FrshAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0001_OAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Fresh Air Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0001_OAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Fresh Air Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0001_OAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Fresh Air Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_OAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_FrshDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_OAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_FrshDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_OAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001.FrshAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SP.OccTempSP |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Occupancy_Mode | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001.OccMode |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_Pressure_High_Filter_Dirty_Status | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupPreFlt.PressureHigh |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RA_Flow | brick:Return_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RA_P-Static | para:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirDuctPrs.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RA_RH | brick:Return_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RA_Temperature | brick:Return_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 |  |  | rdfs:label_en | Damper Position 100 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 |  |  | rdfs:label_en | Damper Position 70 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 |  |  | rdfs:label_en | Damper Position 77.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 |  |  | rdfs:label_en | Damper Position 85 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 |  |  | rdfs:label_en | Damper Position 92.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0001_MinFALoocupTb.RecDmprPos100 |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0001_MinFALoocupTb.RecDmprPos70 |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0001_MinFALoocupTb.RecDmprPos77.5 |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0001_MinFALoocupTb.RecDmprPos85 |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0001_MinFALoocupTb.RecDmprPos92.5 |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF | brick:Return_Fan | brick:hasPart | entity:SSC_AHUB0001_RF_Motor | brick:Motor |  |  | rdfs:label_en | Return Fan Motor
entity:SSC_AHUB0001_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0001_RF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Return Fan AutoMan_Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0001_RF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Return Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_RF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0001_RF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0001_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0001_RF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Return Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0001_RF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Return Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0001_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0001_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Return Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0001_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0001_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Return Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0001_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.kWh |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.kW |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_RF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SA_Flow | brick:Supply_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupAirDuctPrsRmt1.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SA_RH | brick:Supply_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SAP_Setpoint | brick:Static_Pressure_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SP.PressSP |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SAT | brick:Supply_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_AHUB0001_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0001_SF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Supplu Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0001_SF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Supply Fan Auto Man Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0001_SF_FailtoStop | para:Fail_Stop_Alarm |  |  | rdfs:label_en | Supply Fan Fail to Stop |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0001_SF_FailtoStart | para:Fail_Start_Alarm |  |  | rdfs:label_en | Supply Fan FailtoStart |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0001_SF_Status | brick:On_Off_Status |  |  | rdfs:label_en | Supply Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0001_SF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_FailtoStart | para:Fail_Start_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.FTST |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_FailtoStop | para:Fail_Stop_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.FTSP |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0001_SF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0001_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0001_SF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Supply Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0001_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0001_SF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Supply Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0001_SF_Motor | brick:Motor | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value | 50 |  |  | brick:hasUnit | unit:HZ
entity:SSC_AHUB0001_SF_Motor | brick:Motor | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value | 11 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0001_SF_Motor | brick:Motor | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value | 415 |  |  | brick:hasUnit | unit:V
entity:SSC_AHUB0001_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.kWh |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0001_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Supply Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0001_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0001_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Supply Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0001_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.kW |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001.SupFanSts |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_SF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SupFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0001_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_SP.UnOccTempSP |  |  | para:hasEntityId | SSC_AHUB0001
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_Filter | brick:Filter |  |  | rdfs:label_en | Pre Filter and Bag Filter
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_OAD | brick:Outside_Damper |  |  | rdfs:label_en | Outside Air Damper
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_RAD | brick:Return_Damper |  |  | rdfs:label_en | Return Air Damper
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_MAD | brick:Mixed_Damper |  |  | rdfs:label_en | Mixed Air Damper
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_EAD | brick:Exhaust_Damper |  |  | rdfs:label_en | Exhaust Air Damper
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_RF | brick:Return_Fan |  |  | rdfs:label_en | Return Fan
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0002_Heater | brick:Heater |  |  | rdfs:label_en | Heater
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_OA_RH | brick:Outside_Air_Humidity_Sensor |  |  | rdfs:label_en | Fresh Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_OA_Temperature | brick:Outside_Air_Temperature_Sensor |  |  | rdfs:label_en | Fresh Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_RA_RH | brick:Return_Air_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_RA_Temperature | brick:Return_Air_Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_RA_Flow | brick:Return_Air_Flow_Sensor |  |  | rdfs:label_en | Return Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_MA_Temperature | brick:Mixed_Air_Temperature_Sensor |  |  | rdfs:label_en | Mixed Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_SA_Flow | brick:Supply_Air_Flow_Sensor |  |  | rdfs:label_en | Supply Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_SA_RH | brick:Supply_Air_Humidity_Sensor |  |  | rdfs:label_en | Supply Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_SAT | brick:Supply_Air_Temperature_Sensor |  |  | rdfs:label_en | Supply Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_Occupancy_Mode | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_Dehum_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Dehumidification Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_SAP_Setpoint | brick:Static_Pressure_Setpoint |  |  | rdfs:label_en | Pressure Setpoint |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Unoccupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_Enable_Disable_Cmd | brick:System_Enable_Command |  |  | rdfs:label_en | AHU Enable Disable Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_Pressure_High_Filter_Dirty_Status | brick:Filter_Status |  |  | rdfs:label_en | Pressure high Filter Dirty Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_High_Pressure_Alarm | brick:Pressure_Alarm |  |  | rdfs:label_en | Pressure Switch High |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_SA_P-Static | brick:Static_Pressure_Sensor |  |  | rdfs:label_en | Supply Air Duct Remote Pressure 02 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0002_RA_P-Static | para:Return_Air_Static_Pressure_Sensor |  |  | rdfs:label_en | Return Air Duct Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_AHUB0002 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | para:ratedOutsideAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 1440 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | para:ratedSupplyAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 9800 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rec:isFedBy | <FedByASSET> | para:Chilled_Water_Loop_Network
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_AHUB0002 | brick:Air_Handling_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_AHUB0002 |  |  | ref:ifcName | SSC_AHUB0002
entity:SSC_AHUB0002_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 29.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0002_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_AHUB0002_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_AHUB0002_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPart | entity:SSC_AHUB0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | Cooling Thermal Power Meter
entity:SSC_AHUB0002_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0002_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command |  |  | rdfs:label_en | Cooling Valve Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0002_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Cooling Valve Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_CoolVlv.PosCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_CoolVlv.PosFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0002_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Load Consumption |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_AHUB0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0002_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Load Demand |  |  | brick:hasUnit | para:KiloWt
entity:SSC_AHUB0002_Dehum_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SP.DehumSP |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0002_EAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Exhaust Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0002_EAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Exhaust Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0002_EAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Exhaust Fan Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_EAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_ExhDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_EAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_ExhDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_EAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002.ExAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Enable_Disable_Cmd | brick:System_Enable_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002.EnableDisableCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Heater | brick:Heater | brick:hasPoint | entity:SSC_AHUB0002_Heater_Command | brick:Heating_Command |  |  | rdfs:label_en | Heater Control |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_Heater_Command | brick:Heating_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupHtr.HtrCtrl |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_High_Pressure_Alarm | brick:Pressure_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SP.PressSWHigh |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_MA_Temperature | brick:Mixed_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_MixAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0002_MAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Mixed Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0002_MAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Mixed Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_MAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_MixDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_MAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_MixDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_OA_RH | brick:Outside_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_FrshAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_OA_Temperature | brick:Outside_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_FrshAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0002_OAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Fresh Air Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0002_OAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Fresh Air Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0002_OAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Fresh Air Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_OAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_FrshDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_OAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_FrshDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_OAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002.FrshAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SP.OccTempSP |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Occupancy_Mode | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002.OccMode |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_Pressure_High_Filter_Dirty_Status | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupPreFlt.PressureHigh |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RA_Flow | brick:Return_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RA_P-Static | para:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirDuctPrs.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RA_RH | brick:Return_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RA_Temperature | brick:Return_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 |  |  | rdfs:label_en | Damper Position 100 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 |  |  | rdfs:label_en | Damper Position 70 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 |  |  | rdfs:label_en | Damper Position 77.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 |  |  | rdfs:label_en | Damper Position 85 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 |  |  | rdfs:label_en | Damper Position 92.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0002_MinFALoocupTb.RecDmprPos100 |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0002_MinFALoocupTb.RecDmprPos70 |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0002_MinFALoocupTb.RecDmprPos77.5 |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0002_MinFALoocupTb.RecDmprPos85 |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0002_MinFALoocupTb.RecDmprPos92.5 |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF | brick:Return_Fan | brick:hasPart | entity:SSC_AHUB0002_RF_Motor | brick:Motor |  |  | rdfs:label_en | Return Fan Motor
entity:SSC_AHUB0002_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0002_RF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Return Fan AutoMan_Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0002_RF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Return Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_RF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0002_RF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0002_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0002_RF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Return Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0002_RF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Return Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0002_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0002_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Return Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0002_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0002_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Return Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0002_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.kWh |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.kW |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_RF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_RtnFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SA_Flow | brick:Supply_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupAirDuctPrsRmt2.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupAirDuctPrsRmt1.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SA_RH | brick:Supply_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SAP_Setpoint | brick:Static_Pressure_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SP.PressSP |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SAT | brick:Supply_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_AHUB0002_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0002_SF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Supplu Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0002_SF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Supply Fan Auto Man Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0002_SF_FailtoStop | para:Fail_Stop_Alarm |  |  | rdfs:label_en | Supply Fan Fail to Stop |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0002_SF_FailtoStart | para:Fail_Start_Alarm |  |  | rdfs:label_en | Supply Fan FailtoStart |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0002_SF_Status | brick:On_Off_Status |  |  | rdfs:label_en | Supply Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0002_SF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_FailtoStart | para:Fail_Start_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.FTST |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_FailtoStop | para:Fail_Stop_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.FTSP |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0002_SF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0002_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0002_SF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Supply Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0002_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0002_SF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Supply Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0002_SF_Motor | brick:Motor | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value | 50 |  |  | brick:hasUnit | unit:HZ
entity:SSC_AHUB0002_SF_Motor | brick:Motor | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value | 22 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0002_SF_Motor | brick:Motor | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value | 415 |  |  | brick:hasUnit | unit:V
entity:SSC_AHUB0002_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.kWh |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0002_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Supply Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0002_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0002_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Supply Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0002_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.kW |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002.SupFanSts |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_SF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SupFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0002_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0002_SP.UnOccTempSP |  |  | para:hasEntityId | SSC_AHUB0002
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_Filter | brick:Filter |  |  | rdfs:label_en | Pre Filter and Bag Filter
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_OAD | brick:Outside_Damper |  |  | rdfs:label_en | Outside Air Damper
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_RAD | brick:Return_Damper |  |  | rdfs:label_en | Return Air Damper
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_MAD | brick:Mixed_Damper |  |  | rdfs:label_en | Mixed Air Damper
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_EAD | brick:Exhaust_Damper |  |  | rdfs:label_en | Exhaust Air Damper
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_RF | brick:Return_Fan |  |  | rdfs:label_en | Return Fan
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0003_Heater | brick:Heater |  |  | rdfs:label_en | Heater
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_OA_RH | brick:Outside_Air_Humidity_Sensor |  |  | rdfs:label_en | Fresh Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_OA_Temperature | brick:Outside_Air_Temperature_Sensor |  |  | rdfs:label_en | Fresh Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_RA_RH | brick:Return_Air_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_RA_Temperature | brick:Return_Air_Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_RA_Flow | brick:Return_Air_Flow_Sensor |  |  | rdfs:label_en | Return Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_MA_Temperature | brick:Mixed_Air_Temperature_Sensor |  |  | rdfs:label_en | Mixed Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_SA_Flow | brick:Supply_Air_Flow_Sensor |  |  | rdfs:label_en | Supply Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_SA_RH | brick:Supply_Air_Humidity_Sensor |  |  | rdfs:label_en | Supply Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_SAT | brick:Supply_Air_Temperature_Sensor |  |  | rdfs:label_en | Supply Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_Occupancy_Mode | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_Dehum_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Dehumidification Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Unoccupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_Enable_Disable_Cmd | brick:System_Enable_Command |  |  | rdfs:label_en | AHU Enable Disable Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_Pressure_High_Filter_Dirty_Status | brick:Filter_Status |  |  | rdfs:label_en | Pressure high Filter Dirty Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_High_Pressure_Alarm | brick:Pressure_Alarm |  |  | rdfs:label_en | Pressure Switch High |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_SA_P-Static | brick:Static_Pressure_Sensor |  |  | rdfs:label_en | Supply Air Duct Remote Pressure 02 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0003_RA_P-Static | para:Return_Air_Static_Pressure_Sensor |  |  | rdfs:label_en | Return Air Duct Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_AHUB0003 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | para:ratedOutsideAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 320 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | para:ratedSupplyAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 5700 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rec:isFedBy | <FedByASSET> | para:Chilled_Water_Loop_Network
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | rec:locatedIn | entity:SSC_B1_014_VENT_PLANT | rec:Room
entity:SSC_AHUB0003 | brick:Air_Handling_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_AHUB0003 |  |  | ref:ifcName | SSC_AHUB0003
entity:SSC_AHUB0003_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 29.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0003_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_AHUB0003_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_AHUB0003_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPart | entity:SSC_AHUB0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | Cooling Thermal Power Meter
entity:SSC_AHUB0003_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0003_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command |  |  | rdfs:label_en | Cooling Valve Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0003_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Cooling Valve Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_CoolVlv.PosCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_CoolVlv.PosFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0003_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Load Consumption |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_AHUB0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0003_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Load Demand |  |  | brick:hasUnit | para:KiloWt
entity:SSC_AHUB0003_Dehum_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SP.DehumSP |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0003_EAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Exhaust Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0003_EAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Exhaust Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0003_EAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Exhaust Fan Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_EAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_ExhDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_EAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_ExhDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_EAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003.ExAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Enable_Disable_Cmd | brick:System_Enable_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003.EnableDisableCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Heater | brick:Heater | brick:hasPoint | entity:SSC_AHUB0003_Heater_Command | brick:Heating_Command |  |  | rdfs:label_en | Heater Control |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_Heater_Command | brick:Heating_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupHtr.HtrCtrl |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_High_Pressure_Alarm | brick:Pressure_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SP.PressSWHigh |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_MA_Temperature | brick:Mixed_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_MixAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0003_MAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Mixed Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0003_MAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Mixed Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_MAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_MixDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_MAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_MixDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_OA_RH | brick:Outside_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_FrshAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_OA_Temperature | brick:Outside_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_FrshAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0003_OAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Fresh Air Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0003_OAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Fresh Air Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0003_OAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Fresh Air Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_OAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_FrshDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_OAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_FrshDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_OAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003.FrshAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SP.OccTempSP |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Occupancy_Mode | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003.OccMode |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_Pressure_High_Filter_Dirty_Status | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupPreFlt.PressureHigh |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RA_Flow | brick:Return_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RA_P-Static | para:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirDuctPrs.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RA_RH | brick:Return_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RA_Temperature | brick:Return_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 |  |  | rdfs:label_en | Damper Position 100 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 |  |  | rdfs:label_en | Damper Position 70 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 |  |  | rdfs:label_en | Damper Position 77.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 |  |  | rdfs:label_en | Damper Position 85 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 |  |  | rdfs:label_en | Damper Position 92.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0003_MinFALoocupTb.RecDmprPos100 |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0003_MinFALoocupTb.RecDmprPos70 |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0003_MinFALoocupTb.RecDmprPos77.5 |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0003_MinFALoocupTb.RecDmprPos85 |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0003_MinFALoocupTb.RecDmprPos92.5 |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF | brick:Return_Fan | brick:hasPart | entity:SSC_AHUB0003_RF_Motor | brick:Motor |  |  | rdfs:label_en | Return Fan Motor
entity:SSC_AHUB0003_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0003_RF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Return Fan AutoMan_Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0003_RF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Return Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_RF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0003_RF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0003_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0003_RF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Return Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0003_RF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Return Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0003_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0003_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Return Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0003_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0003_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Return Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0003_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.kWh |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.kW |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_RF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_RtnFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SA_Flow | brick:Supply_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupAirDuctPrsRmt2.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupAirDuctPrsRmt1.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SA_RH | brick:Supply_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SAT | brick:Supply_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_AHUB0003_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0003_SF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Supplu Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0003_SF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Supply Fan Auto Man Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0003_SF_FailtoStop | para:Fail_Stop_Alarm |  |  | rdfs:label_en | Supply Fan Fail to Stop |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0003_SF_FailtoStart | para:Fail_Start_Alarm |  |  | rdfs:label_en | Supply Fan FailtoStart |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0003_SF_Status | brick:On_Off_Status |  |  | rdfs:label_en | Supply Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0003_SF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_FailtoStart | para:Fail_Start_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.FTST |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_FailtoStop | para:Fail_Stop_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.FTSP |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0003_SF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0003_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0003_SF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Supply Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0003_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0003_SF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Supply Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0003_SF_Motor | brick:Motor | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value | 50 |  |  | brick:hasUnit | unit:HZ
entity:SSC_AHUB0003_SF_Motor | brick:Motor | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value | 15 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0003_SF_Motor | brick:Motor | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value | 415 |  |  | brick:hasUnit | unit:V
entity:SSC_AHUB0003_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.kWh |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0003_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Supply Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0003_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0003_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Supply Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0003_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.kW |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003.SupFanSts |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_SF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SupFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0003_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0003_SP.UnOccTempSP |  |  | para:hasEntityId | SSC_AHUB0003
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_Filter | brick:Filter |  |  | rdfs:label_en | Pre Filter and Bag Filter
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_OAD | brick:Outside_Damper |  |  | rdfs:label_en | Outside Air Damper
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_RAD | brick:Return_Damper |  |  | rdfs:label_en | Return Air Damper
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_MAD | brick:Mixed_Damper |  |  | rdfs:label_en | Mixed Air Damper
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_EAD | brick:Exhaust_Damper |  |  | rdfs:label_en | Exhaust Air Damper
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_RF | brick:Return_Fan |  |  | rdfs:label_en | Return Fan
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0004_Heater | brick:Heater |  |  | rdfs:label_en | Heater
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_OA_RH | brick:Outside_Air_Humidity_Sensor |  |  | rdfs:label_en | Fresh Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_OA_Temperature | brick:Outside_Air_Temperature_Sensor |  |  | rdfs:label_en | Fresh Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_RH | brick:Return_Air_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_Temperature | brick:Return_Air_Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_Flow | brick:Return_Air_Flow_Sensor |  |  | rdfs:label_en | Return Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_MA_Temperature | brick:Mixed_Air_Temperature_Sensor |  |  | rdfs:label_en | Mixed Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_SA_Flow | brick:Supply_Air_Flow_Sensor |  |  | rdfs:label_en | Supply Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_SA_RH | brick:Supply_Air_Humidity_Sensor |  |  | rdfs:label_en | Supply Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_SAT | brick:Supply_Air_Temperature_Sensor |  |  | rdfs:label_en | Supply Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_Occupancy_Mode | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_Dehum_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Dehumidification Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_SAP_Setpoint | brick:Static_Pressure_Setpoint |  |  | rdfs:label_en | Pressure Setpoint |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Unoccupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_Enable_Disable_Cmd | brick:System_Enable_Command |  |  | rdfs:label_en | AHU Enable Disable Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_Pressure_High_Filter_Dirty_Status | brick:Filter_Status |  |  | rdfs:label_en | Pressure high Filter Dirty Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_High_Pressure_Alarm | brick:Pressure_Alarm |  |  | rdfs:label_en | Pressure Switch High |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_P-Static_01 | para:Return_Air_Static_Pressure_Sensor_01 |  |  | rdfs:label_en | Return Air Duct Pressure 01 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_P-Static_02 | para:Return_Air_Static_Pressure_Sensor_02 |  |  | rdfs:label_en | Return Air Duct Pressure 02 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_SA_P-Static | brick:Static_Pressure_Sensor |  |  | rdfs:label_en | Supply Air Duct Remote Pressure 02 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0004_RA_P-Static | para:Return_Air_Static_Pressure_Sensor |  |  | rdfs:label_en | Return Air Duct Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_AHUB0004 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | para:ratedOutsideAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 1070 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | para:ratedSupplyAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 7800 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rec:isFedBy | <FedByASSET> | para:Chilled_Water_Loop_Network
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rec:locatedIn | entity:SSC_B1_008_VENT_PLANT | rec:Room
entity:SSC_AHUB0004 | brick:Air_Handling_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_AHUB0004 |  |  | ref:ifcName | SSC_AHUB0004
entity:SSC_AHUB0004_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 29.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0004_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_AHUB0004_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_AHUB0004_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPart | entity:SSC_AHUB0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | Cooling Thermal Power Meter
entity:SSC_AHUB0004_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0004_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command |  |  | rdfs:label_en | Cooling Valve Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0004_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Cooling Valve Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_CoolVlv.PosCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_CoolVlv.PosFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0004_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Load Consumption |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_AHUB0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0004_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Load Demand |  |  | brick:hasUnit | para:KiloWt
entity:SSC_AHUB0004_Dehum_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SP.DehumSP |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0004_EAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Exhaust Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0004_EAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Exhaust Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0004_EAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Exhaust Fan Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_EAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_ExhDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_EAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_ExhDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_EAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004.ExAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Enable_Disable_Cmd | brick:System_Enable_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004.EnableDisableCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Heater | brick:Heater | brick:hasPoint | entity:SSC_AHUB0004_Heater_Command | brick:Heating_Command |  |  | rdfs:label_en | Heater Control |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_Heater_Command | brick:Heating_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupHtr.HtrCtrl |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_High_Pressure_Alarm | brick:Pressure_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SP.PressSWHigh |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_MA_Temperature | brick:Mixed_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_MixAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0004_MAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Mixed Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0004_MAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Mixed Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_MAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_MixDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_MAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_MixDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_OA_RH | brick:Outside_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_FrshAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_OA_Temperature | brick:Outside_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_FrshAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0004_OAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Fresh Air Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0004_OAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Fresh Air Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0004_OAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Fresh Air Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_OAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_FrshDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_OAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_FrshDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_OAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004.FrshAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SP.OccTempSP |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Occupancy_Mode | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004.OccMode |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_Pressure_High_Filter_Dirty_Status | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupPreFlt.PressureHigh |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_Flow | brick:Return_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_P-Static | para:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirDuctPrs.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_P-Static_01 | para:Static_Pressure_Sensor_01 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnAirDuctPrs1.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_P-Static_02 | para:Static_Pressure_Sensor_02 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnAirDuctPrs2.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_RH | brick:Return_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RA_Temperature | brick:Return_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 |  |  | rdfs:label_en | Damper Position 100 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 |  |  | rdfs:label_en | Damper Position 70 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 |  |  | rdfs:label_en | Damper Position 77.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 |  |  | rdfs:label_en | Damper Position 85 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 |  |  | rdfs:label_en | Damper Position 92.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0004_MinFALoocupTb.RecDmprPos100 |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0004_MinFALoocupTb.RecDmprPos70 |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0004_MinFALoocupTb.RecDmprPos77.5 |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0004_MinFALoocupTb.RecDmprPos85 |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0004_MinFALoocupTb.RecDmprPos92.5 |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RF | brick:Return_Fan | brick:hasPart | entity:SSC_AHUB0004_RF_Motor | brick:Motor |  |  | rdfs:label_en | Return Fan Motor
entity:SSC_AHUB0004_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0004_RF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Return Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_RF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0004_RF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0004_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0004_RF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Return Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0004_RF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Return Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0004_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0004_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Return Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0004_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0004_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Return Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0004_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnFanDty.kW |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnFanDty.kWh |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnFanDty.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnFanDty.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_RF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_RtnFanDty.TripAlm |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SA_Flow | brick:Supply_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupAirDuctPrsRmt2.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupAirDuctPrsRmt1.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SA_RH | brick:Supply_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SAP_Setpoint | brick:Static_Pressure_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SP.PressSP |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SAT | brick:Supply_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_AHUB0004_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0004_SF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Supplu Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0004_SF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Supply Fan Auto Man Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0004_SF_FailtoStop | para:Fail_Stop_Alarm |  |  | rdfs:label_en | Supply Fan Fail to Stop |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0004_SF_FailtoStart | para:Fail_Start_Alarm |  |  | rdfs:label_en | Supply Fan FailtoStart |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0004_SF_Status | brick:On_Off_Status |  |  | rdfs:label_en | Supply Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0004_SF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_FailtoStart | para:Fail_Start_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.FTST |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_FailtoStop | para:Fail_Stop_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.FTSP |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0004_SF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0004_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0004_SF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Supply Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0004_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0004_SF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Supply Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0004_SF_Motor | brick:Motor | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value | 50 |  |  | brick:hasUnit | unit:HZ
entity:SSC_AHUB0004_SF_Motor | brick:Motor | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value | 18.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0004_SF_Motor | brick:Motor | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value | 415 |  |  | brick:hasUnit | unit:V
entity:SSC_AHUB0004_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.kWh |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0004_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Supply Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0004_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0004_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Supply Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0004_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.kW |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004.SupFanSts |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_SF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SupFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0004_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0004_SP.UnOccTempSP |  |  | para:hasEntityId | SSC_AHUB0004
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_Filter | brick:Filter |  |  | rdfs:label_en | Pre Filter and Bag Filter
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_OAD | brick:Outside_Damper |  |  | rdfs:label_en | Outside Air Damper
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_RAD | brick:Return_Damper |  |  | rdfs:label_en | Return Air Damper
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_MAD | brick:Mixed_Damper |  |  | rdfs:label_en | Mixed Air Damper
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_EAD | brick:Exhaust_Damper |  |  | rdfs:label_en | Exhaust Air Damper
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_RF | brick:Return_Fan |  |  | rdfs:label_en | Return Fan
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPart | entity:SSC_AHUB0005_Heater | brick:Heater |  |  | rdfs:label_en | Heater
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_OA_RH | brick:Outside_Air_Humidity_Sensor |  |  | rdfs:label_en | Fresh Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_OA_Temperature | brick:Outside_Air_Temperature_Sensor |  |  | rdfs:label_en | Fresh Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_RA_RH | brick:Return_Air_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_RA_Temperature | brick:Return_Air_Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_RA_Flow | brick:Return_Air_Flow_Sensor |  |  | rdfs:label_en | Return Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_MA_Temperature | brick:Mixed_Air_Temperature_Sensor |  |  | rdfs:label_en | Mixed Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_SA_Flow | brick:Supply_Air_Flow_Sensor |  |  | rdfs:label_en | Supply Air Flow |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_SA_RH | brick:Supply_Air_Humidity_Sensor |  |  | rdfs:label_en | Supply Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_SAT | brick:Supply_Air_Temperature_Sensor |  |  | rdfs:label_en | Supply Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_Occupancy_Mode | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_Dehum_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Dehumidification Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Unoccupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_Enable_Disable_Cmd | brick:System_Enable_Command |  |  | rdfs:label_en | AHU Enable Disable Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_Pressure_High_Filter_Dirty_Status | brick:Filter_Status |  |  | rdfs:label_en | Pressure high Filter Dirty Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_High_Pressure_Alarm | brick:Pressure_Alarm |  |  | rdfs:label_en | Pressure Switch High |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_SA_P-Static | brick:Static_Pressure_Sensor |  |  | rdfs:label_en | Supply Air Duct Remote Pressure 01 |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:hasPoint | entity:SSC_AHUB0005_RA_P-Static | para:Return_Air_Static_Pressure_Sensor |  |  | rdfs:label_en | Return Air Duct Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_AHUB0005 |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | para:ratedOutsideAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 850 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | para:ratedSupplyAirFlowrate | <blanknode> | <blanknode> |  |  | brick:value | 2000 l/s |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | rec:isFedBy | <FedByASSET> | para:Chilled_Water_Loop_Network
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | rec:locatedIn | entity:SSC_B1_013_CHILLED_WATER | rec:Room
entity:SSC_AHUB0005 | brick:Air_Handling_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_AHUB0005 |  |  | ref:ifcName | SSC_AHUB0005
entity:SSC_AHUB0005_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 29.5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0005_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_AHUB0005_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_AHUB0005_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPart | entity:SSC_AHUB0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | Cooling Thermal Power Meter
entity:SSC_AHUB0005_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0005_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command |  |  | rdfs:label_en | Cooling Valve Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_CHW-Coil_Valve | brick:Cooling_Valve | brick:hasPoint | entity:SSC_AHUB0005_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Cooling Valve Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_CHW-Coil_Valve_Pos-Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_CoolVlv.PosCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_CHW-Coil_Valve_Pos-Feedback | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_CoolVlv.PosFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0005_CHW-Coil_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Load Consumption |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_AHUB0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_AHUB0005_CHW-Coil_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Load Demand |  |  | brick:hasUnit | para:KiloWt
entity:SSC_AHUB0005_Dehum_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SP.DehumSP |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0005_EAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Exhaust Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0005_EAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Exhaust Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_EAD | brick:Exhaust_Damper | brick:hasPoint | entity:SSC_AHUB0005_EAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Exhaust Fan Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_EAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_ExhDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_EAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_ExhDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_EAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005.ExAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Enable_Disable_Cmd | brick:System_Enable_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005.EnableDisableCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Heater | brick:Heater | brick:hasPoint | entity:SSC_AHUB0005_Heater_Command | brick:Heating_Command |  |  | rdfs:label_en | Heater Control |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_Heater_Command | brick:Heating_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupHtr.HtrCtrl |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_High_Pressure_Alarm | brick:Pressure_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SP.PressSWHigh |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_MA_Temperature | brick:Mixed_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_MixAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0005_MAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Mixed Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_MAD | brick:Mixed_Damper | brick:hasPoint | entity:SSC_AHUB0005_MAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Mixed Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_MAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_MixDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_MAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_MixDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_OA_RH | brick:Outside_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_FrshAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_OA_Temperature | brick:Outside_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_FrshAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0005_OAD_Pos_Cmd | brick:Valve_Position_Command |  |  | rdfs:label_en | Fresh Air Damper Position Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0005_OAD_Pos_Fbk | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Fresh Air Damper Position Feedback |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_OAD | brick:Outside_Damper | brick:hasPoint | entity:SSC_AHUB0005_OAD_Pos-Status | brick:Damper_Position_Status |  |  | rdfs:label_en | Fresh Air Damper Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_OAD_Pos_Cmd | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_FrshDmpr.PositionCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_OAD_Pos_Fbk | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_FrshDmpr.PositionFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_OAD_Pos-Status | brick:Damper_Position_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005.FrshAirDmprSts |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Occ_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SP.OccTempSP |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Occupancy_Mode | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005.OccMode |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_Pressure_High_Filter_Dirty_Status | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupPreFlt.PressureHigh |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RA_Flow | brick:Return_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RA_P-Static | para:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0001_RtnAirDuctPrs.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RA_RH | brick:Return_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RA_Temperature | brick:Return_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 |  |  | rdfs:label_en | Damper Position 100 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 |  |  | rdfs:label_en | Damper Position 70 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 |  |  | rdfs:label_en | Damper Position 77.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 |  |  | rdfs:label_en | Damper Position 85 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RAD | brick:Return_Damper | brick:hasPoint | entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 |  |  | rdfs:label_en | Damper Position 92.5 |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_100 | para:Damper_Position_100 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0005_MinFALoocupTb.RecDmprPos100 |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_70 | para:Damper_Position_70 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0005_MinFALoocupTb.RecDmprPos70 |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_77.5 | para:Damper_Position_77.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0005_MinFALoocupTb.RecDmprPos77.5 |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_85 | para:Damper_Position_85 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0005_MinFALoocupTb.RecDmprPos85 |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RAD_ReCr_Damper_Pos_92.5 | para:Damper_Position_92.5 | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB_0005_MinFALoocupTb.RecDmprPos92.5 |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF | brick:Return_Fan | brick:hasPart | entity:SSC_AHUB0005_RF_Motor | brick:Motor |  |  | rdfs:label_en | Return Fan Motor
entity:SSC_AHUB0005_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0005_RF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Return Fan AutoMan_Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_RF | brick:Return_Fan | brick:hasPoint | entity:SSC_AHUB0005_RF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Return Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_RF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0005_RF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0005_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0005_RF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Return Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_RF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0005_RF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Return Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0005_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0005_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Return Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0005_RF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0005_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Return Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0005_RF_Motor_Electrical-Meter_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.kWh |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.kW |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_RF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_RtnFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SA_Flow | brick:Supply_Air_Flow_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupAirFlow.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SA_P-Static | brick:Static_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupAirDuctPrsRmt1.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SA_RH | brick:Supply_Air_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupAirHum.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SAT | brick:Supply_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupAirTemp.PV |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_AHUB0005_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0005_SF_TripAlm | brick:Alarm |  |  | rdfs:label_en | Supplu Fan Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0005_SF_AutoMan_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Supply Fan Auto Man Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0005_SF_FailtoStop | para:Fail_Stop_Alarm |  |  | rdfs:label_en | Supply Fan Fail to Stop |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0005_SF_FailtoStart | para:Fail_Start_Alarm |  |  | rdfs:label_en | Supply Fan FailtoStart |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_SF | brick:Supply_Fan | brick:hasPoint | entity:SSC_AHUB0005_SF_Status | brick:On_Off_Status |  |  | rdfs:label_en | Supply Fan Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_AHUB0005_SF_AutoMan_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.AutoManSts |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_FailtoStart | para:Fail_Start_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.FTST |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_FailtoStop | para:Fail_Stop_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.FTSP |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_Motor | brick:Motor | brick:hasPart | entity:SSC_AHUB0005_SF_Motor_Electrical-Meter | brick:Electrical_Meter |  |  | rdfs:label_en | Electrcial Power Meter
entity:SSC_AHUB0005_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0005_SF_Motor_Speed_Cmd | brick:Speed_Command |  |  | rdfs:label_en | Supply Fan Speed Command |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_AHUB0005_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_AHUB0005_SF_Motor_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Supply Fan Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_AHUB0005_SF_Motor | brick:Motor | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value | 50 |  |  | brick:hasUnit | unit:HZ
entity:SSC_AHUB0005_SF_Motor | brick:Motor | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value | 5 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0005_SF_Motor | brick:Motor | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value | 415 |  |  | brick:hasUnit | unit:V
entity:SSC_AHUB0005_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.kWh |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0005_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Supply Fan Electrical Demand |  |  | brick:hasUnit | unit:KiloW
entity:SSC_AHUB0005_SF_Motor_Electrical-Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_AHUB0005_SF_Motor_Electrical_Energy_Consumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Supply Fan Energy Consumption |  |  | brick:hasUnit | unit:MegaW-HR
entity:SSC_AHUB0005_SF_Motor_Electrical-Meter_Power-Demand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.kW |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_Motor_Speed_Cmd | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.SpeedCmd |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_Motor_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.SpeedFbk |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005.SupFanSts |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_SF_TripAlm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SupFan.TripAlm |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_AHUB0005_UnOcc_Temp_Setpoint | brick:Unoccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_AHUB0005_SP.UnOccTempSP |  |  | para:hasEntityId | SSC_AHUB0005
entity:SSC_B1_001_FM_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.001_FM STORAGE
entity:SSC_B1_002_HV_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.002_HV
entity:SSC_B1_003_TRANSFORMER | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.003_TRANSFORMER
entity:SSC_B1_004_MV_SWITCH_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.004_MV SWITCH ROOM
entity:SSC_B1_005_UPS | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.005_UPS
entity:SSC_B1_006_SERVICE_AREA | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.006_SERVICE AREA
entity:SSC_B1_007_SERVICE_DOCK | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.007_SERVICE DOCK
entity:SSC_B1_008_VENT_PLANT | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.008_VENT PLANT
entity:SSC_B1_009_TOILET | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.009_TOILET
entity:SSC_B1_010_VESTIBULE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.010_VESTIBULE
entity:SSC_B1_011_JANITORS_CLOSET | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.011_JANITORS CLOSET
entity:SSC_B1_012_GENERATOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.012_GENERATOR
entity:SSC_B1_013_CHILLED_WATER | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.013_CHILLED WATER
entity:SSC_B1_014_VENT_PLANT | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.014_VENT PLANT
entity:SSC_B1_015_ENTRANCE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.015_ENTRANCE
entity:SSC_B1_016_SPRINKLER_&_WATER | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.016_SPRINKLER & WATER
entity:SSC_B1_017_MDF-2 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.017_MDF-2
entity:SSC_B1_018_CONDENSER_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.018_CONDENSER ROOM
entity:SSC_B1_019_FM_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.019_FM STORAGE
entity:SSC_B1_020_FM_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.020_FM STORAGE
entity:SSC_B1_021_FM_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.021_FM STORAGE
entity:SSC_B1_022_SSP | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.022_SSP
entity:SSC_B1_023_Q_TEL | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.023_QTEL
entity:SSC_B1_024_BIN_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.024_BIN STORAGE
entity:SSC_B1_025_MAIN_SEC_CONTROL_ROOM | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.025_MAIN SEC. CONTROL ROOM
entity:SSC_B1_026_MDF_SER-1 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.026_MDF/SER-1
entity:SSC_B1_027_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.027_CORRIDOR
entity:SSC_B1_028_FILE_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.028_FILE STORAGE
entity:SSC_B1_029_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.029_CORRIDOR
entity:SSC_B1_030_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.030_CORRIDOR
entity:SSC_B1_031_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.031_CORRIDOR
entity:SSC_B1_032_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.032_CORRIDOR
entity:SSC_B1_034_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.034_CORRIDOR
entity:SSC_B1_035_CORRIDOR | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.035_CORRIDOR
entity:SSC_B1_036_STORAGE | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.036_STORAGE
entity:SSC_B1_038_SER-2 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.038_SER-2
entity:SSC_B1_039_BMS | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.039_BMS
entity:SSC_B1_P-1_P1 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.P-1_LIFT
entity:SSC_B1_P-2_P2 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.P-2_LIFT
entity:SSC_B1_ST-1_STAIR-1 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.ST-1_STAIR-1
entity:SSC_B1_ST-2_STAIR-2 | rec:Room | rec:isPartOf | entity:SSC_Level-B1 | rec:BasementLevel | rdfs:label_en | B1.ST-2_STAIR-2
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0301_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0301 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System |  |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCU3F0301 | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCU3F0301 | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCU3F0301 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCU3F0301 |  |  | ref:ifcName | SSC_CCU3F0301
entity:SSC_CCU3F0301_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.CloggedFilter |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.CommAlm |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.CoolSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.DehumSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.ElectHtrSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.FanSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.Alm |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.HumSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.RtnHumidity |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.AirFlwLoss |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.MainFanOvrld |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.State |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.RunSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.SumAlmSts |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.RtnTemp |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0301_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0301.ActualTempSP |  |  | para:hasEntityId | SSC_CCU3F0301
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:hasPoint | entity:SSC_CCU3F0302_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCU3F0302 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCU3F0302 | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCU3F0302 | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCU3F0302 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCU3F0302 |  |  | ref:ifcName | SSC_CCU3F0302
entity:SSC_CCU3F0302_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.CloggedFilter |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.CommAlm |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.CoolSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.DehumSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.ElectHtrSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.FanSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.Alm |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.HumSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.RtnHumidity |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.AirFlwLoss |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.MainFanOvrld |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.State |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.RunSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.SumAlmSts |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.RtnTemp |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCU3F0302_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCU3F0302.ActualTempSP |  |  | para:hasEntityId | SSC_CCU3F0302
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001A_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001A | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0001A | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0001A | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0001A | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0001A |  |  | ref:ifcName | SSC_CCUB0001A
entity:SSC_CCUB0001A_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.CommAlm |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.CoolSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.DehumSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.FanSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.Alm |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.HumSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.State |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.RunSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001A_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001A.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0001A
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0001B_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0001B | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0001B | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0001B | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0001B | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0001B |  |  | ref:ifcName | SSC_CCUB0001B
entity:SSC_CCUB0001B_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.CommAlm |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.CoolSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.DehumSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.FanSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.Alm |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.HumSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.State |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.RunSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0001B_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0001B.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0001B
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002A_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002A | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0002A | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0002A | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0002A | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0002A |  |  | ref:ifcName | SSC_CCUB0002A
entity:SSC_CCUB0002A_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.CommAlm |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.CoolSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.DehumSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.FanSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.Alm |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.HumSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.State |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.RunSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002A_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002A.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0002A
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0002B_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0002B | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0002B | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0002B | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0002B | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0002B |  |  | ref:ifcName | SSC_CCUB0002B
entity:SSC_CCUB0002B_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.CommAlm |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.CoolSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.DehumSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.FanSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.Alm |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.HumSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.State |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.RunSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0002B_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0002B.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0002B
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0003_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0003 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0003 | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0003 | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0003 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0003 |  |  | ref:ifcName | SSC_CCUB0003
entity:SSC_CCUB0003_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.CommAlm |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.CoolSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.DehumSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.FanSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.Alm |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.HumSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.State |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.RunSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0003_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0003.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0003
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0004_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0004 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0004 | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0004 | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0004 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0004 |  |  | ref:ifcName | SSC_CCUB0004
entity:SSC_CCUB0004_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.CommAlm |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.CoolSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.DehumSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.FanSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.Alm |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.HumSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.State |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.RunSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0004_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0004.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0004
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005A_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005A | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0005A | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0005A | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0005A | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0005A |  |  | ref:ifcName | SSC_CCUB0005A
entity:SSC_CCUB0005A_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.CommAlm |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.CoolSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.DehumSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.FanSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.Alm |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.HumSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.State |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.RunSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005A_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005A.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0005A
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0005B_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0005B | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0005B | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0005B | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0005B | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0005B |  |  | ref:ifcName | SSC_CCUB0005B
entity:SSC_CCUB0005B_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.CommAlm |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.CoolSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.DehumSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.FanSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.Alm |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.HumSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.State |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.RunSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0005B_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0005B.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0005B
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006A_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006A | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0006A | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0006A | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0006A | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0006A |  |  | ref:ifcName | SSC_CCUB0006A
entity:SSC_CCUB0006A_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.CommAlm |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.CoolSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.DehumSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.FanSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.Alm |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.HumSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.State |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.RunSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006A_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006A.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0006A
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0006B_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0006B | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0006B | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0006B | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0006B | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0006B |  |  | ref:ifcName | SSC_CCUB0006B
entity:SSC_CCUB0006B_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.CommAlm |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.CoolSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.DehumSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.FanSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.Alm |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.HumSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.State |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.RunSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0006B_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0006B.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0006B
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0007_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0007 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0007 | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0007 | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0007 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0007 |  |  | ref:ifcName | SSC_CCUB0007
entity:SSC_CCUB0007_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.CommAlm |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.CoolSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.DehumSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.FanSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.Alm |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.HumSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.State |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.RunSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0007_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0007.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0007
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Humidity | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Return Air Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Return Air Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Humidity_Setpoint | brick:Humidity_Setpoint |  |  | rdfs:label_en | Actual Humidity Setpoint |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Actual Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Communication_Alarm | brick:Communication_Loss_Alarm |  |  | rdfs:label_en | Communication Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm |  |  | rdfs:label_en | AirFlwLoss |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_General_Fault | brick:Alarm |  |  | rdfs:label_en | Alm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Clogged_Filter | brick:Filter_Status |  |  | rdfs:label_en | CloggedFilter |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Cool_On_Status | brick:Cooling_Mode_Status |  |  | rdfs:label_en | CoolSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Dehumidifcation_On_Status | para:Dehumidification_On_Status |  |  | rdfs:label_en | DehumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Electric_Heater_On_Status | para:Heater_On_Status |  |  | rdfs:label_en | ElectHtrSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Fan_On_Status | brick:On_Off_Status |  |  | rdfs:label_en | FanSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Humidification_On_Status | para:Humidification_On_Status |  |  | rdfs:label_en | HumSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Main_Fan_Overload | brick:Overload_Alarm |  |  | rdfs:label_en | MainFanOvrld |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Running_Status | brick:Run_Status |  |  | rdfs:label_en | RunSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Operating_State | brick:Operating_Mode_Status |  |  | rdfs:label_en | State |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:hasPoint | entity:SSC_CCUB0008_Summary_Alarm_Status | para:Summary_Alarm |  |  | rdfs:label_en | SumAlmSts |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CCUB0008 | brick:CRAC | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en |  |  |  | rdfs:comment | Serves Level 1 & Level 3 VAVs; coil/fan/points pending AHU schedule + IO list.
entity:SSC_CCUB0008 | brick:CRAC | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CCUB0008 | brick:CRAC | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CCUB0008 | brick:CRAC | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CCUB0008 |  |  | ref:ifcName | SSC_CCUB0008
entity:SSC_CCUB0008_Clogged_Filter | brick:Filter_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.CloggedFilter |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Communication_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.CommAlm |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Cool_On_Status | brick:Cooling_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.CoolSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Dehumidifcation_On_Status | para:Dehumidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.DehumSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Electric_Heater_On_Status | para:Heater_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.ElectHtrSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Fan_On_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.FanSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_General_Fault | brick:Fault_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.Alm |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Humidification_On_Status | para:Humidification_On_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.HumSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Humidity | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.RtnHumidity |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Humidity_Setpoint | brick:Humidity_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.ActualHumiditySP |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Loss_of_Airflow | brick:Air_Flow_Loss_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.AirFlwLoss |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Main_Fan_Overload | brick:Overload_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.MainFanOvrld |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Operating_State | brick:Operating_Mode_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.State |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.RunSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Summary_Alarm_Status | para:Summary_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.SumAlmSts |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.RtnTemp |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CCUB0008_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CCUB0008.ActualTempSP |  |  | para:hasEntityId | SSC_CCUB0008
entity:SSC_CHW_CHWP01 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP01_Motor | brick:Motor |  |  | rdfs:label_en | SSC_CHW_CHWP01 Motor
entity:SSC_CHW_CHWP01 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP01_Electrical_Meter | brick:Electrical_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP01 Electrical Meter
entity:SSC_CHW_CHWP01 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP01_Thermal_Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP01 Thermal Meter
entity:SSC_CHW_CHWP01 | brick:Water_Pump | brick:hasPoint | entity:SSC_CHW_CHWP01_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration |  |  | rdfs:label_en | ScheduledPM Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP01 | brick:Water_Pump | brick:hasPoint | entity:SSC_CHW_CHWP01_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration |  |  | rdfs:label_en | UnScheduled Outage Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP01 | brick:Water_Pump | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CHW Pump
entity:SSC_CHW_CHWP01 | brick:Water_Pump | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CHW_CHWP01 | brick:Water_Pump | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CHW_CHWP01 | brick:Water_Pump | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_CHWP01 |  |  | ref:ifcName | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_Electrical_Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_CHW_CHWP01_Power_Sensor | brick:Power_Sensor |  |  | rdfs:label_en | Power |  |  | brick:hasUnit | unit:KiloW
entity:SSC_CHW_CHWP01_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP01_Speed_Command | brick:Speed_Command |  |  | rdfs:label_en | Speed Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_CHWP01_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP01_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_CHW_CHWP01_Power_Sensor | brick:Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.kW |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_Speed_Command | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.SpeedCmd |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.SpeedFbk |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_Thermal_Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_CHW_CHWP01_Thermal_Power_Sensor | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Thermal Load Fan |  |  | brick:hasUnit | para:KiloWt
entity:SSC_CHW_CHWP01_Thermal_Power_Sensor | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.ThermLoadFan |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP01_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP01.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP01
entity:SSC_CHW_CHWP02 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP02_Motor | brick:Motor |  |  | rdfs:label_en | SSC_CHW_CHWP02 Motor
entity:SSC_CHW_CHWP02 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP02_Electrical_Meter | brick:Electrical_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP02 Electrical Meter
entity:SSC_CHW_CHWP02 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP02_Thermal_Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP02 Thermal Meter
entity:SSC_CHW_CHWP02 | brick:Water_Pump | brick:hasPoint | entity:SSC_CHW_CHWP02_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration |  |  | rdfs:label_en | ScheduledPM Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP02 | brick:Water_Pump | brick:hasPoint | entity:SSC_CHW_CHWP02_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration |  |  | rdfs:label_en | UnScheduled Outage Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP02 | brick:Water_Pump | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CHW Pump
entity:SSC_CHW_CHWP02 | brick:Water_Pump | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CHW_CHWP02 | brick:Water_Pump | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CHW_CHWP02 | brick:Water_Pump | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_CHWP02 |  |  | ref:ifcName | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_Electrical_Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_CHW_CHWP02_Power_Sensor | brick:Power_Sensor |  |  | rdfs:label_en | Power |  |  | brick:hasUnit | unit:KiloW
entity:SSC_CHW_CHWP02_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP02_Speed_Command | brick:Speed_Command |  |  | rdfs:label_en | Speed Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_CHWP02_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP02_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_CHW_CHWP02_Power_Sensor | brick:Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.kW |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_Speed_Command | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.SpeedCmd |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.SpeedFbk |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_Thermal_Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_CHW_CHWP02_Thermal_Power_Sensor | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Thermal Load Fan |  |  | brick:hasUnit | para:KiloWt
entity:SSC_CHW_CHWP02_Thermal_Power_Sensor | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.ThermLoadFan |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP02_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP02.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP02
entity:SSC_CHW_CHWP03 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP03_Motor | brick:Motor |  |  | rdfs:label_en | SSC_CHW_CHWP03 Motor
entity:SSC_CHW_CHWP03 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP03_Electrical_Meter | brick:Electrical_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP03 Electrical Meter
entity:SSC_CHW_CHWP03 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP03_Thermal_Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP03 Thermal Meter
entity:SSC_CHW_CHWP03 | brick:Water_Pump | brick:hasPoint | entity:SSC_CHW_CHWP03_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration |  |  | rdfs:label_en | ScheduledPM Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP03 | brick:Water_Pump | brick:hasPoint | entity:SSC_CHW_CHWP03_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration |  |  | rdfs:label_en | UnScheduled Outage Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP03 | brick:Water_Pump | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CHW Pump
entity:SSC_CHW_CHWP03 | brick:Water_Pump | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CHW_CHWP03 | brick:Water_Pump | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CHW_CHWP03 | brick:Water_Pump | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_CHWP03 |  |  | ref:ifcName | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_Electrical_Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_CHW_CHWP03_Power_Sensor | brick:Power_Sensor |  |  | rdfs:label_en | Power |  |  | brick:hasUnit | unit:KiloW
entity:SSC_CHW_CHWP03_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP03_Speed_Command | brick:Speed_Command |  |  | rdfs:label_en | Speed Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_CHWP03_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP03_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_CHW_CHWP03_Power_Sensor | brick:Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.kW |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_Speed_Command | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.SpeedCmd |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.SpeedFbk |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_Thermal_Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_CHW_CHWP03_Thermal_Power_Sensor | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Thermal Load Fan |  |  | brick:hasUnit | para:KiloWt
entity:SSC_CHW_CHWP03_Thermal_Power_Sensor | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.ThermLoadFan |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP03_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP03.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP03
entity:SSC_CHW_CHWP04 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP04_Motor | brick:Motor |  |  | rdfs:label_en | SSC_CHW_CHWP04 Motor
entity:SSC_CHW_CHWP04 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP04_Electrical_Meter | brick:Electrical_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP04 Electrical Meter
entity:SSC_CHW_CHWP04 | brick:Water_Pump | brick:hasPart | entity:SSC_CHW_CHWP04_Thermal_Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | SSC_CHW_CHWP04 Thermal Meter
entity:SSC_CHW_CHWP04 | brick:Water_Pump | brick:hasPoint | entity:SSC_CHW_CHWP04_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration |  |  | rdfs:label_en | ScheduledPM Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP04 | brick:Water_Pump | brick:hasPoint | entity:SSC_CHW_CHWP04_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration |  |  | rdfs:label_en | UnScheduled Outage Hours (Manual Entry) |  |  | brick:hasUnit | unit:HR
entity:SSC_CHW_CHWP04 | brick:Water_Pump | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | CHW Pump
entity:SSC_CHW_CHWP04 | brick:Water_Pump | rec:isFedBy | entity:<Fedby> | para:Chilled_Water_Loop_Network
entity:SSC_CHW_CHWP04 | brick:Water_Pump | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_CHW_CHWP04 | brick:Water_Pump | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_CHWP04 |  |  | ref:ifcName | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_Electrical_Meter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_CHW_CHWP04_Power_Sensor | brick:Power_Sensor |  |  | rdfs:label_en | Power |  |  | brick:hasUnit | unit:KiloW
entity:SSC_CHW_CHWP04_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP04_Speed_Command | brick:Speed_Command |  |  | rdfs:label_en | Speed Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_CHWP04_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_CHWP04_Speed_Fbk | brick:Speed_Sensor |  |  | rdfs:label_en | Speed Feedback |  |  | brick:hasUnit | unit:RPM
entity:SSC_CHW_CHWP04_Power_Sensor | brick:Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.kW |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_Scheduled_PM_Hours | para:Scheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_Speed_Command | brick:Speed_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.SpeedCmd |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_Speed_Fbk | brick:Speed_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.SpeedFbk |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_Thermal_Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_CHW_CHWP04_Thermal_Power_Sensor | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Thermal Load Fan |  |  | brick:hasUnit | para:KiloWt
entity:SSC_CHW_CHWP04_Thermal_Power_Sensor | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.ThermLoadFan |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_CHWP04_UNScheduled_Outage_Hours | para:UnScheduled_Hrs_Duration | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_CHWP04.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_CHW_CHWP04
entity:SSC_CHW_HE01 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE01_Return_Valve | brick:Valve |  |  | rdfs:label_en | Return Valve
entity:SSC_CHW_HE01 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve |  |  | rdfs:label_en | Supply Isolation Valve
entity:SSC_CHW_HE01 | brick:Heat_Exchanger | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | SSC_CHW_HE01
entity:SSC_CHW_HE01 | brick:Heat_Exchanger | rec:isFedBy |  | para:Chilled_Water_Loop_Network
entity:SSC_CHW_HE01 | brick:Heat_Exchanger | rec:locatedIn |  | rec:Room
entity:SSC_CHW_HE01 | brick:Heat_Exchanger | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_HE01 |  |  | ref:ifcName | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPart | entity:SSC_CHW_HE01_Return_Valve_Motor | brick:Motor |  |  | rdfs:label_en | Motor
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Open_Close_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Open Close Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor |  |  | rdfs:label_en | Differential Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Position_Command | brick:Valve_Position_Command |  |  | rdfs:label_en | RTN Valve Position Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | RTN Valve Position |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | RTN Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_DiffPrs.PV |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE01_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Open_Close_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.OpenCloseSts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.PosFbk |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Position_Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.PosCmd |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Return_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_RtnMtrVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Manual Auto Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Close_Command | para:Open_command |  |  | rdfs:label_en | Close Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Open_Command | para:Close_command |  |  | rdfs:label_en | Open Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Supply Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE01_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE01_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature Sensor |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CHW_HE01_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupIsoVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve_Close_Command | para:Open_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupIsoVlv.CloseCmd |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupIsoVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve_Open_Command | para:Close_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupIsoVlv.OpenCmd |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupIsoVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE01_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE01_SupTemp.PV |  |  | para:hasEntityId | SSC_CHW_HE01
entity:SSC_CHW_HE02 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE02_Return_Valve | brick:Valve |  |  | rdfs:label_en | Return Valve
entity:SSC_CHW_HE02 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve |  |  | rdfs:label_en | Supply Isolation Valve
entity:SSC_CHW_HE02 | brick:Heat_Exchanger | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | SSC_CHW_HE02
entity:SSC_CHW_HE02 | brick:Heat_Exchanger | rec:isFedBy |  | para:Chilled_Water_Loop_Network
entity:SSC_CHW_HE02 | brick:Heat_Exchanger | rec:locatedIn |  | rec:Room
entity:SSC_CHW_HE02 | brick:Heat_Exchanger | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_HE02 |  |  | ref:ifcName | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPart | entity:SSC_CHW_HE02_Return_Valve_Motor | brick:Motor |  |  | rdfs:label_en | Motor
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Open_Close_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Open Close Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor |  |  | rdfs:label_en | Differential Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Position_Command | brick:Valve_Position_Command |  |  | rdfs:label_en | RTN Valve Position Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | RTN Valve Position |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | RTN Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_DiffPrs.PV |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE02_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Open_Close_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.OpenCloseSts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.PosFbk |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Position_Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.PosCmd |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Return_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_RtnMtrVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Manual Auto Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Close_Command | para:Open_command |  |  | rdfs:label_en | Close Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Open_Command | para:Close_command |  |  | rdfs:label_en | Open Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Supply Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE02_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE02_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature Sensor |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CHW_HE02_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupIsoVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve_Close_Command | para:Open_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupIsoVlv.CloseCmd |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupIsoVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve_Open_Command | para:Close_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupIsoVlv.OpenCmd |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupIsoVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE02_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE02_SupTemp.PV |  |  | para:hasEntityId | SSC_CHW_HE02
entity:SSC_CHW_HE03 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE03_Return_Valve | brick:Valve |  |  | rdfs:label_en | Return Valve
entity:SSC_CHW_HE03 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve |  |  | rdfs:label_en | Supply Isolation Valve
entity:SSC_CHW_HE03 | brick:Heat_Exchanger | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | SSC_CHW_HE03
entity:SSC_CHW_HE03 | brick:Heat_Exchanger | rec:isFedBy |  | para:Chilled_Water_Loop_Network
entity:SSC_CHW_HE03 | brick:Heat_Exchanger | rec:locatedIn |  | rec:Room
entity:SSC_CHW_HE03 | brick:Heat_Exchanger | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_HE03 |  |  | ref:ifcName | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPart | entity:SSC_CHW_HE03_Return_Valve_Motor | brick:Motor |  |  | rdfs:label_en | Motor
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Open_Close_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Open Close Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor |  |  | rdfs:label_en | Differential Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Position_Command | brick:Valve_Position_Command |  |  | rdfs:label_en | RTN Valve Position Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | RTN Valve Position |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | RTN Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_DiffPrs.PV |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE03_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Open_Close_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.OpenCloseSts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.PosFbk |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Position_Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.PosCmd |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Return_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_RtnMtrVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Manual Auto Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Close_Command | para:Open_command |  |  | rdfs:label_en | Close Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Open_Command | para:Close_command |  |  | rdfs:label_en | Open Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Supply Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE03_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE03_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature Sensor |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CHW_HE03_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupIsoVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve_Close_Command | para:Open_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupIsoVlv.CloseCmd |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupIsoVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve_Open_Command | para:Close_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupIsoVlv.OpenCmd |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupIsoVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE03_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE03_SupTemp.PV |  |  | para:hasEntityId | SSC_CHW_HE03
entity:SSC_CHW_HE04 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE04_Return_Valve | brick:Valve |  |  | rdfs:label_en | Return Valve
entity:SSC_CHW_HE04 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve |  |  | rdfs:label_en | Supply Isolation Valve
entity:SSC_CHW_HE04 | brick:Heat_Exchanger | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | SSC_CHW_HE04
entity:SSC_CHW_HE04 | brick:Heat_Exchanger | rec:isFedBy |  | para:Chilled_Water_Loop_Network
entity:SSC_CHW_HE04 | brick:Heat_Exchanger | rec:locatedIn |  | rec:Room
entity:SSC_CHW_HE04 | brick:Heat_Exchanger | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_HE04 |  |  | ref:ifcName | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPart | entity:SSC_CHW_HE04_Return_Valve_Motor | brick:Motor |  |  | rdfs:label_en | Motor
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Open_Close_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Open Close Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor |  |  | rdfs:label_en | Differential Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Position_Command | brick:Valve_Position_Command |  |  | rdfs:label_en | RTN Valve Position Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | RTN Valve Position |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | RTN Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_DiffPrs.PV |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE04_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Open_Close_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.OpenCloseSts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.PosFbk |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Position_Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.PosCmd |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Return_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_RtnMtrVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Manual Auto Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Close_Command | para:Open_command |  |  | rdfs:label_en | Close Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Open_Command | para:Close_command |  |  | rdfs:label_en | Open Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Supply Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE04_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE04_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature Sensor |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CHW_HE04_Supply_Valve_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupIsoVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve_Close_Command | para:Open_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupIsoVlv.CloseCmd |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve_Manual_Auto_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupIsoVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve_Open_Command | para:Close_command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupIsoVlv.OpenCmd |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupIsoVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE04_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE04_SupTemp.PV |  |  | para:hasEntityId | SSC_CHW_HE04
entity:SSC_CHW_HE05 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE05_Return_Valve | brick:Valve |  |  | rdfs:label_en | Return Valve
entity:SSC_CHW_HE05 | brick:Heat_Exchanger | brick:hasPart | entity:SSC_CHW_HE05_Supply_Valve | brick:Isolation_Valve |  |  | rdfs:label_en | Supply Isolation Valve
entity:SSC_CHW_HE05 | brick:Heat_Exchanger | brick:isPartOf | entity:CHW-System | brick:Chilled_Water_System | rdfs:label_en | SSC_CHW_HE05
entity:SSC_CHW_HE05 | brick:Heat_Exchanger | rec:isFedBy |  | para:Chilled_Water_Loop_Network
entity:SSC_CHW_HE05 | brick:Heat_Exchanger | rec:locatedIn |  | rec:Room
entity:SSC_CHW_HE05 | brick:Heat_Exchanger | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_CHW_HE05 |  |  | ref:ifcName | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPart | entity:SSC_CHW_HE05_Return_Valve_Motor | brick:Motor |  |  | rdfs:label_en | Motor
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Open_Close_Status | brick:Open_Close_Status |  |  | rdfs:label_en | Open Close Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor |  |  | rdfs:label_en | Differential Pressure |  |  | brick:hasUnit | unit:PA
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Position_Command | brick:Valve_Position_Command |  |  | rdfs:label_en | RTN Valve Position Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | RTN Valve Position |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve | brick:Valve | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Status | brick:Open_Close_Status |  |  | rdfs:label_en | RTN Valve Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve_Diff_Prs | brick:Differential_Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_DiffPrs.PV |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve_Motor | brick:Motor | brick:hasPoint | entity:SSC_CHW_HE05_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_CHW_HE05_Return_Valve_Motor_Auto_Manual_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.AutoManCmdSts |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.AutoManSts |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Open_Close_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.OpenCloseSts |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.PosFbk |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Position_Command | brick:Valve_Position_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.PosCmd |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Return_Valve_Status | brick:Open_Close_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_RtnMtrVlv.Sts |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_CHW_HE05_Supply_Valve | brick:Isolation_Valve | brick:hasPoint | entity:SSC_CHW_HE05_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature Sensor |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_CHW_HE05_Supply_Valve_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_CHW_HE05_SupTemp.PV |  |  | para:hasEntityId | SSC_CHW_HE05
entity:SSC_DXB0001 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0001_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0001 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0001_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0001 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0001_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0001 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_DXB0001 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0001 | para:DXUnit | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_DXB0001 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0001 |  |  | ref:ifcName | SSC_DXB0001
entity:SSC_DXB0001_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0001.Alm |  |  | para:hasEntityId | SSC_DXB0001
entity:SSC_DXB0001_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0001.RunSts |  |  | para:hasEntityId | SSC_DXB0001
entity:SSC_DXB0001_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0001.SpcTemp |  |  | para:hasEntityId | SSC_DXB0001
entity:SSC_DXB0002 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0002_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0002 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0002_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0002 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0002_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0002 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_DXB0002 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0002 | para:DXUnit | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_DXB0002 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0002 |  |  | ref:ifcName | SSC_DXB0002
entity:SSC_DXB0002_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0002.Alm |  |  | para:hasEntityId | SSC_DXB0002
entity:SSC_DXB0002_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0002.RunSts |  |  | para:hasEntityId | SSC_DXB0002
entity:SSC_DXB0002_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0002.SpcTemp |  |  | para:hasEntityId | SSC_DXB0002
entity:SSC_DXB0003 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0003_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0003 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0003_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0003 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0003_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0003 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_DXB0003 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0003 | para:DXUnit | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_DXB0003 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0003 |  |  | ref:ifcName | SSC_DXB0003
entity:SSC_DXB0003_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0003.Alm |  |  | para:hasEntityId | SSC_DXB0003
entity:SSC_DXB0003_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0003.RunSts |  |  | para:hasEntityId | SSC_DXB0003
entity:SSC_DXB0003_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0003.SpcTemp |  |  | para:hasEntityId | SSC_DXB0003
entity:SSC_DXB0004 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0004_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0004 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0004_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0004 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0004_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0004 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_DXB0004 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0004 | para:DXUnit | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_DXB0004 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0004 |  |  | ref:ifcName | SSC_DXB0004
entity:SSC_DXB0004_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0004.Alm |  |  | para:hasEntityId | SSC_DXB0004
entity:SSC_DXB0004_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0004.RunSts |  |  | para:hasEntityId | SSC_DXB0004
entity:SSC_DXB0004_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0004.SpcTemp |  |  | para:hasEntityId | SSC_DXB0004
entity:SSC_DXB0005 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0005_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0005 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0005_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0005 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0005_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0005 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_DXB0005 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0005 | para:DXUnit | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_DXB0005 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0005 |  |  | ref:ifcName | SSC_DXB0005
entity:SSC_DXB0005_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0005.Alm |  |  | para:hasEntityId | SSC_DXB0005
entity:SSC_DXB0005_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0005.RunSts |  |  | para:hasEntityId | SSC_DXB0005
entity:SSC_DXB0005_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0005.SpcTemp |  |  | para:hasEntityId | SSC_DXB0005
entity:SSC_DXB0006 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0006_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0006 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0006_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0006 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0006_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0006 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_DXB0006 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0006 | para:DXUnit | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_DXB0006 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0006 |  |  | ref:ifcName | SSC_DXB0006
entity:SSC_DXB0006_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0006.Alm |  |  | para:hasEntityId | SSC_DXB0006
entity:SSC_DXB0006_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0006.RunSts |  |  | para:hasEntityId | SSC_DXB0006
entity:SSC_DXB0006_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0006.SpcTemp |  |  | para:hasEntityId | SSC_DXB0006
entity:SSC_DXB0007 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0007_Humidity_Sensor | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_DXB0007 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0007_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0007 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0007_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0007 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0007_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0007 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_DXB0007 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0007 | para:DXUnit | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_DXB0007 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0007 |  |  | ref:ifcName | SSC_DXB0007
entity:SSC_DXB0007_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0007.Alm |  |  | para:hasEntityId | SSC_DXB0007
entity:SSC_DXB0007_Humidity_Sensor | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0007.Humidity |  |  | para:hasEntityId | SSC_DXB0007
entity:SSC_DXB0007_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0007.RunSts |  |  | para:hasEntityId | SSC_DXB0007
entity:SSC_DXB0007_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0007.SpcTemp |  |  | para:hasEntityId | SSC_DXB0007
entity:SSC_DXB0008 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0008_Humidity_Sensor | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_DXB0008 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0008_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0008 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0008_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0008 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0008_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0008 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_DXB0008 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0008 | para:DXUnit | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_DXB0008 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0008 |  |  | ref:ifcName | SSC_DXB0008
entity:SSC_DXB0008_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0008.Alm |  |  | para:hasEntityId | SSC_DXB0008
entity:SSC_DXB0008_Humidity_Sensor | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0008.Humidity |  |  | para:hasEntityId | SSC_DXB0008
entity:SSC_DXB0008_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0008.RunSts |  |  | para:hasEntityId | SSC_DXB0008
entity:SSC_DXB0008_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0008.SpcTemp |  |  | para:hasEntityId | SSC_DXB0008
entity:SSC_DXB0009 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0009_Humidity_Sensor | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_DXB0009 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0009_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0009 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0009_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0009 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0009_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0009 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_DXB0009 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0009 | para:DXUnit | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_DXB0009 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0009 |  |  | ref:ifcName | SSC_DXB0009
entity:SSC_DXB0009_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0009.Alm |  |  | para:hasEntityId | SSC_DXB0009
entity:SSC_DXB0009_Humidity_Sensor | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0009.Humidity |  |  | para:hasEntityId | SSC_DXB0009
entity:SSC_DXB0009_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0009.RunSts |  |  | para:hasEntityId | SSC_DXB0009
entity:SSC_DXB0009_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0009.SpcTemp |  |  | para:hasEntityId | SSC_DXB0009
entity:SSC_DXB0010 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0010_Humidity_Sensor | brick:Relative_Humidity_Sensor |  |  | rdfs:label_en | Humidity |  |  | brick:hasUnit | unit:PERCENT_RH
entity:SSC_DXB0010 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0010_Temperature_Sensor | brick:Temperature_Sensor |  |  | rdfs:label_en | Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_DXB0010 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0010_Alarm | brick:Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0010 | para:DXUnit | brick:hasPoint | entity:SSC_DXB0010_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_DXB0010 | para:DXUnit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_DXB0010 |  |  | rdfs:comment | COMMENTS
entity:SSC_DXB0010 | para:DXUnit | rec:locatedIn | entity:<Location> | rec:Room
entity:SSC_DXB0010 | para:DXUnit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_DXB0010 |  |  | ref:ifcName | SSC_DXB0010
entity:SSC_DXB0010_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0010.Alm |  |  | para:hasEntityId | SSC_DXB0010
entity:SSC_DXB0010_Humidity_Sensor | brick:Relative_Humidity_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0010.Humidity |  |  | para:hasEntityId | SSC_DXB0010
entity:SSC_DXB0010_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0010.RunSts |  |  | para:hasEntityId | SSC_DXB0010
entity:SSC_DXB0010_Temperature_Sensor | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_DXB0010.SpcTemp |  |  | para:hasEntityId | SSC_DXB0010
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0001_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0001_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0001_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_FCU0001 | rec:modelNumber | CPR173R4
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | rec:feeds | entity:<FCU_Serving_Location> | rec:Room
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | rec:isFedBy | <SOURCE_ASSET>
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_B1_016_SPRINKLER_&_WATER | rec:Room
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0001 |  |  | ref:ifcName | SSC_FCU0001
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0001 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0001_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0001_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.861 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0001_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0001_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0001_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0001_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0001_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0001_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0001_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0001_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0001_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0001_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0001_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.OccSts |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.RmTemp |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0001_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0001_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0001_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0001_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0001_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0001_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.StopCmd |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.TempCtrl |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.StartCmd |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0001_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0001.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0001
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0002_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0002_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0002_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_FCU0002 | rec:modelNumber | CPR173R4
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | rec:feeds | entity:<FCU_Serving_Location> | rec:Room
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | rec:isFedBy | <SOURCE_ASSET>
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_B1_025_MAIN_SEC_CONTROL_ROOM | rec:Room
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0002 |  |  | ref:ifcName | SSC_FCU0002
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0002 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0002_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0002_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.861 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0002_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0002_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0002_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0002_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0002_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0002_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0002_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0002_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0002_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0002_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0002_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.OccSts |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.RmTemp |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0002_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0002_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0002_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0002_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0002_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0002_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.StopCmd |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.TempCtrl |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.StartCmd |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0002_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0002.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0002
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0003_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0003_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0003_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_FCU0003 | rec:modelNumber | CPR173R4
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | rec:feeds | entity:<FCU_Serving_Location> | rec:Room
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | rec:isFedBy | <SOURCE_ASSET>
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_B1_039_BMS | rec:Room
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0003 |  |  | ref:ifcName | SSC_FCU0003
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0003 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0003_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0003_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.861 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0003_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0003_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0003_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0003_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0003_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0003_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0003_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0003_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0003_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0003_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0003_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.OccSts |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.RmTemp |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0003_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0003_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0003_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0003_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0003_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0003_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.StopCmd |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.TempCtrl |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.StartCmd |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0003_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0003.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0003
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0004_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0004_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0004_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_FCU0004 | rec:modelNumber | CPR173R4
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | rec:feeds | entity:<FCU_Serving_Location> | rec:Room
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | rec:isFedBy | <SOURCE_ASSET>
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_008_AV_ROOM | rec:Room
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0004 |  |  | ref:ifcName | SSC_FCU0004
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0004 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0004_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0004_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.861 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0004_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0004_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0004_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0004_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0004_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0004_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0004_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0004_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0004_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0004_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0004_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.OccSts |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.RmTemp |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0004_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0004_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0004_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0004_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0004_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0004_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.StopCmd |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.TempCtrl |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.StartCmd |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0004_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0004.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0004
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0005_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0005_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0005_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_FCU0005 | rec:modelNumber | CPR173R4
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | rec:feeds | entity:<FCU_Serving_Location> | rec:Room
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | rec:isFedBy | <SOURCE_ASSET>
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_027_IDF_1 | rec:Room
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0005 |  |  | ref:ifcName | SSC_FCU0005
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0005 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0005_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0005_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.861 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0005_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0005_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0005_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0005_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0005_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0005_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0005_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0005_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0005_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0005_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0005_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.OccSts |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.RmTemp |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0005_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0005_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0005_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0005_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0005_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0005_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.StopCmd |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.TempCtrl |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.StartCmd |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0005_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0005.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0005
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0006_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0006_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0006_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0006_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_FCU0006 | rec:modelNumber | CPR173R4
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | rec:feeds | entity:<FCU_Serving_Location> | rec:Room
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | rec:isFedBy | <SOURCE_ASSET>
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_027_IDF_1 | rec:Room
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0006 |  |  | ref:ifcName | SSC_FCU0006
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0006 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0006_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0006_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.861 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0006_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0006_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0006_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0006_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0006_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0006_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0006_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0006_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0006_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0006_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0006_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.OccSts |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.RmTemp |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0006_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0006_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0006_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0006_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0006_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0006_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.StopCmd |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.TempCtrl |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.StartCmd |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0006_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0006.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0006
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0007_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0007_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0007_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0007_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_FCU0007 | rec:modelNumber | CPR173R4
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | rec:feeds | entity:<FCU_Serving_Location> | rec:Room
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | rec:isFedBy | <SOURCE_ASSET>
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_039_IDF_2 | rec:Room
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0007 |  |  | ref:ifcName | SSC_FCU0007
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0007 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0007_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0007_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.861 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0007_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0007_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0007_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0007_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0007_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0007_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0007_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0007_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0007_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0007_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0007_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.OccSts |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.RmTemp |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0007_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0007_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0007_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0007_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0007_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0007_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.StopCmd |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.TempCtrl |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.StartCmd |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0007_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0007.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0007
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0008_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0008_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0008_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0008_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_FCU0008 | rec:modelNumber | CPR173R4
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | rec:feeds | entity:<FCU_Serving_Location> | rec:Room
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | rec:isFedBy | <SOURCE_ASSET>
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_039_IDF_2 | rec:Room
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0008 |  |  | ref:ifcName | SSC_FCU0008
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0008 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0008_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0008_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.861 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0008_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0008_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0008_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0008_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0008_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0008_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0008_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0008_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0008_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0008_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0008_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.OccSts |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.RmTemp |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0008_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0008_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0008_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0008_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0008_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0008_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.StopCmd |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.TempCtrl |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.StartCmd |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0008_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0008.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0008
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0009_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0009_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0009_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0009_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_FCU0009 | rec:modelNumber | CPR173R4
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | rec:feeds | entity:<FCU_Serving_Location> | rec:Room
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | rec:isFedBy | <SOURCE_ASSET>
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_028_CORRIDOR | rec:Room
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0009 |  |  | ref:ifcName | SSC_FCU0009
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0009 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0009_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0009_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.861 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0009_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0009_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0009_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0009_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0009_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0009_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0009_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0009_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0009_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0009_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0009_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.OccSts |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.RmTemp |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0009_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0009_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0009_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0009_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0009_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0009_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.StopCmd |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.TempCtrl |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.StartCmd |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0009_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0009.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0009
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0010_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0010_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0010_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0010_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_FCU0010 | rec:modelNumber | CPR173R4
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | rec:feeds | entity:<FCU_Serving_Location> | rec:Room
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | rec:isFedBy | <SOURCE_ASSET>
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_01_010_CORRIDOR | rec:Room
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0010 |  |  | ref:ifcName | SSC_FCU0010
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0010 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0010_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0010_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.861 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0010_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0010_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0010_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0010_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0010_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0010_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0010_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0010_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0010_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0010_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0010_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.OccSts |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.RmTemp |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0010_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0010_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0010_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0010_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0010_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0010_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.StopCmd |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.TempCtrl |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.StartCmd |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0010_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0010.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0010
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0011_CHW-Coil | brick:Chilled_Water_Coil |  |  | rdfs:label_en | Chilled Water Coil
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0011_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter |  |  | rdfs:label_en | FCU Chilled Water Thermal Power Virtual Meter
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0011_ElectricalVirtualMeter | brick:Electrical_Meter |  |  | rdfs:label_en | FCU Electrical Virtual Meter
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPart | entity:SSC_FCU0011_SF | brick:Supply_Fan |  |  | rdfs:label_en | Supply Fan
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Schedule_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Scheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_UnScheduled_Hrs | brick:Duration_Sensor |  |  | rdfs:label_en | Unscheduled Hours Mannual |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint |  |  | rdfs:label_en | Occupied Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Room_Temperature | brick:Room_Air_Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours |  |  | rdfs:label_en | Cooling Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours |  |  | rdfs:label_en | Fan Mode Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:isPartOf | entity:HVAC | brick:System | rdfs:label_en | SSC_FCU0011 | rec:modelNumber | CPR173R4
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | rec:feeds | entity:<FCU_Serving_Location> | rec:Room
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | rec:isFedBy | <SOURCE_ASSET>
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | rec:locatedIn | entity:SSC_03_033_PRINTING | rec:Room
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_FCU0011 |  |  | ref:ifcName | SSC_FCU0011
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupied Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0011 | brick:Fan_Coil_Unit | brick:hasPoint | entity:SSC_FCU0011_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command |  |  | rdfs:label_en | Temp Ctrl - SCADA / Thermostat |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0011_CHW-Coil | brick:Chilled_Water_Coil | brick:coolingCapacity | <blanknode> | <blanknode> |  |  | brick:value | 5.861 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0011_CHW-Coil | brick:Chilled_Water_Coil | brick:hasPart | entity:SSC_FCU0011_CHW-Coil_Valve | brick:Cooling_Valve |  |  | rdfs:label_en | Chilled Water Cooling Valve
entity:SSC_FCU0011_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWTH_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Cooling-Load-Demand | brick:Thermal_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | CWPWR_KWT_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_CoolingMode_OperationDuration | para:Cooling_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONCOOL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0011_Cooling-Load-Consumption | brick:Thermal_Energy_Usage_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Consumption CALC |  |  | brick:hasUnit | para:KiloWt-HR
entity:SSC_FCU0011_Cooling-Thermal-Virtual-Meter | brick:Thermal_Power_Meter | brick:hasPoint | entity:SSC_FCU0011_Cooling-Load-Demand | brick:Thermal_Power_Sensor |  |  | rdfs:label_en | Cooling Thermal Power Demand CALC |  |  | brick:hasUnit | para:KiloWt
entity:SSC_FCU0011_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERCONSUMP_KWH_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_ElectricalDemand | brick:Electric_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ELECTRICITYPOWERDEMAND_KW_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0011_ElectricalConsumption | brick:Electrical_Energy_Usage_Sensor |  |  | rdfs:label_en | Electricity Power Consumption CALC |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_FCU0011_ElectricalVirtualMeter | brick:Electrical_Meter | brick:hasPoint | entity:SSC_FCU0011_ElectricalDemand | brick:Electric_Power_Sensor |  |  | rdfs:label_en | Electricity Power Demand CALC |  |  | brick:hasUnit | unit:KiloW
entity:SSC_FCU0011_FanMode_OperationDuration | para:Fan_Mode_Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONFAN_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.OccSts |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Occupied_Temp_Setpoint | brick:ccupied_Air_Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.OccCoolSP |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Room_Temperature | brick:Room_Air_Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.RmTemp |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Schedule_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.CalcEntryScheduledHrs |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_SF | brick:Supply_Fan | brick:hasPart | entity:SSC_FCU0011_SF_Motor | brick:Motor |  |  | rdfs:label_en | Supply Fan Motor
entity:SSC_FCU0011_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0011_Start_Command | para:Start_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0011_SF_Motor | brick:Motor | brick:hasPoint | entity:SSC_FCU0011_Stop_Command | para:Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_FCU0011_Start_Command | para:Start_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.StopCmd |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Stop_Command | para:Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.TempCtrl |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Temp_Cntrl_SCADA_or_Thermostat | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.StartCmd |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.EffectiveSP |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_FCU0011_UnScheduled_Hrs | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_FCU0011.CalcEntryUnscheduledHrs |  |  | para:hasEntityId | SSC_FCU0011
entity:SSC_GEFB0001 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_GEFB0001_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_GEFB0001 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_GEFB0001_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_GEFB0001 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_GEFB0001_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_GEFB0001 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC_GEFB0001 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_GEFB0001 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_GEFB0001 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_GEFB0001 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_GEFB0001 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_GEFB0001 |  |  | ref:ifcName | SSC_GEFB0001
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Auto_Command_Status | para:Command_Status |  |  | rdfs:label_en | Auto Manual Command Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Exhaust_Fan_in_Auto_Mode | brick:Mode_Command |  |  | rdfs:label_en | Exhaust Fan in Auto Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Exhaust_Fan_Healthy | brick:Status |  |  | rdfs:label_en | Exhaust Fan Healthy (For Internal Use Only) |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Running_Status | brick:On_Off_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor | brick:Motor | brick:hasPoint | entity:SSC_GEFB0001_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_GEFB0001_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.AutoCmd |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Auto_Command_Status | para:Command_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.AutoManCmdSts |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.AutoManSts |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Exhaust_Fan_Healthy | brick:Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.iEFSts |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Exhaust_Fan_in_Auto_Mode | brick:Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.EFAutoMode |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.ManCmd |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Running_Status | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.RunSts |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.StartCmd |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.StopCmd |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_GEFB0001.TripAlm |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_GEFB0001_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_GEFB0001
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_KEF0103_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_KEF0103_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0103_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0103_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0103_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0103_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC_KEF0103 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC_KEF0103 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_KEF0103 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_KEF0103 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_KEF0103 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_KEF0103 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_KEF0103 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_KEF0103 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_KEF0103 |  |  | ref:ifcName | SSC_KEF0103
entity:SSC_KEF0103 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_KEF0103 |  |  | ref:ifcName | SSC_KEF0103
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Running_Status | brick:On_Off_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Running_Status | brick:On_Off_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0103_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0103_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.AutoCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.AutoCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.AutoManSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.AutoManSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.LocSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.LocSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.ManCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.ManCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Running_Status | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.RunSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Running_Status | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.RunSts |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.StartCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.StartCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.StopCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.StopCmd |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.TripAlm |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0103.TripAlm |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0103_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0103
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_KEF0303_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_KEF0303_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0303_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0303_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0303_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_KEF0303_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC_KEF0303 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC_KEF0303 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_KEF0303 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_KEF0303 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_KEF0303 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_KEF0303 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_KEF0303 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_KEF0303 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_KEF0303 |  |  | ref:ifcName | SSC_KEF0303
entity:SSC_KEF0303 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_KEF0303 |  |  | ref:ifcName | SSC_KEF0303
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Running_Status | brick:On_Off_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Running_Status | brick:On_Off_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor | brick:Motor | brick:hasPoint | entity:SSC_KEF0303_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_KEF0303_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.AutoCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.AutoCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.AutoManSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.AutoManSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.LocSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.LocSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.ManCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.ManCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Running_Status | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.RunSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Running_Status | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.RunSts |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.StartCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.StartCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.StopCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.StopCmd |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.TripAlm |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_KEF0303.TripAlm |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_KEF0303_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_KEF0303
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Battery_Voltage | brick:Battery_Voltage_Sensor |  |  | rdfs:label_en | Battery Voltage |  |  | brick:hasUnit | unit:V
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Current_Reading | brick:Current_Sensor |  |  | rdfs:label_en | Current Reading |  |  | brick:hasUnit | unit:A
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Engine_Oil_Pressure_Reading | brick:Pressure_Sensor |  |  | rdfs:label_en | Engine Oil Pressure Reading |  |  | brick:hasUnit | unit:PA
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Frequency_Reading | brick:Frequency_Sensor |  |  | rdfs:label_en | Frequency Reading |  |  | brick:hasUnit | unit:HZ
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Apparent_Power | brick:Apparent_Power_Sensor |  |  | rdfs:label_en | Apparent Power |  |  | brick:hasUnit | unit:KVA
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Active_Power | brick:Active_Power_Sensor |  |  | rdfs:label_en | Active Power |  |  | brick:hasUnit | unit:KiloW
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Energy | brick:Energy_Sensor |  |  | rdfs:label_en | Energy |  |  | brick:hasUnit | unit:KiloWHR
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Generator_Running_Status | brick:Run_Status |  |  | rdfs:label_en | Generator Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Runtime_Meter | brick:Duration_Sensor |  |  | rdfs:label_en | Runtime Meter |  |  | brick:hasUnit | unit:HR
entity:SSC_MV_Generator | para:Generator | brick:hasPoint | entity:SSC_MV_Generator_Voltage | brick:Voltage_Sensor |  |  | rdfs:label_en | Voltage |  |  | brick:hasUnit | unit:V
entity:SSC_MV_Generator | para:Generator | brick:isPartOf | entity:HVAC | entity:Electrical_System | brick:System | SSC_MV_Generator |  |  | brick:aliasOf | <AliasOf>
entity:SSC_MV_Generator | para:Generator | para:ratedFrequency | <blanknode> | <blanknode> |  |  | brick:value |  |  |  | brick:hasUnit | unit:HZ
entity:SSC_MV_Generator | para:Generator | para:ratedPower | <blanknode> | <blanknode> |  |  | brick:value |  |  |  | brick:hasUnit | unit:KVA
entity:SSC_MV_Generator | para:Generator | para:ratedVoltage | <blanknode> | <blanknode> |  |  | brick:value |  |  |  | brick:hasUnit | unit:V
entity:SSC_MV_Generator | para:Generator | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_MV_Generator |  |  | ref:ifcName | SSC_MV_Generator
entity:SSC_MV_Generator_Active_Power | brick:Active_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.kW |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Apparent_Power | brick:Apparent_Power_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.kVA |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Battery_Voltage | brick:Battery_Voltage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.BattVoltage |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Current_Reading | brick:Current_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.Current |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Energy | brick:Energy_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.kWh |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Engine_Oil_Pressure_Reading | brick:Pressure_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.EngOilPrs |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Frequency_Reading | brick:Frequency_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.Frequency |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Generator_Running_Status | brick:Run_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.RunSts |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Runtime_Meter | brick:Duration_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.RuntimeMtr |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_MV_Generator_Voltage | brick:Voltage_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_MV_Generator.Voltage |  |  | para:hasEntityId | SSC_MV_Generator
entity:SSC_ST-10_STAIR-10 | rec:Room | rec:isPartOf | entity:SSC_Level-01 | rec:Level | rdfs:label_en | ST-10_STAIR-10
entity:SSC_TEF0101 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_TEF0101_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_TEF0101 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0101_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0101 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0101_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0101 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC_TEF0101 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_TEF0101 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_TEF0101 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_TEF0101 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_TEF0101 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_TEF0101 |  |  | ref:ifcName | SSC_TEF0101
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_PDSL_OnOff_Status | brick:Status |  |  | rdfs:label_en | PDSL On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Running_Status | brick:Fan_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0101_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0101_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.AutoCmd |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.AutoManSts |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.LocSts |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.ManCmd |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_PDSL_OnOff_Status | brick:Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101_PDSL.OnOffSts |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101_RtnAirPrsSW.Alm |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Running_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.RunSts |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.StartCmd |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.StopCmd |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0101.TripAlm |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0101_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0101
entity:SSC_TEF0102 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_TEF0102_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_TEF0102 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0102_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0102 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0102_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0102 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC_TEF0102 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_TEF0102 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_TEF0102 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_TEF0102 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_TEF0102 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_TEF0102 |  |  | ref:ifcName | SSC_TEF0102
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_PDSL_OnOff_Status | brick:Status |  |  | rdfs:label_en | PDSL On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Running_Status | brick:Fan_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0102_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0102_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.AutoCmd |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.AutoManSts |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.LocSts |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.ManCmd |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_PDSL_OnOff_Status | brick:Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102_PDSL.OnOffSts |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102_RtnAirPrsSW.Alm |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Running_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.RunSts |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.StartCmd |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.StopCmd |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0102.TripAlm |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0102_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0102
entity:SSC_TEF0301 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_TEF0301_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_TEF0301 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0301_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0301 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0301_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0301 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC_TEF0301 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_TEF0301 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_TEF0301 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_TEF0301 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_TEF0301 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_TEF0301 |  |  | ref:ifcName | SSC_TEF0301
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_PDSL_OnOff_Status | brick:Status |  |  | rdfs:label_en | PDSL On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Running_Status | brick:Fan_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0301_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0301_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.AutoCmd |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.AutoManSts |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.LocSts |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.ManCmd |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_PDSL_OnOff_Status | brick:Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301_PDSL.OnOffSts |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301_RtnAirPrsSW.Alm |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Running_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.RunSts |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.StartCmd |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.StopCmd |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0301.TripAlm |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0301_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0301
entity:SSC_TEF0302 | brick:Exhaust_Fan | brick:hasPart | entity:SSC_TEF0302_Motor | brick:Motor |  |  | rdfs:label_en | Garauge Exhaust Fan Motor
entity:SSC_TEF0302 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0302_Starttime | para:Start_Time |  |  | rdfs:label_en | Start Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0302 | brick:Exhaust_Fan | brick:hasPoint | entity:SSC_TEF0302_Stoptime | para:Stop_Time |  |  | rdfs:label_en | Stop Time |  |  | brick:hasUnit | unit:EPOCH |  |  | para:format | hh:mma
entity:SSC_TEF0302 | brick:Exhaust_Fan | brick:isPartOf | entity:HVAC | brick:HVAC_System | rdfs:label_en | SSC_TEF0302 |  |  | brick:aliasOf | <AliasOf>
entity:SSC_TEF0302 | brick:Exhaust_Fan | brick:ratedPowerInput | <blanknode> | <blanknode> |  |  | brick:value | 0.86 |  |  | brick:hasUnit | unit:KiloW
entity:SSC_TEF0302 | brick:Exhaust_Fan | rec:feeds | entity:Level7_Office0367 | rec:Room
entity:SSC_TEF0302 | brick:Exhaust_Fan | rec:locatedIn | entity:Level7_Office0367 | rec:Room | rec:modelNumber | AVT8X |  |  | rec:manufacturedBy | NuAire
entity:SSC_TEF0302 | brick:Exhaust_Fan | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_TEF0302 |  |  | ref:ifcName | SSC_TEF0302
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Auto_Command | brick:Automatic_Mode_Command |  |  | rdfs:label_en | Auto Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Auto_Manual_Status | brick:Manual_Auto_Status |  |  | rdfs:label_en | Auto Manual Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status |  |  | rdfs:label_en | Local On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_PDSL_OnOff_Status | brick:Status |  |  | rdfs:label_en | PDSL On Off Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Manual_Command | brick:Fan_Command |  |  | rdfs:label_en | Manual Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Running_Status | brick:Fan_Status |  |  | rdfs:label_en | Running Status |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Start_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Start Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Stop_Command | brick:Start_Stop_Command |  |  | rdfs:label_en | Stop Command |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Trip_Alarm | brick:Alarm |  |  | rdfs:label_en | Trip Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor | brick:Motor | brick:hasPoint | entity:SSC_TEF0302_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm |  |  | rdfs:label_en | General Alarm |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_TEF0302_Motor_Auto_Command | brick:Automatic_Mode_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.AutoCmd |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Auto_Manual_Status | brick:Manual_Auto_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.AutoManSts |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_LOC_On_Off_Status | brick:Fan_On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.LocSts |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Manual_Command | brick:Fan_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.ManCmd |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_PDSL_OnOff_Status | brick:Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302_PDSL.OnOffSts |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Rtn_Air_Prs_Sw_Alarm | brick:Air_Flow_Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302_RtnAirPrsSW.Alm |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Running_Status | brick:Fan_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.RunSts |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Start_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.StartCmd |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Stop_Command | brick:Start_Stop_Command | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.StopCmd |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Motor_Trip_Alarm | brick:Alarm | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_TEF0302.TripAlm |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Starttime | para:Start_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | START_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_TEF0302_Stoptime | para:Stop_Time | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | STOP_TSMS_CALC |  |  | para:hasEntityId | SSC_TEF0302
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0001_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0001_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0001 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_B1_015_ENTRANCE | rec:Room | brick:aliasOf
entity:SSC_VAV0001 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0001 |  |  | ref:ifcName | SSC_VAV0001
entity:SSC_VAV0001_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.AirFlow |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0001_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0001_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.DmprPos |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.OccSts |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.RmTemp |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0001.SP |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0001_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0001
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0002_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0002_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0002 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_014_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0002 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0002 |  |  | ref:ifcName | SSC_VAV0002
entity:SSC_VAV0002_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.AirFlow |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0002_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0002_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.DmprPos |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.OccSts |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.RmTemp |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0002.SP |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0002_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0002
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0003_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0003_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0003 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_014_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0003 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0003 |  |  | ref:ifcName | SSC_VAV0003
entity:SSC_VAV0003_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.AirFlow |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0003_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0003_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.DmprPos |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.OccSts |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.RmTemp |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0003.SP |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0003_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0003
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0004_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0004_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0004 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_014_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0004 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0004 |  |  | ref:ifcName | SSC_VAV0004
entity:SSC_VAV0004_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.AirFlow |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0004_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0004_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.DmprPos |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.OccSts |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.RmTemp |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0004.SP |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0004_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0004
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0005_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0005_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0005 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_015_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0005 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0005 |  |  | ref:ifcName | SSC_VAV0005
entity:SSC_VAV0005_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.AirFlow |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0005_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0005_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.DmprPos |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.OccSts |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.RmTemp |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0005.SP |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0005_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0005
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0006_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0006_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0006 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_015_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0006 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0006 |  |  | ref:ifcName | SSC_VAV0006
entity:SSC_VAV0006_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.AirFlow |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0006_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0006_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.DmprPos |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.OccSts |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.RmTemp |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0006.SP |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0006_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0006
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0007_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0007_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0007 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_015_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0007 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0007 |  |  | ref:ifcName | SSC_VAV0007
entity:SSC_VAV0007_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.AirFlow |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0007_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0007_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.DmprPos |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.OccSts |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.RmTemp |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0007.SP |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0007_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0007
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0008_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0008_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0008 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_024_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0008 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0008 |  |  | ref:ifcName | SSC_VAV0008
entity:SSC_VAV0008_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.AirFlow |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0008_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0008_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.DmprPos |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.OccSts |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.RmTemp |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0008.SP |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0008_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0008
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0009_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0009_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0009 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0009 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0009 |  |  | ref:ifcName | SSC_VAV0009
entity:SSC_VAV0009_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.AirFlow |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0009_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0009_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.DmprPos |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.OccSts |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.RmTemp |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0009.SP |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0009_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0009
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0010_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0010_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0010 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0010 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0010 |  |  | ref:ifcName | SSC_VAV0010
entity:SSC_VAV0010_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.AirFlow |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0010_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0010_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.DmprPos |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.OccSts |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.RmTemp |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0010.SP |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0010_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0010
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0011_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0011_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0011 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0011 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0011 |  |  | ref:ifcName | SSC_VAV0011
entity:SSC_VAV0011_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.AirFlow |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0011_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0011_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.DmprPos |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.OccSts |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.RmTemp |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0011.SP |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0011_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0011
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0012_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0012_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0012 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0012 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0012 |  |  | ref:ifcName | SSC_VAV0012
entity:SSC_VAV0012_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.AirFlow |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0012_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0012_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.DmprPos |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.OccSts |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.RmTemp |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0012.SP |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0012_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0012
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0013_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0013_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0013 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0013 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0013 |  |  | ref:ifcName | SSC_VAV0013
entity:SSC_VAV0013_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.AirFlow |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0013_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0013_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.DmprPos |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.OccSts |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.RmTemp |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0013.SP |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0013_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0013
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0014_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0014_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0014 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_019_PRAYER_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0014 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0014 |  |  | ref:ifcName | SSC_VAV0014
entity:SSC_VAV0014_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.AirFlow |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0014_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0014_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.DmprPos |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.OccSts |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.RmTemp |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0014.SP |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0014_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0014
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0015_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0015_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0015 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_ROOM_NO_42 | rec:Room | brick:aliasOf
entity:SSC_VAV0015 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0015 |  |  | ref:ifcName | SSC_VAV0015
entity:SSC_VAV0015_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.AirFlow |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0015_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0015_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.DmprPos |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.OccSts |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.RmTemp |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0015.SP |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0015_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0015
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0016_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0016_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0016 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_ROOM_NO_43 | rec:Room | brick:aliasOf
entity:SSC_VAV0016 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0016 |  |  | ref:ifcName | SSC_VAV0016
entity:SSC_VAV0016_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.AirFlow |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0016_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0016_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.DmprPos |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.OccSts |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.RmTemp |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0016.SP |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0016_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0016
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0017_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0017_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0017 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_ROOM_NO_44 | rec:Room | brick:aliasOf
entity:SSC_VAV0017 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0017 |  |  | ref:ifcName | SSC_VAV0017
entity:SSC_VAV0017_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.AirFlow |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0017_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0017_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.DmprPos |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.OccSts |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.RmTemp |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0017.SP |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0017_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0017
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0018_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0018_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0018 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0018 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0018 |  |  | ref:ifcName | SSC_VAV0018
entity:SSC_VAV0018_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.AirFlow |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0018_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0018_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.DmprPos |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.OccSts |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.RmTemp |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0018.SP |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0018_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0018
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0019_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0019_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0019 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0019 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0019 |  |  | ref:ifcName | SSC_VAV0019
entity:SSC_VAV0019_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.AirFlow |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0019_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0019_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.DmprPos |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.OccSts |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.RmTemp |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0019.SP |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0019_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0019
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0020_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0020_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0020 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_029_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0020 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0020 |  |  | ref:ifcName | SSC_VAV0020
entity:SSC_VAV0020_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.AirFlow |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0020_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0020_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.DmprPos |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.OccSts |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.RmTemp |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0020.SP |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0020_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0020
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0021_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0021_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0021 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_013_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0021 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0021 |  |  | ref:ifcName | SSC_VAV0021
entity:SSC_VAV0021_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.AirFlow |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0021_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0021_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.DmprPos |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.OccSts |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.RmTemp |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0021.SP |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0021_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0021
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0022_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0022_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0022 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_003_OPEN_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0022 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0022 |  |  | ref:ifcName | SSC_VAV0022
entity:SSC_VAV0022_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.AirFlow |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0022_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0022_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.DmprPos |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.OccSts |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.RmTemp |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0022.SP |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0022_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0022
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0023_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0023_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0023 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_003_OPEN_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0023 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0023 |  |  | ref:ifcName | SSC_VAV0023
entity:SSC_VAV0023_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.AirFlow |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0023_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0023_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.DmprPos |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.OccSts |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.RmTemp |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0023.SP |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0023_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0023
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0024_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0024_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0024 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_001_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0024 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0024 |  |  | ref:ifcName | SSC_VAV0024
entity:SSC_VAV0024_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.AirFlow |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0024_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0024_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.DmprPos |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.OccSts |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.RmTemp |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0024.SP |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0024_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0024
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0025_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0025_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0025 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_002_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0025 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0025 |  |  | ref:ifcName | SSC_VAV0025
entity:SSC_VAV0025_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.AirFlow |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0025_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0025_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.DmprPos |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.OccSts |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.RmTemp |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0025.SP |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0025_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0025
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0026_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0026_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0026 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_002_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0026 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0026 |  |  | ref:ifcName | SSC_VAV0026
entity:SSC_VAV0026_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.AirFlow |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0026_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0026_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.DmprPos |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.OccSts |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.RmTemp |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0026.SP |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0026_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0026
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0027_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0027_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0027 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_002_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0027 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0027 |  |  | ref:ifcName | SSC_VAV0027
entity:SSC_VAV0027_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.AirFlow |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0027_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0027_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.DmprPos |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.OccSts |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.RmTemp |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0027.SP |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0027_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0027
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0028_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0028_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0028 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_002_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0028 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0028 |  |  | ref:ifcName | SSC_VAV0028
entity:SSC_VAV0028_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.AirFlow |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0028_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0028_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.DmprPos |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.OccSts |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.RmTemp |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0028.SP |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0028_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0028
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0029_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0029_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0029 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_001_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0029 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0029 |  |  | ref:ifcName | SSC_VAV0029
entity:SSC_VAV0029_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.AirFlow |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0029_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0029_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.DmprPos |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.OccSts |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.RmTemp |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0029.SP |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0029_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0029
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0030_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0030_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0030 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_016_SHELL_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0030 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0030 |  |  | ref:ifcName | SSC_VAV0030
entity:SSC_VAV0030_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.AirFlow |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0030_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0030_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.DmprPos |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.OccSts |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.RmTemp |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0030.SP |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0030_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0030
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0031_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0031_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0031 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_001_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0031 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0031 |  |  | ref:ifcName | SSC_VAV0031
entity:SSC_VAV0031_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.AirFlow |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0031_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0031_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.DmprPos |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.OccSts |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.RmTemp |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0031.SP |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0031_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0031
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0032_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0032_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0032 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_018_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0032 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0032 |  |  | ref:ifcName | SSC_VAV0032
entity:SSC_VAV0032_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.AirFlow |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0032_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0032_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.DmprPos |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.OccSts |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.RmTemp |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0032.SP |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0032_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0032
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0033_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0033_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0033 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_028_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0033 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0033 |  |  | ref:ifcName | SSC_VAV0033
entity:SSC_VAV0033_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.AirFlow |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0033_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0033_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.DmprPos |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.OccSts |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.RmTemp |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0033.SP |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0033_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0033
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0034_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0034_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0034 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_003_OPEN_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0034 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0034 |  |  | ref:ifcName | SSC_VAV0034
entity:SSC_VAV0034_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.AirFlow |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0034_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0034_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.DmprPos |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.OccSts |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.RmTemp |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0034.SP |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0034_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0034
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0035_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0035_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0035 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_010_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0035 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0035 |  |  | ref:ifcName | SSC_VAV0035
entity:SSC_VAV0035_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.AirFlow |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0035_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0035_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.DmprPos |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.OccSts |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.RmTemp |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0035.SP |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0035_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0035
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0036_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0036_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0036 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_022_ABLUTION_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0036 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0036 |  |  | ref:ifcName | SSC_VAV0036
entity:SSC_VAV0036_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.AirFlow |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0036_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0036_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.DmprPos |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.OccSts |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.RmTemp |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0036.SP |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0036_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0036
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0037_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0037_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0037 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_008_AV_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0037 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0037 |  |  | ref:ifcName | SSC_VAV0037
entity:SSC_VAV0037_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.AirFlow |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0037_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0037_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.DmprPos |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.OccSts |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.RmTemp |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0037.SP |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0037_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0037
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0038_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0038_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0038 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_ST-4_STAIR_4 | rec:Room | brick:aliasOf
entity:SSC_VAV0038 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0038 |  |  | ref:ifcName | SSC_VAV0038
entity:SSC_VAV0038_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.AirFlow |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0038_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0038_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.DmprPos |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.OccSts |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.RmTemp |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0038.SP |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0038_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0038
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0039_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0039_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0039 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_01_003_OPEN_SPACE | rec:Room | brick:aliasOf
entity:SSC_VAV0039 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0039 |  |  | ref:ifcName | SSC_VAV0039
entity:SSC_VAV0039_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.AirFlow |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0039_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0039_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.DmprPos |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.OccSts |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.RmTemp |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0039.SP |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0039_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0039
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0040_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0040_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0040 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_006_CONFERENCE_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0040 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0040 |  |  | ref:ifcName | SSC_VAV0040
entity:SSC_VAV0040_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.AirFlow |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0040_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0040_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.DmprPos |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.OccSts |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.RmTemp |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0040.SP |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0040_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0040
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0041_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0041_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0041 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0041 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0041 |  |  | ref:ifcName | SSC_VAV0041
entity:SSC_VAV0041_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.AirFlow |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0041_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0041_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.DmprPos |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.OccSts |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.RmTemp |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0041.SP |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0041_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0041
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0042_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0042_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0042 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0042 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0042 |  |  | ref:ifcName | SSC_VAV0042
entity:SSC_VAV0042_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.AirFlow |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0042_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0042_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.DmprPos |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.OccSts |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.RmTemp |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0042.SP |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0042_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0042
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0043_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0043_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0043 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_004_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0043 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0043 |  |  | ref:ifcName | SSC_VAV0043
entity:SSC_VAV0043_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.AirFlow |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0043_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0043_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.DmprPos |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.OccSts |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.RmTemp |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0043.SP |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0043_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0043
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0044_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0044_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0044 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_001_FOYER | rec:Room | brick:aliasOf
entity:SSC_VAV0044 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0044 |  |  | ref:ifcName | SSC_VAV0044
entity:SSC_VAV0044_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.AirFlow |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0044_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0044_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.DmprPos |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.OccSts |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.RmTemp |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0044.SP |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0044_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0044
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0045_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0045_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0045 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_001_FOYER | rec:Room | brick:aliasOf
entity:SSC_VAV0045 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0045 |  |  | ref:ifcName | SSC_VAV0045
entity:SSC_VAV0045_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.AirFlow |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0045_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0045_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.DmprPos |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.OccSts |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.RmTemp |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0045.SP |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0045_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0045
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0046_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0046_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0046 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_002_LOBBY | rec:Room | brick:aliasOf
entity:SSC_VAV0046 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0046 |  |  | ref:ifcName | SSC_VAV0046
entity:SSC_VAV0046_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.AirFlow |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0046_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0046_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.DmprPos |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.OccSts |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.RmTemp |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0046.SP |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0046_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0046
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0047_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0047_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0047 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_002_LOBBY | rec:Room | brick:aliasOf
entity:SSC_VAV0047 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0047 |  |  | ref:ifcName | SSC_VAV0047
entity:SSC_VAV0047_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.AirFlow |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0047_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0047_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.DmprPos |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.OccSts |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.RmTemp |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0047.SP |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0047_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0047
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0048_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0048_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0048 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_002_LOBBY | rec:Room | brick:aliasOf
entity:SSC_VAV0048 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0048 |  |  | ref:ifcName | SSC_VAV0048
entity:SSC_VAV0048_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.AirFlow |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0048_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0048_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.DmprPos |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.OccSts |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.RmTemp |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0048.SP |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0048_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0048
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0049_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0049_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0049 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_002_LOBBY | rec:Room | brick:aliasOf
entity:SSC_VAV0049 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0049 |  |  | ref:ifcName | SSC_VAV0049
entity:SSC_VAV0049_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.AirFlow |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0049_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0049_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.DmprPos |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.OccSts |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.RmTemp |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0049.SP |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0049_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0049
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0050_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0050_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0050 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_003_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0050 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0050 |  |  | ref:ifcName | SSC_VAV0050
entity:SSC_VAV0050_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.AirFlow |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0050_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0050_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.DmprPos |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.OccSts |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.RmTemp |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0050.SP |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0050_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0050
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0051_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0051_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0051 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0051 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0051 |  |  | ref:ifcName | SSC_VAV0051
entity:SSC_VAV0051_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.AirFlow |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0051_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0051_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.DmprPos |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.OccSts |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.RmTemp |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0051.SP |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0051_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0051
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0052_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0052_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0052 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_02_006_CONFERENCE_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0052 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0052 |  |  | ref:ifcName | SSC_VAV0052
entity:SSC_VAV0052_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.AirFlow |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0052_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0052_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.DmprPos |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.OccSts |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.RmTemp |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0052.SP |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0052_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0052
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0053_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0053_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0053 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_015_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0053 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0053 |  |  | ref:ifcName | SSC_VAV0053
entity:SSC_VAV0053_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.AirFlow |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0053_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0053_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.DmprPos |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.OccSts |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.RmTemp |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0053.SP |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0053_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0053
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0054_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0054_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0054 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_014_VISITORS_CUBICLE | rec:Room | brick:aliasOf
entity:SSC_VAV0054 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0054 |  |  | ref:ifcName | SSC_VAV0054
entity:SSC_VAV0054_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.AirFlow |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0054_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0054_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.DmprPos |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.OccSts |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.RmTemp |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0054.SP |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0054_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0054
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0055_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0055_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0055 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_013_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0055 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0055 |  |  | ref:ifcName | SSC_VAV0055
entity:SSC_VAV0055_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.AirFlow |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0055_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0055_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.DmprPos |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.OccSts |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.RmTemp |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0055.SP |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0055_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0055
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0056_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0056_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0056 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_012_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0056 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0056 |  |  | ref:ifcName | SSC_VAV0056
entity:SSC_VAV0056_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.AirFlow |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0056_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0056_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.DmprPos |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.OccSts |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.RmTemp |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0056.SP |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0056_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0056
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0057_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0057_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0057 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_011_VISITORS_CUBICLE | rec:Room | brick:aliasOf
entity:SSC_VAV0057 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0057 |  |  | ref:ifcName | SSC_VAV0057
entity:SSC_VAV0057_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.AirFlow |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0057_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0057_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.DmprPos |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.OccSts |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.RmTemp |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0057.SP |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0057_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0057
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0058_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0058_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0058 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_010_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0058 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0058 |  |  | ref:ifcName | SSC_VAV0058
entity:SSC_VAV0058_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.AirFlow |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0058_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0058_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.DmprPos |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.OccSts |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.RmTemp |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0058.SP |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0058_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0058
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0059_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0059_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0059 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_009_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0059 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0059 |  |  | ref:ifcName | SSC_VAV0059
entity:SSC_VAV0059_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.AirFlow |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0059_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0059_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.DmprPos |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.OccSts |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.RmTemp |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0059.SP |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0059_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0059
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0060_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0060_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0060 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_008_VISITORS_CUBICLE | rec:Room | brick:aliasOf
entity:SSC_VAV0060 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0060 |  |  | ref:ifcName | SSC_VAV0060
entity:SSC_VAV0060_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.AirFlow |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0060_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0060_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.DmprPos |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.OccSts |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.RmTemp |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0060.SP |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0060_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0060
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0061_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0061_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0061 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_007_OPERATIONS_MANAGER | rec:Room | brick:aliasOf
entity:SSC_VAV0061 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0061 |  |  | ref:ifcName | SSC_VAV0061
entity:SSC_VAV0061_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.AirFlow |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0061_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0061_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.DmprPos |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.OccSts |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.RmTemp |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0061.SP |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0061_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0061
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0062_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0062_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0062 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_006_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0062 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0062 |  |  | ref:ifcName | SSC_VAV0062
entity:SSC_VAV0062_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.AirFlow |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0062_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0062_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.DmprPos |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.OccSts |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.RmTemp |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0062.SP |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0062_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0062
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0063_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0063_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0063 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | rec:locatedIn | #N/A | rec:Room | brick:aliasOf
entity:SSC_VAV0063 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0063 |  |  | ref:ifcName | SSC_VAV0063
entity:SSC_VAV0063_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.AirFlow |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0063_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0063_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.DmprPos |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.OccSts |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.RmTemp |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0063.SP |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0063_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0063
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0064_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0064_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0064 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_006_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0064 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0064 |  |  | ref:ifcName | SSC_VAV0064
entity:SSC_VAV0064_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.AirFlow |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0064_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0064_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.DmprPos |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.OccSts |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.RmTemp |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0064.SP |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0064_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0064
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0065_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0065_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0065 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_005_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0065 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0065 |  |  | ref:ifcName | SSC_VAV0065
entity:SSC_VAV0065_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.AirFlow |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0065_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0065_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.DmprPos |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.OccSts |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.RmTemp |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0065.SP |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0065_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0065
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0066_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0066_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0066 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_004_VISITORS_CUBICLE | rec:Room | brick:aliasOf
entity:SSC_VAV0066 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0066 |  |  | ref:ifcName | SSC_VAV0066
entity:SSC_VAV0066_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.AirFlow |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0066_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0066_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.DmprPos |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.OccSts |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.RmTemp |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0066.SP |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0066_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0066
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0067_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0067_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0067 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_003_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0067 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0067 |  |  | ref:ifcName | SSC_VAV0067
entity:SSC_VAV0067_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.AirFlow |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0067_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0067_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.DmprPos |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.OccSts |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.RmTemp |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0067.SP |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0067_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0067
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0068_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0068_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0068 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0068 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0068 |  |  | ref:ifcName | SSC_VAV0068
entity:SSC_VAV0068_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.AirFlow |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0068_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0068_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.DmprPos |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.OccSts |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.RmTemp |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0068.SP |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0068_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0068
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0069_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0069_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0069 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0069 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0069 |  |  | ref:ifcName | SSC_VAV0069
entity:SSC_VAV0069_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.AirFlow |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0069_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0069_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.DmprPos |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.OccSts |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.RmTemp |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0069.SP |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0069_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0069
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0070_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0070_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0070 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_001_DIRECTORS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0070 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0070 |  |  | ref:ifcName | SSC_VAV0070
entity:SSC_VAV0070_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.AirFlow |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0070_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0070_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.DmprPos |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.OccSts |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.RmTemp |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0070.SP |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0070_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0070
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0071_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0071_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0071 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0071 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0071 |  |  | ref:ifcName | SSC_VAV0071
entity:SSC_VAV0071_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.AirFlow |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0071_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0071_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.DmprPos |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.OccSts |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.RmTemp |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0071.SP |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0071_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0071
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0072_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0072_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0072 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0072 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0072 |  |  | ref:ifcName | SSC_VAV0072
entity:SSC_VAV0072_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.AirFlow |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0072_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0072_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.DmprPos |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.OccSts |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.RmTemp |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0072.SP |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0072_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0072
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0073_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0073_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0073 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0073 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0073 |  |  | ref:ifcName | SSC_VAV0073
entity:SSC_VAV0073_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.AirFlow |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0073_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0073_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.DmprPos |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.OccSts |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.RmTemp |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0073.SP |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0073_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0073
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0074_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0074_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0074 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0074 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0074 |  |  | ref:ifcName | SSC_VAV0074
entity:SSC_VAV0074_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.AirFlow |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0074_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0074_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.DmprPos |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.OccSts |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.RmTemp |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0074.SP |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0074_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0074
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0075_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0075_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0075 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0075 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0075 |  |  | ref:ifcName | SSC_VAV0075
entity:SSC_VAV0075_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.AirFlow |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0075_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0075_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.DmprPos |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.OccSts |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.RmTemp |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0075.SP |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0075_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0075
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0076_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0076_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0076 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0076 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0076 |  |  | ref:ifcName | SSC_VAV0076
entity:SSC_VAV0076_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.AirFlow |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0076_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0076_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.DmprPos |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.OccSts |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.RmTemp |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0076.SP |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0076_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0076
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0077_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0077_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0077 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0077 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0077 |  |  | ref:ifcName | SSC_VAV0077
entity:SSC_VAV0077_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.AirFlow |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0077_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0077_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.DmprPos |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.OccSts |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.RmTemp |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0077.SP |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0077_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0077
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0078_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0078_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0078 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_031_ASSOC_DIRECTORS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0078 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0078 |  |  | ref:ifcName | SSC_VAV0078
entity:SSC_VAV0078_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.AirFlow |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0078_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0078_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.DmprPos |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.OccSts |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.RmTemp |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0078.SP |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0078_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0078
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0079_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0079_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0079 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_030_ASSOC_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0079 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0079 |  |  | ref:ifcName | SSC_VAV0079
entity:SSC_VAV0079_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.AirFlow |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0079_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0079_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.DmprPos |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.OccSts |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.RmTemp |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0079.SP |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0079_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0079
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0080_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0080_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0080 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_030_ASSOC_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0080 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0080 |  |  | ref:ifcName | SSC_VAV0080
entity:SSC_VAV0080_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.AirFlow |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0080_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0080_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.DmprPos |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.OccSts |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.RmTemp |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0080.SP |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0080_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0080
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0081_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0081_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0081 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_029_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0081 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0081 |  |  | ref:ifcName | SSC_VAV0081
entity:SSC_VAV0081_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.AirFlow |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0081_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0081_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.DmprPos |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.OccSts |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.RmTemp |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0081.SP |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0081_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0081
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0082_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0082_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0082 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_028_VISITORS_CUBICLE | rec:Room | brick:aliasOf
entity:SSC_VAV0082 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0082 |  |  | ref:ifcName | SSC_VAV0082
entity:SSC_VAV0082_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.AirFlow |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0082_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0082_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.DmprPos |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.OccSts |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.RmTemp |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0082.SP |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0082_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0082
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0083_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0083_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0083 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_027_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0083 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0083 |  |  | ref:ifcName | SSC_VAV0083
entity:SSC_VAV0083_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.AirFlow |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0083_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0083_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.DmprPos |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.OccSts |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.RmTemp |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0083.SP |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0083_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0083
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0084_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0084_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0084 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_026_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0084 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0084 |  |  | ref:ifcName | SSC_VAV0084
entity:SSC_VAV0084_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.AirFlow |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0084_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0084_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.DmprPos |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.OccSts |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.RmTemp |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0084.SP |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0084_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0084
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0085_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0085_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0085 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_026_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0085 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0085 |  |  | ref:ifcName | SSC_VAV0085
entity:SSC_VAV0085_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.AirFlow |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0085_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0085_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.DmprPos |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.OccSts |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.RmTemp |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0085.SP |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0085_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0085
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0086_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0086_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0004 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0086 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_026_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0086 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0086 |  |  | ref:ifcName | SSC_VAV0086
entity:SSC_VAV0086_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.AirFlow |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0086_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0086_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.DmprPos |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.OccSts |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.RmTemp |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0086.SP |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0086_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0086
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0087_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0087_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0087 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_025_SECRETARIAL_AREA | rec:Room | brick:aliasOf
entity:SSC_VAV0087 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0087 |  |  | ref:ifcName | SSC_VAV0087
entity:SSC_VAV0087_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.AirFlow |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0087_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0087_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.DmprPos |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.OccSts |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.RmTemp |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0087.SP |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0087_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0087
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0088_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0088_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0088 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_024_VISITORS_CUBICLE | rec:Room | brick:aliasOf
entity:SSC_VAV0088 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0088 |  |  | ref:ifcName | SSC_VAV0088
entity:SSC_VAV0088_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.AirFlow |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0088_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0088_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.DmprPos |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.OccSts |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.RmTemp |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0088.SP |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0088_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0088
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0089_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0089_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0089 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_023_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0089 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0089 |  |  | ref:ifcName | SSC_VAV0089
entity:SSC_VAV0089_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.AirFlow |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0089_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0089_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.DmprPos |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.OccSts |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.RmTemp |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0089.SP |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0089_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0089
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0090_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0090_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0090 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_022_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0090 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0090 |  |  | ref:ifcName | SSC_VAV0090
entity:SSC_VAV0090_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.AirFlow |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0090_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0090_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.DmprPos |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.OccSts |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.RmTemp |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0090.SP |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0090_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0090
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0091_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0091_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0091 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_021_VISITORS_CUBICLE | rec:Room | brick:aliasOf
entity:SSC_VAV0091 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0091 |  |  | ref:ifcName | SSC_VAV0091
entity:SSC_VAV0091_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.AirFlow |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0091_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0091_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.DmprPos |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.OccSts |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.RmTemp |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0091.SP |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0091_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0091
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0092_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0092_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0092 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_020_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0092 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0092 |  |  | ref:ifcName | SSC_VAV0092
entity:SSC_VAV0092_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.AirFlow |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0092_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0092_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.DmprPos |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.OccSts |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.RmTemp |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0092.SP |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0092_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0092
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0093_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0093_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0093 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_019_IT_MANAGERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0093 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0093 |  |  | ref:ifcName | SSC_VAV0093
entity:SSC_VAV0093_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.AirFlow |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0093_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0093_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.DmprPos |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.OccSts |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.RmTemp |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0093.SP |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0093_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0093
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0094_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0094_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0094 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_018_VISITORS_CUBICLE | rec:Room | brick:aliasOf
entity:SSC_VAV0094 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0094 |  |  | ref:ifcName | SSC_VAV0094
entity:SSC_VAV0094_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.AirFlow |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0094_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0094_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.DmprPos |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.OccSts |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.RmTemp |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0094.SP |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0094_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0094
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0095_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0095_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0095 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_017_RESEARCHERS_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0095 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0095 |  |  | ref:ifcName | SSC_VAV0095
entity:SSC_VAV0095_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.AirFlow |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0095_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0095_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.DmprPos |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.OccSts |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.RmTemp |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0095.SP |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0095_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0095
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0096_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0096_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0096 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_016_LOUNGE | rec:Room | brick:aliasOf
entity:SSC_VAV0096 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0096 |  |  | ref:ifcName | SSC_VAV0096
entity:SSC_VAV0096_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.AirFlow |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0096_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0096_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.DmprPos |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.OccSts |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.RmTemp |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0096.SP |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0096_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0096
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0097_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0097_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0097 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_016_LOUNGE | rec:Room | brick:aliasOf
entity:SSC_VAV0097 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0097 |  |  | ref:ifcName | SSC_VAV0097
entity:SSC_VAV0097_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.AirFlow |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0097_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0097_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.DmprPos |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.OccSts |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.RmTemp |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0097.SP |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0097_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0097
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0098_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0098_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0098 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_049_IT_OFFICE | rec:Room | brick:aliasOf
entity:SSC_VAV0098 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0098 |  |  | ref:ifcName | SSC_VAV0098
entity:SSC_VAV0098_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.AirFlow |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0098_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0098_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.DmprPos |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.OccSts |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.RmTemp |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0098.SP |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0098_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0098
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0099_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0099_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0099 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_042_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0099 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0099 |  |  | ref:ifcName | SSC_VAV0099
entity:SSC_VAV0099_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.AirFlow |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0099_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0099_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.DmprPos |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.OccSts |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.RmTemp |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0099.SP |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0099_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0099
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0100_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0100_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0001 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0100 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_041_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0100 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0100 |  |  | ref:ifcName | SSC_VAV0100
entity:SSC_VAV0100_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.AirFlow |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0100_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0100_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.DmprPos |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.OccSts |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.RmTemp |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0100.SP |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0100_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0100
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0101_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0101_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0101 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_044_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0101 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0101 |  |  | ref:ifcName | SSC_VAV0101
entity:SSC_VAV0101_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.AirFlow |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0101_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0101_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.DmprPos |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.OccSts |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.RmTemp |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0101.SP |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0101_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0101
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0102_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0102_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0102_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0102_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0102_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0102_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0102_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0102_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0102 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_034_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0102 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0102 |  |  | ref:ifcName | SSC_VAV0102
entity:SSC_VAV0102_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.AirFlow |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0102_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0102_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.DmprPos |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.OccSts |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.RmTemp |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0102.SP |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0102_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0102
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0103_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0103_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0103_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0103_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0103_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0103_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0103_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0103_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0103 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_034_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0103 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0103 |  |  | ref:ifcName | SSC_VAV0103
entity:SSC_VAV0103_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.AirFlow |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0103_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0103_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.DmprPos |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.OccSts |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.RmTemp |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0103.SP |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0103_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0103
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0104_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0104_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0104 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_034_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0104 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0104 |  |  | ref:ifcName | SSC_VAV0104
entity:SSC_VAV0104_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.AirFlow |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0104_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0104_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.DmprPos |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.OccSts |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.RmTemp |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0104.SP |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0104_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0104
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0105_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0105_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0105 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_034_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0105 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0105 |  |  | ref:ifcName | SSC_VAV0105
entity:SSC_VAV0105_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.AirFlow |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0105_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0105_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.DmprPos |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.OccSts |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.RmTemp |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0105.SP |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0105_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0105
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0106_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0106_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | rec:isFedBy | entity:SSC_AHUB0002 | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0106 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_042_CORRIDOR | rec:Room | brick:aliasOf
entity:SSC_VAV0106 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0106 |  |  | ref:ifcName | SSC_VAV0106
entity:SSC_VAV0106_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.AirFlow |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0106_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0106_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.DmprPos |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.OccSts |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.RmTemp |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0106.SP |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0106_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0106
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0107_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0107_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0107 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0107 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0107 |  |  | ref:ifcName | SSC_VAV0107
entity:SSC_VAV0107_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.AirFlow |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0107_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0107_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.DmprPos |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.OccSts |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.RmTemp |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0107.SP |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0107_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0107
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPart | entity:SSC_VAV0108_Damper_Controller | brick:Controller |  |  | rdfs:label_en | Damper Controller
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_Air_Flow_Sensor | brick:Supply_Air_Flow |  |  | rdfs:label_en | Air Flow Sensor |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_ActiveState_CALC | brick:On_Off_Status |  |  | rdfs:label_en | Active State CALC |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_TotalOperationDuration | para:Operation_Hours |  |  | rdfs:label_en | Operating Duration CALC |  |  | brick:hasUnit | unit:HR
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_Effective_Temp_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Effective temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_Room_Temperature | brick:Temperature_Sensor |  |  | rdfs:label_en | Room Temperature |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_Temperature_Setpoint | brick:Temperature_Setpoint |  |  | rdfs:label_en | Temperature Setpoint |  |  | brick:hasUnit | unit:DEG_C
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:hasPoint | entity:SSC_VAV0108_Occupancy_Status | brick:Occupancy_Status |  |  | rdfs:label_en | Occupancy Mode |  |  | brick:hasUnit | unit:UNITLESS
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | brick:isPartOf | entity:HVAC | brick:System
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | para:ratedReheatCapacity | 1.5 |  |  |  | brick:hasUnit | unit:KiloW
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | para:ratedSupplyAirFlowrate | 165 |  |  |  | brick:hasUnit | unit:L-PER-SEC
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | rec:isFedBy | #N/A | brick:Air_Handling_Unit | rdfs:label_en | SSC_VAV0108 |  |  | rec:modelNumber | NBONEOB |  |  | para:vavBoxType |  |  |  | para:inletSize | 158 |  |  | para:outletSize | 350x175 |  |  | para:plenumBoxSize | Nil
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | rec:locatedIn | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | rec:Room | brick:aliasOf
entity:SSC_VAV0108 | brick:Variable_Air_Volume_Box | ref:hasExternalReference | <blanknode> | ref:IFCReference |  |  | para:IFC_ID | SSC_VAV0108 |  |  | ref:ifcName | SSC_VAV0108
entity:SSC_VAV0108_ActiveState_CALC | brick:On_Off_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | ACTIVESTATE_NA_CALC |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Air_Flow_Sensor | brick:Supply_Air_Flow | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.AirFlow |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Damper_Controller | brick:Controller | brick:hasPoint | entity:SSC_VAV0108_Damper_Position | brick:Valve_Position_Sensor |  |  | rdfs:label_en | Damper Position |  |  | brick:hasUnit | unit:PERCENT
entity:SSC_VAV0108_Damper_Position | brick:Valve_Position_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.DmprPos |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Effective_Temp_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.EffectiveSP |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Occupancy_Status | brick:Occupancy_Status | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.OccSts |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Room_Temperature | brick:Temperature_Sensor | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.RmTemp |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_Temperature_Setpoint | brick:Temperature_Setpoint | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | SSC_VAV0108.SP |  |  | para:hasEntityId | SSC_VAV0108
entity:SSC_VAV0108_TotalOperationDuration | para:Operation_Hours | ref:hasExternalReference | <blanknode> | ref:TimeseriesReference |  |  | ref:hasTimeseriesId | OPDURATIONTOTAL_HRS_CALC |  |  | para:hasEntityId | SSC_VAV0108
para:Chilled_Water_Loop_Network | owl:Class | rdfs:subClassOf | brick:HVAC_Equipment |  | rdfs:label_en | Chilled Water Loop Network
para:Close_command | owl:Class | rdfs:subClassOf | brick:Open_Close_Command |  | rdfs:label_en | Close Command
para:Command_Status | owl:Class | rdfs:subClassOf | brick:Manual_Auto_Status |  | rdfs:label_en | Auto Manual Command Status
para:Cooling_Mode_Operation_Hours | owl:Class | rdfs:subClassOf | para:Operation_Hours |  | rdfs:label_en | Cooling Mode Operating Duration
para:Damper_Position_100 | owl:Class | rdfs:subClassOf | brick:Valve_Position_Command |  | rdfs:comment | Damper Position 100%
para:Damper_Position_70 | owl:Class | rdfs:subClassOf | brick:Valve_Position_Command |  | rdfs:comment | Damper Position 70%
para:Damper_Position_77.5 | owl:Class | rdfs:subClassOf | brick:Valve_Position_Command |  | rdfs:comment | Damper Position 77.5%
para:Damper_Position_85 | owl:Class | rdfs:subClassOf | brick:Valve_Position_Command |  | rdfs:comment | Damper Position 85%
para:Damper_Position_92.5 | owl:Class | rdfs:subClassOf | brick:Valve_Position_Command |  | rdfs:comment | Damper Position 92.5%
para:Dehumidification_On_Status | owl:Class | rdfs:subClassOf | brick:Operating_Mode_Status |  | rdfs:label_en | Dehumidification On Status
para:DXUnit | owl:Class | rdfs:subClassOf | brick:Electrical_Equipment |  | rdfs:label_en | DX Unit
para:Fail_Start_Alarm | owl:Class | rdfs:subClassOf | brick:Alarm |  | rdfs:label_en | Fail to Start Alarm
para:Fail_Stop_Alarm | owl:Class | rdfs:subClassOf | brick:Alarm |  | rdfs:label_en | Fail to Stop Alarm
para:Fan_Mode_Operation_Hours | owl:Class | rdfs:subClassOf | para:Operation_Hours |  | rdfs:label_en | Fan Mode Operating Duration
para:Generator | owl:Class | rdfs:subClassOf | brick:Electrical_Equipment |  | rdfs:label_en | Generator
para:Heater_On_Status | owl:Class | rdfs:subClassOf | brick:Operating_Mode_Status |  | rdfs:label_en | Heater On Status
para:Humidification_On_Status | owl:Class | rdfs:subClassOf | brick:Operating_Mode_Status |  | rdfs:label_en | Humidification On Status
para:Open_command | owl:Class | rdfs:subClassOf | brick:Open_Close_Command |  | rdfs:label_en | Open Command
para:Operation_Hours | owl:Class | rdfs:subClassOf | brick:Duration_Sensor |  | rdfs:label_en | Operating Duration
para:Return_Air_Static_Pressure_Sensor | owl:Class | rdfs:subClassOf | brick:Air_Static_Pressure_Sensor |  | rdfs:label_en | Return Air Static Pressure
para:Return_Air_Static_Pressure_Sensor_01 | owl:Class | rdfs:subClassOf | brick:Air_Static_Pressure_Sensor |  | rdfs:label_en | Return Air Static Pressure 01
para:Return_Air_Static_Pressure_Sensor_02 | owl:Class | rdfs:subClassOf | brick:Air_Static_Pressure_Sensor |  | rdfs:label_en | Return Air Static Pressure 02
para:Scheduled_Hrs_Duration | owl:Class | rdfs:subClassOf | brick:Duration_Sensor |  | rdfs:label_en | Scheduled Hours of Operation
para:Start_Command | owl:Class | rdfs:subClassOf | brick:Start_Stop_Command |  | rdfs:label_en | Start Command
para:Start_Time | owl:Class | rdfs:subClassOf | brick:Duration_Sensor |  | rdfs:label_en | Start Time
para:Static_Pressure_Sensor | owl:Class | rdfs:subClassOf | brick:Supply_Air_Static_Pressure_Sensor |  | rdfs:label_en | Static Pressure Sensor
para:Static_Pressure_Sensor_01 | owl:Class | rdfs:subClassOf | brick:Supply_Air_Static_Pressure_Sensor |  | rdfs:label_en | Static Pressure Sensor 01
para:Static_Pressure_Sensor_02 | owl:Class | rdfs:subClassOf | brick:Supply_Air_Static_Pressure_Sensor |  | rdfs:label_en | Static Pressure Sensor 02
para:Static_Pressure_Sensor_Remote_01 | owl:Class | rdfs:subClassOf | brick:Supply_Air_Static_Pressure_Sensor |  | rdfs:label_en | Static Pressure Remote Sensor 01
para:Static_Pressure_Sensor_Remote_02 | owl:Class | rdfs:subClassOf | brick:Supply_Air_Static_Pressure_Sensor |  | rdfs:label_en | Static Pressure Remote Sensor 02
para:Stop_Command | owl:Class | rdfs:subClassOf | brick:Start_Stop_Command |  | rdfs:label_en | Stop Command
para:Stop_Time | owl:Class | rdfs:subClassOf | brick:Duration_Sensor |  | rdfs:label_en | Stop Time
para:Summary_Alarm | owl:Class | rdfs:subClassOf | brick:Alarm |  | rdfs:label_en | Summary Alarm
para:UnScheduled_Hrs_Duration | owl:Class | rdfs:subClassOf | brick:Duration_Sensor |  | rdfs:label_en | UnScheduled Hours of Operation
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri We need to add the building entity:SSC - rec:Building and assign the relationship rec:hasPart with the floors (rec:Level) like done in Dar Cairo because we are going to have other buildings this is an important identifier
Note on G2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G47: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G53: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G59: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G64: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G65: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G67: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G78: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G79: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G80: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G82: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G84: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G88: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G93: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G95: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G96: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G97: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G98: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G99: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G100: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G101: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G104: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G105: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G106: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G107: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G108: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G109: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G110: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G111: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G112: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G113: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G114: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G115: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G121: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G768: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G769: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G770: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G771: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G772: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G773: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G774: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G775: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G776: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G777: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G778: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G779: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G780: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G781: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G782: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G783: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G784: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G785: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G786: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G787: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G788: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G789: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G790: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G791: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G792: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G793: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G794: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G795: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G796: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G797: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G798: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G799: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G800: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G801: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G802: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G803: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G804: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G805: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G806: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G807: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on G808: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s not keep the “_” in the labels, it is to identify spaces between words in the ontology naming but the labels are going to show on the UI we can replace them with “ - “ or just a space
Note on I814: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I815: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I816: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I817: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I818: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I819: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I820: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I821: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I822: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I823: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I824: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I825: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I852: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I853: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I854: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I855: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I856: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I857: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I858: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I859: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I860: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I861: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I862: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I863: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I890: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I891: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I892: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I893: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I894: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I895: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I896: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I897: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I898: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I899: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I900: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I901: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I928: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I929: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I930: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I931: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I932: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I933: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I934: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I935: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I936: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I937: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I938: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I939: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I966: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I967: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I968: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I969: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I970: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I971: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I972: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I973: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I974: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I975: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I976: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I977: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I1004: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I1005: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I1006: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I1007: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I1008: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I1009: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I1010: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I1011: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I1012: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I1013: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I1014: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I1015: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I1042: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I1043: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I1044: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I1045: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I1046: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I1047: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I1048: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I1049: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I1050: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I1051: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I1052: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I1053: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I1080: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I1081: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I1082: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I1083: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I1084: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I1085: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I1086: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I1087: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I1088: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I1089: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I1090: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I1091: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I1118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I1119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I1120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I1121: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I1122: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I1123: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I1124: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I1125: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I1126: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I1127: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I1128: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I1129: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I1156: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I1157: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I1158: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I1159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I1160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I1161: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I1162: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I1163: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I1164: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I1165: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I1166: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I1167: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I1194: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I1195: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I1196: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I1197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I1198: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I1199: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I1200: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I1201: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I1202: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I1203: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I1204: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I1205: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I1232: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I1233: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I1234: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I1235: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I1236: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I1237: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I1238: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I1239: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I1240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I1241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I1242: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I1243: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I1270: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I1271: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I1272: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I1273: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I1274: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I1275: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I1276: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I1277: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I1278: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I1279: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I1280: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I1281: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on I1308: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri These point labels are going to be visible on the UI, they need to be clearly stated - here “Air Flow Loss Alarm’
Note on I1309: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri General Fault Alarm
Note on I1310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Clogged Filter Alarm
Note on I1311: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Cooling Mode Status
Note on I1312: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Dehumidification Status
Note on I1313: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Heating Mode Status
Note on I1314: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Fan Status
Note on I1315: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Humidification Status
Note on I1316: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Main Fan Overload
Note on I1317: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Unit Run Status
Note on I1318: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Operating Mode Status
Note on I1319: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Summary Alarm
Note on E2482: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2496: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2505: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2519: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2528: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2542: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2551: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2565: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2574: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2588: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2597: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2611: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2620: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2634: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2643: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2657: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2666: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2680: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2689: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2703: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2712: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2726: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2735: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2749: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2758: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2772: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2781: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2795: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2804: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2818: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2827: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2841: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2850: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2864: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2873: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2887: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2896: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2910: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2919: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2933: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2942: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2956: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2965: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B2979: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E2988: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3002: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3011: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3025: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3034: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3048: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3057: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3071: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3080: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3094: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3126: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3140: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3149: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3163: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3172: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3195: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3209: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3218: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3232: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3255: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3264: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3278: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3301: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3324: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3333: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3347: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3356: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3370: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3379: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3393: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3402: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3416: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3425: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3439: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3448: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3462: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3471: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3485: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3494: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3508: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3517: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3531: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3540: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3554: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3563: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3577: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3586: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3600: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3609: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3623: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3632: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3646: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3655: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3669: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3678: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3692: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3701: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3715: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3724: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3738: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3747: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3761: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3770: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3784: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3793: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3807: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3816: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3830: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3839: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3853: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3862: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3876: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3885: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3899: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3908: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3922: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3931: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3945: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3954: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3968: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E3977: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B3991: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4000: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4014: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4023: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4037: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4046: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4060: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4069: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4083: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4092: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4106: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4115: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4129: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4138: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4152: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4161: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4175: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4184: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4198: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4207: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4221: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4230: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4244: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4253: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4276: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4290: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4299: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4313: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4322: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4336: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4345: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4368: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4382: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4391: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4405: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4414: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4428: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4437: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4451: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4460: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4474: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4483: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4497: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4506: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4520: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4529: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4543: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4552: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4566: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4575: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4589: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4598: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4612: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4621: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4635: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4644: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4658: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4667: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4681: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4690: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4704: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4713: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4727: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4736: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4750: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4759: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4773: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4782: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4796: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4805: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4819: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4828: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4842: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4851: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4865: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4874: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4888: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4897: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4911: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4920: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4934: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on E4943: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on B4957: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri Let’s create a subclass under brick:Temperature_Setpoint and call it para:Effective_Temperature_Setpoint to segregate between both setpoints
Note on D4972: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Naresh Vedachalam @Ahmad Sharaf Al Masri This is a subclass of brick:HVAC_Equipment