## Legend
QNL datapoint ledger v2
Rebuilt from the reviewer decisions in column AF ("My suggestions") and validated against QF_SSC_Ontology_ver02.
New columns | Meaning
My suggestions (AF) | The reviewer decision, verbatim. Drives final_class.
final_class | The resolved class for the point, per the AF decision.
final_from | Which ladder rung the class came from (see below).
note | Deprecation replacement or reviewer note carried onto the row.
ssc_confirms | yes/no - does QF_SSC_Ontology_ver02 use this exact class?
ssc_uses | How many times SSC instantiates that class.
ssc_cross_check | Exact SSC match, or the nearest SSC point class by name overlap (Jaccard j).
final_from value | Meaning
Dar Cairo | Reused the Dar Cairo class (ladder step 1).
Brick 1.4 | Reviewer chose "Brick 1.4 exact" - the OK Brick candidate.
Brick 1.4 (reviewer) | Reviewer named the Brick class directly (e.g. Room_Air_Temperature_Sensor).
Dar Cairo (deprecated, kept) | CHW temp: kept the deprecated Dar Cairo class per reviewer; note names the entering/leaving replacement.
Previous project (SSC) | Reused a class SSC already coined (ladder step 3): Fail_Start/Fail_Stop_Alarm, Scheduled/UnScheduled_Hrs_Duration.
para (new) | Genuinely new para class to hand over: para:Trip_Alarm (subclass brick:Alarm, following SSC Fail_*_Alarm pattern).
Build status (updated)
All signatures placed | Per-unit membership now comes from Selected_PARA_OS_Data_Points_v4.0.xlsx, so both universal and partial-coverage signatures are written. 2,215 points on AHU/VAV/CAV/FCU.
Timeseries ids | Filled from the IO list SourceTag - no placeholders remain.
Units | Taken from the IO list, not the Selected sheet: 30 Selected rows have humidity/temperature units transposed.
Scope | AHU, VAV, CAV, FCU only. CCU/EF/DX/HEX/KEF/SEF/TEF/GEN are out of scope - no equipment in the register.

## Ledger
family | kind | part | point | units | of | example_tag | historian_description | unit_of_measure | signal | match_phrase | match_phrase_source | point_kind | part_device | part_class_darcairo | part_class_score | part_class_from | part_status | darcairo_class | darcairo_score | darcairo_uses | darcairo_evidence | runner_up | runner_up_score | darcairo_class_in_brick | brick_candidate | brick_candidate_status | brick_candidate_score | proposed_class | proposed_from | status | My suggestions | final_class | final_from | note | ssc_confirms | ssc_uses | ssc_cross_check
AHUB | point |  | EnableDisableCmd | 15 | 15 | QNL_AHUB001.EnableDisableCmd | Enable/Disable Command (1=Enabled, 0=Disabled) |  | discrete | Enable/Disable Command (1=Enabled, 0=Disabled) | historian description | Command | [5 empty] | brick:On_Off_Command | 0.14 | 68 | class name | brick:On_Command | 0.14 | OK | brick:Disable_Command | OK | 0.29 |  |  | needs-you: no match - propose a para: class | Dar Cairo | brick:On_Off_Command | Dar Cairo |  | no |  | nearest SSC: brick:System_Enable_Command (j=0.29)
AHUB | point |  | RtnHumiditySP | 15 | 15 | QNL_AHUB001.RtnHumiditySP | QNL AHU-B0001 Basement Level AHU Plant Room B04 | %rH | analog | return air humidity setpoint | expanded from the tag | Setpoint | [5 empty] | brick:Supply_Air_Static_Pressure_Setpoint | 0.29 | 52 | class name | para:Winter_Supply_Air_Temperature_Setpoint | 0.29 | OK | brick:Return_Air_Humidity_Setpoint | OK | 1.00 | brick:Return_Air_Humidity_Setpoint | Brick 1.4 exact | auto | Brick 1.4 exact | brick:Return_Air_Humidity_Setpoint | Brick 1.4 |  | no |  | nearest SSC: brick:Return_Air_Humidity_Sensor (j=0.75)
AHUB | point | CHWRtnTemp | PV | 15 | 15 | QNL_AHUB001_CHWRtnTemp.PV | Process Value | °C | analog | chilled water return temperature | expanded from the tag | Sensor | [5 empty] | brick:Chilled_Water_Return_Temperature_Sensor | 0.80 | 5 | class name | brick:Entering_Chilled_Water_Temperature_Sensor | 0.50 | DEPRECATED | brick:Leaving_Chilled_Water_Temperature_Sensor | OK | 1.00 | brick:Leaving_Chilled_Water_Temperature_Sensor | Brick 1.4 migration: deprecated CHW supply/return -> entering/leaving (AHU-coil frame; supply=entering, return=leaving) | auto | Dar Cairo even if Deprecated. Just add a not at the end of the row that there is a new one and name it | brick:Chilled_Water_Return_Temperature_Sensor | Dar Cairo (deprecated, kept) | DEPRECATED in Brick 1.4. Current replacement: brick:Leaving_Chilled_Water_Temperature_Sensor (AHU-coil frame: return = leaving). Kept Dar Cairo class as the established join key per reviewer. | no |  | nearest SSC: brick:Return_Air_Temperature_Sensor (j=0.4)
AHUB | point | CHWSupTemp | PV | 15 | 15 | QNL_AHUB001_CHWSupTemp.PV | Process Value | °C | analog | chilled water supply temperature | expanded from the tag | Sensor | [5 empty] | brick:Chilled_Water_Supply_Temperature_Sensor | 0.80 | 4 | class name | brick:Chilled_Water_Return_Temperature_Sensor | 0.50 | DEPRECATED | brick:Entering_Chilled_Water_Temperature_Sensor | OK | 1.00 | brick:Entering_Chilled_Water_Temperature_Sensor | Brick 1.4 migration: deprecated CHW supply/return -> entering/leaving (AHU-coil frame; supply=entering, return=leaving) | auto | Dar Cairo even if Deprecated. Just add a not at the end of the row that there is a new one and name it | brick:Chilled_Water_Supply_Temperature_Sensor | Dar Cairo (deprecated, kept) | DEPRECATED in Brick 1.4. Current replacement: brick:Entering_Chilled_Water_Temperature_Sensor (AHU-coil frame: supply = entering). Kept Dar Cairo class as the established join key per reviewer. | no |  | nearest SSC: brick:Supply_Air_Temperature_Sensor (j=0.4)
AHUB | part+point | CoolVlv | PosFbk | 15 | 15 | QNL_AHUB001_CoolVlv.PosFbk | QNL AHU-B0001 Cooling Valve TV-2000A | % | analog | position feedback | expanded from the tag | Sensor | valve | brick:Cooling_Valve | 1.00 | Dar Cairo | ok | brick:Valve_Position_Sensor | 0.40 | 24 | class name [matched on part+point] | brick:Valve_Position_Command | 0.12 | OK | brick:Valve_Position_Sensor | OK | 0.40 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Valve_Position_Sensor | Dar Cairo |  | yes | 133 | exact: brick:Valve_Position_Sensor
AHUB | point | FrshAirTemp | PV | 15 | 15 | QNL_AHUB001_FrshAirTemp.PV | Process Value | °C | analog | fresh air temperature | expanded from the tag | Sensor | [5 empty] | brick:Outside_Air_Temperature_Sensor | 0.75 | 3 | class name | brick:Air_Temperature_Sensor | 0.50 | OK | brick:Outside_Air_Temperature_Sensor | OK | 1.00 | brick:Outside_Air_Temperature_Sensor | Dar Cairo | auto | Dar Cairo | brick:Outside_Air_Temperature_Sensor | Dar Cairo |  | yes | 5 | exact: brick:Outside_Air_Temperature_Sensor
AHUB | point | MixAirTemp | PV | 15 | 15 | QNL_AHUB001_MixAirTemp.PV | Process Value | °C | analog | mixed air temperature | expanded from the tag | Sensor | [5 empty] | brick:Air_Temperature_Sensor | 0.50 | 1 | class name | brick:Return_Air_Temperature_Sensor | 0.40 | OK | brick:Mixed_Air_Temperature_Sensor | OK | 1.00 | brick:Mixed_Air_Temperature_Sensor | Brick 1.4 exact | auto | Brick 1.4 exact | brick:Mixed_Air_Temperature_Sensor | Brick 1.4 |  | yes | 5 | exact: brick:Mixed_Air_Temperature_Sensor
AHUB | point | RtnAirDuctPrs | PV | 15 | 15 | QNL_AHUB001_RtnAirDuctPrs.PV | Process Value | Pa | analog | return air duct pressure | expanded from the tag | Sensor | [5 empty] | brick:Return_Air_Temperature_Sensor | 0.33 | 24 | class name | brick:Return_Air_Humidity_Sensor | 0.33 | OK | brick:Return_Air_Differential_Pressure_Sensor | OK | 0.50 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Return_Air_Differential_Pressure_Sensor | Brick 1.4 |  | no |  | nearest SSC: para:Return_Air_Static_Pressure_Sensor (j=0.6)
AHUB | point | RtnAirHumd | PV | 15 | 15 | QNL_AHUB001_RtnAirHumd.PV | Process Value | %rH | analog | return air humidity | expanded from the tag | Sensor | [5 empty] | brick:Return_Air_Humidity_Sensor | 0.75 | 20 | class name | brick:Return_Air_Temperature_Sensor | 0.40 | OK | brick:Return_Air_Humidity_Sensor | OK | 1.00 | brick:Return_Air_Humidity_Sensor | Dar Cairo | auto | Dar Cairo | brick:Return_Air_Humidity_Sensor | Dar Cairo |  | yes | 5 | exact: brick:Return_Air_Humidity_Sensor
AHUB | point | RtnAirTemp | PV | 15 | 15 | QNL_AHUB001_RtnAirTemp.PV | Process Value | °C | analog | return air temperature | expanded from the tag | Sensor | [5 empty] | brick:Return_Air_Temperature_Sensor | 0.75 | 24 | class name | brick:Air_Temperature_Sensor | 0.50 | OK | brick:Return_Air_Temperature_Sensor | OK | 1.00 | brick:Return_Air_Temperature_Sensor | Dar Cairo | auto | Dar Cairo | brick:Return_Air_Temperature_Sensor | Dar Cairo |  | yes | 5 | exact: brick:Return_Air_Temperature_Sensor
AHUB | point | SupAirDuctPrs | PV | 15 | 15 | QNL_AHUB001_SupAirDuctPrs.PV | Process Value | Pa | analog | supply air duct pressure | expanded from the tag | Sensor | [5 empty] | brick:Supply_Air_Static_Pressure_Sensor | 0.50 | 52 | class name | brick:Supply_Air_Temperature_Sensor | 0.33 | OK | brick:Supply_Air_Differential_Pressure_Sensor | OK | 0.50 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Supply_Air_Differential_Pressure_Sensor | Brick 1.4 |  | no |  | nearest SSC: brick:Supply_Air_Flow_Sensor (j=0.4)
AHUB | point | SupAirFlow | PV | 15 | 15 | QNL_AHUB001_SupAirFlow.PV | Process Value | m/s | analog | supply air flow | expanded from the tag | Sensor | [5 empty] | brick:Supply_Air_Flow_Sensor | 0.75 | 18 | class name | brick:Air_Flow_Sensor | 0.50 | OK | brick:Supply_Air_Flow_Sensor | OK | 1.00 | brick:Supply_Air_Flow_Sensor | Dar Cairo | auto | Dar Cairo | brick:Supply_Air_Flow_Sensor | Dar Cairo |  | yes | 113 | exact: brick:Supply_Air_Flow_Sensor
AHUB | point | SupAirHumd | PV | 15 | 15 | QNL_AHUB001_SupAirHumd.PV | Process Value | %rH | analog | supply air humidity | expanded from the tag | Sensor | [5 empty] | brick:Supply_Air_Humidity_Sensor | 0.75 | 3 | class name | brick:Supply_Air_Temperature_Sensor | 0.40 | OK | brick:Supply_Air_Humidity_Sensor | OK | 1.00 | brick:Supply_Air_Humidity_Sensor | Dar Cairo | auto | Dar Cairo | brick:Supply_Air_Humidity_Sensor | Dar Cairo |  | yes | 5 | exact: brick:Supply_Air_Humidity_Sensor
AHUB | point | SupAirTemp | PV | 15 | 15 | QNL_AHUB001_SupAirTemp.PV | Process Value | °C | analog | supply air temperature | expanded from the tag | Sensor | [5 empty] | brick:Supply_Air_Temperature_Sensor | 0.75 | 20 | class name | brick:Preheat_Supply_Air_Temperature_Sensor | 0.60 | OK | brick:Supply_Air_Temperature_Sensor | OK | 1.00 | brick:Supply_Air_Temperature_Sensor | Dar Cairo | auto | Dar Cairo | brick:Supply_Air_Temperature_Sensor | Dar Cairo |  | yes | 5 | exact: brick:Supply_Air_Temperature_Sensor
AHUB | part+point | SupFan | AutoManCmd | 14 | 15 | QNL_AHUB002_SupFan.AutoManCmd | Auto/Manual Command |  | discrete | Auto/Manual Command | historian description | Command | fan | brick:Supply_Fan | 1.00 | Dar Cairo | ok | brick:On_Off_Command | 0.33 | 68 | class name | brick:On_Command | 0.33 | OK | brick:Fan_Command | OK | 0.40 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:On_Off_Command | Dar Cairo |  | no |  | nearest SSC: brick:Manual_Auto_Status (j=0.5)
AHUB | part+point | SupFan | FTSP | 14 | 15 | QNL_AHUB002_SupFan.FTSP | Fail to Stop Alarm |  | discrete | Fail to Stop Alarm | historian description | Alarm | fan | brick:Supply_Fan | 1.00 | Dar Cairo | ok | brick:Alarm | 0.25 | 33 | class name | brick:Fire_Alarm | 0.20 | OK | brick:Supply_Air_Temperature_Alarm | OK | 0.25 |  |  | needs-you: confirm the Dar Cairo candidate | propose a para: class to identify multiple alarms from each other using the point names | para:Fail_Stop_Alarm | Previous project (SSC) | Reuses SSC precedent para:Fail_Stop_Alarm (5 uses). Alarm distinguished by point name. | yes | 5 | exact: para:Fail_Stop_Alarm
AHUB | part+point | SupFan | FTST | 14 | 15 | QNL_AHUB002_SupFan.FTST | Fail to Start Alarm |  | discrete | Fail to Start Alarm | historian description | Alarm | fan | brick:Supply_Fan | 1.00 | Dar Cairo | ok | brick:Alarm | 0.25 | 33 | class name | brick:Fire_Alarm | 0.20 | OK | brick:Supply_Air_Temperature_Alarm | OK | 0.25 |  |  | needs-you: confirm the Dar Cairo candidate | propose a para: class to identify multiple alarms from each other using the point names | para:Fail_Start_Alarm | Previous project (SSC) | Reuses SSC precedent para:Fail_Start_Alarm (5 uses). Alarm distinguished by point name. | yes | 5 | exact: para:Fail_Start_Alarm
AHUB | part+point | SupFan | SpeedFbk | 14 | 15 | QNL_AHUB002_SupFan.SpeedFbk | Speed Feedback | % | analog | Speed Feedback | historian description | Sensor | fan | brick:Supply_Fan | 1.00 | Dar Cairo | ok | para:Over_Speed_Sensor | 0.25 | 1 | class name | para:Engine_Speed_Sensor | 0.25 | not in Brick 1.4 | brick:Speed_Sensor | OK | 0.20 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Speed_Sensor | Brick 1.4 |  | yes | 14 | exact: brick:Speed_Sensor
AHUB | part+point | SupFan | TripAlm | 14 | 15 | QNL_AHUB002_SupFan.TripAlm | Trip Alarm |  | discrete | Trip Alarm | historian description | Alarm | fan | brick:Supply_Fan | 1.00 | Dar Cairo | ok | brick:Alarm | 0.50 | 33 | class name | brick:Fire_Alarm | 0.33 | OK | brick:Supply_Air_Temperature_Alarm | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | propose a para: class to identify multiple alarms from each other using the point names | para:Trip_Alarm | para (new) | New para subclass of brick:Alarm, following the SSC para:Fail_Start_Alarm / para:Fail_Stop_Alarm naming pattern. SSC currently types TripAlm generically as brick:Alarm; this splits it out by point name per reviewer. | no |  | nearest SSC: brick:Alarm (j=0.5)
AHUB | part+point | SupFan | kW | 14 | 15 | QNL_AHUB002_SupFan.kW | Power | kW | analog | electric power | expanded from the tag | Sensor | fan | brick:Supply_Fan | 1.00 | Dar Cairo | ok | brick:Electric_Power_Sensor | 0.67 | 713 | class name | brick:Thermal_Power_Sensor | 0.25 | OK | brick:Electric_Power_Sensor | OK | 0.40 | brick:Electric_Power_Sensor | Dar Cairo | auto | Dar Cairo | brick:Electric_Power_Sensor | Dar Cairo |  | yes | 21 | exact: brick:Electric_Power_Sensor
AHUB | part+point | SupFan | kWH | 14 | 15 | QNL_AHUB002_SupFan.kWH | Energy | kWh | analog | electrical energy | expanded from the tag | Sensor | fan | brick:Supply_Fan | 1.00 | Dar Cairo | ok | brick:Electrical_Energy_Usage_Sensor | 0.50 | 819 | class name | brick:Energy_Sensor | 0.33 | OK | brick:Electrical_Energy_Usage_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Electrical_Energy_Usage_Sensor | Dar Cairo |  | yes | 21 | exact: brick:Electrical_Energy_Usage_Sensor
AHUB | point | AvgSpcHumd | PV | 9 | 15 | QNL_AHUB001_AvgSpcHumd.PV | Process Value | %rH | analog | average space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.20 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.17 | OK | brick:Humidity_Sensor | OK | 0.25 |  |  | needs-you: no match - propose a para: class | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | AvgSpcTemp | PV | 9 | 15 | QNL_AHUB001_AvgSpcTemp.PV | Process Value | °C | analog | average space temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.25 | 110 | class name | para:UPS_Temperature_Sensor | 0.20 | OK | brick:Average_Zone_Air_Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Average_Zone_Air_Temperature_Sensor | Brick 1.4 |  | no |  | nearest SSC: brick:Temperature_Sensor (j=0.33)
AHUB | part+point | IntrnlEADmpr | PositionCtrl | 7 | 15 | QNL_AHUB001_IntrnlEADmpr.PositionCtrl | QNL AHU-B0001 Internal Exhaust Air Damper MD-2000G | % | analog | position command | expanded from the tag | Command | damper | brick:Exhaust_Damper | 0.50 | Dar Cairo | needs-you: weak part match | brick:Damper_Position_Command | 0.67 | 29 | class name | brick:On_Off_Command | 0.50 | OK | brick:Damper_Position_Command | OK | 0.50 | brick:Damper_Position_Command | Dar Cairo | auto | Dar Cairo | brick:Damper_Position_Command | Dar Cairo |  | no |  | nearest SSC: brick:Valve_Position_Command (j=0.67)
AHUB | part+point | IntrnlFADmpr | PositionCtrl | 7 | 15 | QNL_AHUB001_IntrnlFADmpr.PositionCtrl | QNL AHU-B0001 Internal Fresh Air Damper MD-2000C | % | analog | position command | expanded from the tag | Command | damper | brick:Outside_Damper | 0.50 | Dar Cairo | needs-you: weak part match | brick:Damper_Position_Command | 0.67 | 29 | class name | brick:On_Off_Command | 0.50 | OK | brick:Damper_Position_Command | OK | 0.50 | brick:Damper_Position_Command | Dar Cairo | auto | Dar Cairo, Outside damper can be considered fresh air damper | brick:Damper_Position_Command | Dar Cairo | Outside damper can be considered fresh air damper | no |  | nearest SSC: brick:Valve_Position_Command (j=0.67)
AHUB | point | RtnAirFlow | PV | 7 | 15 | QNL_AHUB001_RtnAirFlow.PV | Process Value | m/s | analog | return air flow | expanded from the tag | Sensor | [5 empty] | brick:Return_Air_Flow_Sensor | 0.75 | 15 | class name | brick:Air_Flow_Sensor | 0.50 | OK | brick:Return_Air_Flow_Sensor | OK | 1.00 | brick:Return_Air_Flow_Sensor | Dar Cairo | auto | Dar Cairo | brick:Return_Air_Flow_Sensor | Dar Cairo |  | yes | 5 | exact: brick:Return_Air_Flow_Sensor
AHUB | part+point | IntrnlEADmpr | PositionFbk | 6 | 15 | QNL_AHUB001_IntrnlEADmpr.PositionFbk | QNL AHU-B0001 Internal Exhaust Air Damper MD-2000G | % | analog | position feedback | expanded from the tag | Sensor | damper | brick:Exhaust_Damper | 0.50 | Dar Cairo | needs-you: weak part match | brick:Damper_Position_Sensor | 0.29 | 74 | class name [matched on part+point] | brick:Exhaust_Air_Temperature_Sensor | 0.25 | OK | brick:Damper_Position_Sensor | OK | 0.29 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Damper_Position_Sensor | Dar Cairo |  | no |  | nearest SSC: brick:Valve_Position_Sensor (j=0.33)
AHUB | part+point | IntrnlFADmpr | PositionFbk | 6 | 15 | QNL_AHUB001_IntrnlFADmpr.PositionFbk | QNL AHU-B0001 Internal Fresh Air Damper MD-2000C | % | analog | position feedback | expanded from the tag | Sensor | damper | brick:Outside_Damper | 0.50 | Dar Cairo | needs-you: weak part match | brick:Damper_Position_Sensor | 0.29 | 74 | class name [matched on part+point] | brick:Outside_Air_Flow_Sensor | 0.25 | OK | brick:Damper_Position_Sensor | OK | 0.29 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo, Outside damper can be considered fresh air damper | brick:Damper_Position_Sensor | Dar Cairo | Outside damper can be considered fresh air damper | no |  | nearest SSC: brick:Valve_Position_Sensor (j=0.33)
AHUB | part+point | RtnFan | AutoManCmd | 6 | 15 | QNL_AHUB010_RtnFan.AutoManCmd | Auto/Manual Command |  | discrete | Auto/Manual Command | historian description | Command | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | brick:On_Off_Command | 0.33 | 68 | class name | brick:On_Command | 0.33 | OK | brick:Fan_Command | OK | 0.40 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:On_Off_Command | Dar Cairo |  | no |  | nearest SSC: brick:Manual_Auto_Status (j=0.5)
AHUB | part+point | RtnFan | SpeedFbk | 6 | 15 | QNL_AHUB010_RtnFan.SpeedFbk | Speed Feedback | % | analog | Speed Feedback | historian description | Sensor | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | para:Over_Speed_Sensor | 0.25 | 1 | class name | para:Engine_Speed_Sensor | 0.25 | not in Brick 1.4 | brick:Speed_Sensor | OK | 0.20 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Speed_Sensor | Brick 1.4 |  | yes | 14 | exact: brick:Speed_Sensor
AHUB | part+point | RtnFan | TripAlm | 6 | 15 | QNL_AHUB010_RtnFan.TripAlm | Trip Alarm |  | discrete | Trip Alarm | historian description | Alarm | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | brick:Alarm | 0.50 | 33 | class name | brick:Fire_Alarm | 0.33 | OK | brick:Return_Air_Temperature_Alarm | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | propose a para: class to identify multiple alarms from each other using the point names | para:Trip_Alarm | para (new) | New para subclass of brick:Alarm, following the SSC para:Fail_Start_Alarm / para:Fail_Stop_Alarm naming pattern. SSC currently types TripAlm generically as brick:Alarm; this splits it out by point name per reviewer. | no |  | nearest SSC: brick:Alarm (j=0.5)
AHUB | part+point | RtnFan | kW | 6 | 15 | QNL_AHUB010_RtnFan.kW | Power | kW | analog | electric power | expanded from the tag | Sensor | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | brick:Electric_Power_Sensor | 0.67 | 713 | class name | brick:Thermal_Power_Sensor | 0.25 | OK | brick:Electric_Power_Sensor | OK | 0.40 | brick:Electric_Power_Sensor | Dar Cairo | auto | Dar Cairo | brick:Electric_Power_Sensor | Dar Cairo |  | yes | 21 | exact: brick:Electric_Power_Sensor
AHUB | part+point | RtnFan | kWH | 6 | 15 | QNL_AHUB010_RtnFan.kWH | Energy | kWh | analog | electrical energy | expanded from the tag | Sensor | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | brick:Electrical_Energy_Usage_Sensor | 0.50 | 819 | class name | brick:Energy_Sensor | 0.33 | OK | brick:Electrical_Energy_Usage_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Electrical_Energy_Usage_Sensor | Dar Cairo |  | yes | 21 | exact: brick:Electrical_Energy_Usage_Sensor
AHUB | point | SpcHumd01 | PV | 6 | 15 | QNL_AHUB002_SpcHumd01.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | SpcHumd02 | PV | 6 | 15 | QNL_AHUB002_SpcHumd02.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | SpcHumd03 | PV | 6 | 15 | QNL_AHUB002_SpcHumd03.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | SpcHumd04 | PV | 6 | 15 | QNL_AHUB002_SpcHumd04.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | SpcHumd05 | PV | 5 | 15 | QNL_AHUB002_SpcHumd05.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | SpcTemp01 | PV | 5 | 15 | QNL_AHUB002_SpcTemp01.PV | Process Value | °C | analog | space temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | use brick:Room_Air_Temperature_Sensor | brick:Room_Air_Temperature_Sensor | Brick 1.4 (reviewer) |  | yes | 11 | exact: brick:Room_Air_Temperature_Sensor
AHUB | point | SpcTemp02 | PV | 5 | 15 | QNL_AHUB002_SpcTemp02.PV | Process Value | °C | analog | space temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | use brick:Room_Air_Temperature_Sensor | brick:Room_Air_Temperature_Sensor | Brick 1.4 (reviewer) |  | yes | 11 | exact: brick:Room_Air_Temperature_Sensor
AHUB | point | SpcTemp03 | PV | 5 | 15 | QNL_AHUB002_SpcTemp03.PV | Process Value | °C | analog | space temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | use brick:Room_Air_Temperature_Sensor | brick:Room_Air_Temperature_Sensor | Brick 1.4 (reviewer) |  | yes | 11 | exact: brick:Room_Air_Temperature_Sensor
AHUB | point | SpcTemp04 | PV | 5 | 15 | QNL_AHUB002_SpcTemp04.PV | Process Value | °C | analog | space temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | use brick:Room_Air_Temperature_Sensor | brick:Room_Air_Temperature_Sensor | Brick 1.4 (reviewer) |  | yes | 11 | exact: brick:Room_Air_Temperature_Sensor
AHUB | point | DuctTemp01 | PV | 4 | 15 | QNL_AHUB001_DuctTemp01.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | DuctTemp02 | PV | 4 | 15 | QNL_AHUB001_DuctTemp02.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | SpcHumd06 | PV | 4 | 15 | QNL_AHUB002_SpcHumd06.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | DuctHumd01 | PV | 3 | 15 | QNL_AHUB001_DuctHumd01.PV | Process Value | %rH | analog | duct humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | DuctHumd02 | PV | 3 | 15 | QNL_AHUB001_DuctHumd02.PV | Process Value | %rH | analog | duct humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | DuctTemp03 | PV | 3 | 15 | QNL_AHUB001_DuctTemp03.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | DuctTemp04 | PV | 3 | 15 | QNL_AHUB001_DuctTemp04.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | SpcHumd07 | PV | 3 | 15 | QNL_AHUB002_SpcHumd07.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | SpcTemp05 | PV | 3 | 15 | QNL_AHUB002_SpcTemp05.PV | Process Value | °C | analog | space temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | use brick:Room_Air_Temperature_Sensor | brick:Room_Air_Temperature_Sensor | Brick 1.4 (reviewer) |  | yes | 11 | exact: brick:Room_Air_Temperature_Sensor
AHUB | point | DuctHumd03 | PV | 2 | 15 | QNL_AHUB001_DuctHumd03.PV | Process Value | %rH | analog | duct humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | DuctHumd04 | PV | 2 | 15 | QNL_AHUB001_DuctHumd04.PV | Process Value | %rH | analog | duct humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | DuctTemp05 | PV | 2 | 15 | QNL_AHUB001_DuctTemp05.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | DuctTemp06 | PV | 2 | 15 | QNL_AHUB001_DuctTemp06.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | DuctTemp07 | PV | 2 | 15 | QNL_AHUB001_DuctTemp07.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | SpcTemp06 | PV | 2 | 15 | QNL_AHUB002_SpcTemp06.PV | Process Value | °C | analog | space temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | use brick:Room_Air_Temperature_Sensor | brick:Room_Air_Temperature_Sensor | Brick 1.4 (reviewer) |  | yes | 11 | exact: brick:Room_Air_Temperature_Sensor
AHUB | point | DuctHumd | PV | 1 | 15 | QNL_AHUB010_DuctHumd.PV | Process Value | %rH | analog | duct humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | DuctHumd05 | PV | 1 | 15 | QNL_AHUB001_DuctHumd05.PV | Process Value | %rH | analog | duct humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | DuctHumd06 | PV | 1 | 15 | QNL_AHUB001_DuctHumd06.PV | Process Value | %rH | analog | duct humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | DuctHumd07 | PV | 1 | 15 | QNL_AHUB001_DuctHumd07.PV | Process Value | %rH | analog | duct humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | DuctTemp | PV | 1 | 15 | QNL_AHUB010_DuctTemp.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | DuctTemp08 | PV | 1 | 15 | QNL_AHUB006_DuctTemp08.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | DuctTemp09 | PV | 1 | 15 | QNL_AHUB006_DuctTemp09.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | DuctTemp10 | PV | 1 | 15 | QNL_AHUB006_DuctTemp10.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | DuctTemp11 | PV | 1 | 15 | QNL_AHUB006_DuctTemp11.PV | Process Value | °C | analog | duct temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Temperature_Sensor | Dar Cairo |  | yes | 137 | exact: brick:Temperature_Sensor
AHUB | point | FACHWRtnTemp | PV | 1 | 15 | QNL_AHUB001_FACHWRtnTemp.PV | Process Value | °C | analog | fresh air chilled water return temperature | expanded from the tag | Sensor | [5 empty] | brick:Chilled_Water_Return_Temperature_Sensor | 0.57 | 5 | class name | brick:Return_Air_Temperature_Sensor | 0.43 | DEPRECATED | brick:Leaving_Chilled_Water_Temperature_Sensor | OK | 1.00 | brick:Leaving_Chilled_Water_Temperature_Sensor | Brick 1.4 migration: deprecated CHW supply/return -> entering/leaving (AHU-coil frame; supply=entering, return=leaving) | auto | Dar Cairo even if Deprecated. Just add a not at the end of the row that there is a new one and name it | brick:Chilled_Water_Return_Temperature_Sensor | Dar Cairo (deprecated, kept) | DEPRECATED in Brick 1.4. Current replacement: brick:Leaving_Chilled_Water_Temperature_Sensor (AHU-coil frame: return = leaving). Kept Dar Cairo class as the established join key per reviewer. | no |  | nearest SSC: brick:Return_Air_Temperature_Sensor (j=0.5)
AHUB | point | FACHWSupTemp | PV | 1 | 15 | QNL_AHUB001_FACHWSupTemp.PV | Process Value | °C | analog | fresh air chilled water supply temperature | expanded from the tag | Sensor | [5 empty] | brick:Chilled_Water_Supply_Temperature_Sensor | 0.57 | 4 | class name | brick:Supply_Air_Temperature_Sensor | 0.43 | DEPRECATED | brick:Entering_Chilled_Water_Temperature_Sensor | OK | 1.00 | brick:Entering_Chilled_Water_Temperature_Sensor | Brick 1.4 migration: deprecated CHW supply/return -> entering/leaving (AHU-coil frame; supply=entering, return=leaving) | auto | Dar Cairo even if Deprecated. Just add a not at the end of the row that there is a new one and name it | brick:Chilled_Water_Supply_Temperature_Sensor | Dar Cairo (deprecated, kept) | DEPRECATED in Brick 1.4. Current replacement: brick:Entering_Chilled_Water_Temperature_Sensor (AHU-coil frame: supply = entering). Kept Dar Cairo class as the established join key per reviewer. | no |  | nearest SSC: brick:Supply_Air_Temperature_Sensor (j=0.5)
AHUB | part+point | RtnFan1 | AutoManCmd | 1 | 15 | QNL_AHUB001_RtnFan1.AutoManCmd | Auto/Manual Command |  | discrete | Auto/Manual Command | historian description | Command | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | brick:On_Off_Command | 0.33 | 68 | class name | brick:On_Command | 0.33 | OK | brick:Fan_Command | OK | 0.40 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:On_Off_Command | Dar Cairo |  | no |  | nearest SSC: brick:Manual_Auto_Status (j=0.5)
AHUB | part+point | RtnFan1 | RunSts | 1 | 15 | QNL_AHUB001_RtnFan1.RunSts | Running Status |  | discrete | Running Status | historian description | Status | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | brick:On_Off_Status | 0.50 | 219 | class name | brick:Status | 0.50 | OK | brick:Fan_On_Off_Status | OK | 0.50 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:On_Off_Status | Dar Cairo |  | yes | 134 | exact: brick:On_Off_Status
AHUB | part+point | RtnFan1 | SpeedFbk | 1 | 15 | QNL_AHUB001_RtnFan1.SpeedFbk | Speed Feedback | % | analog | Speed Feedback | historian description | Sensor | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | para:Over_Speed_Sensor | 0.25 | 1 | class name | para:Engine_Speed_Sensor | 0.25 | not in Brick 1.4 | brick:Speed_Sensor | OK | 0.20 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Speed_Sensor | Brick 1.4 |  | yes | 14 | exact: brick:Speed_Sensor
AHUB | part+point | RtnFan1 | TripAlm | 1 | 15 | QNL_AHUB001_RtnFan1.TripAlm | Trip Alarm |  | discrete | Trip Alarm | historian description | Alarm | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | brick:Alarm | 0.50 | 33 | class name | brick:Fire_Alarm | 0.33 | OK | brick:Return_Air_Temperature_Alarm | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | propose a para: class to identify multiple alarms from each other using the point names | para:Trip_Alarm | para (new) | New para subclass of brick:Alarm, following the SSC para:Fail_Start_Alarm / para:Fail_Stop_Alarm naming pattern. SSC currently types TripAlm generically as brick:Alarm; this splits it out by point name per reviewer. | no |  | nearest SSC: brick:Alarm (j=0.5)
AHUB | part+point | RtnFan1 | kW | 1 | 15 | QNL_AHUB001_RtnFan1.kW | Power | kW | analog | electric power | expanded from the tag | Sensor | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | brick:Electric_Power_Sensor | 0.67 | 713 | class name | brick:Thermal_Power_Sensor | 0.25 | OK | brick:Electric_Power_Sensor | OK | 0.40 | brick:Electric_Power_Sensor | Dar Cairo | auto | Dar Cairo | brick:Electric_Power_Sensor | Dar Cairo |  | yes | 21 | exact: brick:Electric_Power_Sensor
AHUB | part+point | RtnFan2 | AutoManCmd | 1 | 15 | QNL_AHUB001_RtnFan2.AutoManCmd | Auto/Manual Command |  | discrete | Auto/Manual Command | historian description | Command | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | brick:On_Off_Command | 0.33 | 68 | class name | brick:On_Command | 0.33 | OK | brick:Fan_Command | OK | 0.40 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:On_Off_Command | Dar Cairo |  | no |  | nearest SSC: brick:Manual_Auto_Status (j=0.5)
AHUB | part+point | RtnFan2 | SpeedFbk | 1 | 15 | QNL_AHUB001_RtnFan2.SpeedFbk | Speed Feedback | % | analog | Speed Feedback | historian description | Sensor | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | para:Over_Speed_Sensor | 0.25 | 1 | class name | para:Engine_Speed_Sensor | 0.25 | not in Brick 1.4 | brick:Speed_Sensor | OK | 0.20 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Speed_Sensor | Brick 1.4 |  | yes | 14 | exact: brick:Speed_Sensor
AHUB | part+point | RtnFan2 | TripAlm | 1 | 15 | QNL_AHUB001_RtnFan2.TripAlm | Trip Alarm |  | discrete | Trip Alarm | historian description | Alarm | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | brick:Alarm | 0.50 | 33 | class name | brick:Fire_Alarm | 0.33 | OK | brick:Return_Air_Temperature_Alarm | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | propose a para: class to identify multiple alarms from each other using the point names | para:Trip_Alarm | para (new) | New para subclass of brick:Alarm, following the SSC para:Fail_Start_Alarm / para:Fail_Stop_Alarm naming pattern. SSC currently types TripAlm generically as brick:Alarm; this splits it out by point name per reviewer. | no |  | nearest SSC: brick:Alarm (j=0.5)
AHUB | part+point | RtnFan2 | kW | 1 | 15 | QNL_AHUB001_RtnFan2.kW | Power | kW | analog | electric power | expanded from the tag | Sensor | fan | brick:Return_Fan | 1.00 | Brick 1.4 exact | ok | brick:Electric_Power_Sensor | 0.67 | 713 | class name | brick:Thermal_Power_Sensor | 0.25 | OK | brick:Electric_Power_Sensor | OK | 0.40 | brick:Electric_Power_Sensor | Dar Cairo | auto | Dar Cairo | brick:Electric_Power_Sensor | Dar Cairo |  | yes | 21 | exact: brick:Electric_Power_Sensor
AHUB | point | SpcHumd | PV | 1 | 15 | QNL_AHUB007_SpcHumd.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | SpcHumd08 | PV | 1 | 15 | QNL_AHUB006_SpcHumd08.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | SpcHumd09 | PV | 1 | 15 | QNL_AHUB006_SpcHumd09.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | SpcHumd10 | PV | 1 | 15 | QNL_AHUB006_SpcHumd10.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | SpcHumd11 | PV | 1 | 15 | QNL_AHUB006_SpcHumd11.PV | Process Value | %rH | analog | space humidity | expanded from the tag | Sensor | [5 empty] | brick:Relative_Humidity_Sensor | 0.25 | 110 | class name | brick:Return_Air_Humidity_Sensor | 0.20 | OK | brick:Humidity_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Relative_Humidity_Sensor | Dar Cairo |  | yes | 18 | exact: brick:Relative_Humidity_Sensor
AHUB | point | SpcTemp | PV | 1 | 15 | QNL_AHUB007_SpcTemp.PV | Process Value | °C | analog | space temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | use brick:Room_Air_Temperature_Sensor | brick:Room_Air_Temperature_Sensor | Brick 1.4 (reviewer) |  | yes | 11 | exact: brick:Room_Air_Temperature_Sensor
AHUB | point | SpcTemp07 | PV | 1 | 15 | QNL_AHUB002_SpcTemp07.PV | Process Value | °C | analog | space temperature | expanded from the tag | Sensor | [5 empty] | brick:Temperature_Sensor | 0.33 | 110 | class name | para:UPS_Temperature_Sensor | 0.25 | OK | brick:Temperature_Sensor | OK | 0.33 |  |  | needs-you: confirm the Dar Cairo candidate | use brick:Room_Air_Temperature_Sensor | brick:Room_Air_Temperature_Sensor | Brick 1.4 (reviewer) |  | yes | 11 | exact: brick:Room_Air_Temperature_Sensor
AHUB | part+point | SupFan1 | kW | 1 | 15 | QNL_AHUB001_SupFan1.kW | Power | kW | analog | electric power | expanded from the tag | Sensor | fan | brick:Supply_Fan | 1.00 | Dar Cairo | ok | brick:Electric_Power_Sensor | 0.67 | 713 | class name | brick:Thermal_Power_Sensor | 0.25 | OK | brick:Electric_Power_Sensor | OK | 0.40 | brick:Electric_Power_Sensor | Dar Cairo | auto | Dar Cairo | brick:Electric_Power_Sensor | Dar Cairo |  | yes | 21 | exact: brick:Electric_Power_Sensor
AHUB | part+point | SupFan2 | kW | 1 | 15 | QNL_AHUB001_SupFan2.kW | Power | kW | analog | electric power | expanded from the tag | Sensor | fan | brick:Supply_Fan | 1.00 | Dar Cairo | ok | brick:Electric_Power_Sensor | 0.67 | 713 | class name | brick:Thermal_Power_Sensor | 0.25 | OK | brick:Electric_Power_Sensor | OK | 0.40 | brick:Electric_Power_Sensor | Dar Cairo | auto | Dar Cairo | brick:Electric_Power_Sensor | Dar Cairo |  | yes | 21 | exact: brick:Electric_Power_Sensor
CAV | point |  | DmprPos | 50 | 51 | QNL_CAV_1F_S11_001.DmprPos | Damper Position | % | analog | Damper Position | historian description | [6 empty] | brick:Damper_Position_Sensor | 0.67 | 74 | class name | brick:Damper_Position_Command | 0.67 | OK | brick:Damper_Position_Command | OK | 0.67 | brick:Damper_Position_Sensor | Dar Cairo | auto | Dar Cairo | brick:Damper_Position_Sensor | Dar Cairo |  | no |  | nearest SSC: brick:Damper_Position_Status (j=0.67)
CAV | point |  | DuctAirFlow | 50 | 51 | QNL_CAV_1F_S11_001.DuctAirFlow | Duct Air Flow | l/s | analog | Duct Air Flow | historian description | [6 empty] | brick:Air_Flow_Sensor | 0.50 | 23 | class name | brick:Supply_Air_Flow_Sensor | 0.40 | OK | brick:Air_Flow_Alarm | OK | 0.50 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Air_Flow_Sensor | Dar Cairo |  | no |  | nearest SSC: brick:Return_Air_Flow_Sensor (j=0.5)
CAV | point |  | EffectiveSP | 50 | 51 | QNL_CAV_1F_S11_001.EffectiveSP | Effective Temperature Setpoint | °C | analog | Effective Temperature Setpoint | historian description | Setpoint | [5 empty] | brick:Cooling_Temperature_Setpoint | 0.50 | 52 | class name | para:HRW_Heating_Temperature_Setpoint | 0.40 | OK | brick:Effective_Air_Temperature_Setpoint | OK | 0.75 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Effective_Air_Temperature_Setpoint | Brick 1.4 |  | no |  | nearest SSC: brick:Temperature_Setpoint (j=0.67)
CAV | point |  | RmTemp | 6 | 51 | QNL_CAV_B_S12_002.RmTemp | Room/Space Temperature | °C | analog | Room/Space Temperature | historian description | [6 empty] | para:Room_Air_Temperature | 0.50 | 52 | class name | brick:Temperature_Sensor | 0.25 | not in Brick 1.4 | brick:Room_Air_Temperature_Sensor | OK | 0.40 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Room_Air_Temperature_Sensor | Brick 1.4 |  | yes | 11 | exact: brick:Room_Air_Temperature_Sensor
FCU | point |  | CalcEntryScheduledHrs | 137 | 137 | QNL_FCU_1F_001.CalcEntryScheduledHrs | ScheduledPM Hours (Manual Entry) | Hrs | analog | ScheduledPM Hours (Manual Entry) | historian description | Hours | [5 empty] | para:Operation_Hours | 0.20 | 200 | class name | para:Occupied_Hours | 0.20 | not in Brick 1.4 | tag:Manual | OK | 0.07 |  |  | needs-you: no match - propose a para: class | propose a para: class | para:Scheduled_Hrs_Duration | Previous project (SSC) | Reuses SSC precedent para:Scheduled_Hrs_Duration (parent brick:Duration_Sensor). Same manual-entry operating-hours point; no new class minted. | yes | 4 | exact: para:Scheduled_Hrs_Duration
FCU | point |  | CalcEntryUnscheduledHrs | 137 | 137 | QNL_FCU_1F_001.CalcEntryUnscheduledHrs | UnScheduled Outage Hours (Manual Entry) | hrs | analog | UnScheduled Outage Hours (Manual Entry) | historian description | Hours | [5 empty] | para:Operation_Hours | 0.17 | 200 | class name | para:Occupied_Hours | 0.17 | not in Brick 1.4 | tag:Manual | OK | 0.06 |  |  | needs-you: no match - propose a para: class | propose a para: class | para:UnScheduled_Hrs_Duration | Previous project (SSC) | Reuses SSC precedent para:UnScheduled_Hrs_Duration (parent brick:Duration_Sensor). Same manual-entry operating-hours point; no new class minted. | yes | 4 | exact: para:UnScheduled_Hrs_Duration
FCU | point |  | EffectiveSP | 137 | 137 | QNL_FCU_1F_001.EffectiveSP | QNL FCU-1F-001 Terrace Floor Zone-03 South East IDF Room | °C | analog | effective temperature setpoint | expanded from the tag | Setpoint | [5 empty] | brick:Cooling_Temperature_Setpoint | 0.50 | 52 | class name | para:HRW_Heating_Temperature_Setpoint | 0.40 | OK | brick:Effective_Air_Temperature_Setpoint | OK | 0.75 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Effective_Air_Temperature_Setpoint | Brick 1.4 |  | no |  | nearest SSC: brick:Temperature_Setpoint (j=0.67)
FCU | point |  | ValveFbk | 137 | 137 | QNL_FCU_1F_001.ValveFbk | QNL FCU-1F-001 Terrace Floor Zone-03 South East IDF Room | % | analog | valve position feedback | expanded from the tag | Sensor | [5 empty] | brick:Valve_Position_Sensor | 0.50 | 24 | class name | brick:Damper_Position_Sensor | 0.20 | OK | brick:Valve_Position_Sensor | OK | 0.50 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Valve_Position_Sensor | Dar Cairo |  | yes | 133 | exact: brick:Valve_Position_Sensor
FCU | point |  | RtnAirTemp | 82 | 137 | QNL_FCU_1F_002.RtnAirTemp | Return Air Temperature | °C | analog | Return Air Temperature | historian description | [6 empty] | brick:Return_Air_Temperature_Sensor | 0.75 | 24 | class name | para:Room_Air_Temperature | 0.50 | OK | brick:Return_Air_Temperature_Alarm | OK | 0.75 | brick:Return_Air_Temperature_Sensor | Dar Cairo | auto | Dar Cairo | brick:Return_Air_Temperature_Sensor | Dar Cairo |  | yes | 5 | exact: brick:Return_Air_Temperature_Sensor
FCU | point |  | RtnTempSP | 82 | 137 | QNL_FCU_1F_002.RtnTempSP | Return Air Temperature SetPoint | °C | analog | Return Air Temperature SetPoint | historian description | Setpoint | [5 empty] | para:Winter_Supply_Air_Temperature_Setpoint | 0.50 | 20 | class name | para:Summer_Supply_Air_Temperature_Setpoint | 0.50 | not in Brick 1.4 | brick:Return_Air_Temperature_Setpoint | OK | 1.00 | brick:Return_Air_Temperature_Setpoint | Brick 1.4 exact | auto | Brick 1.4 exact | brick:Return_Air_Temperature_Setpoint | Brick 1.4 |  | no |  | nearest SSC: brick:Return_Air_Temperature_Sensor (j=0.75)
FCU | point |  | RmTemp | 59 | 137 | QNL_FCU_1F_001.RmTemp | QNL FCU-1F-001 Terrace Floor Zone-03 South East IDF Room | °C | analog | room temperature | expanded from the tag | [6 empty] | para:Room_Air_Temperature | 0.67 | 52 | class name | brick:Temperature_Sensor | 0.33 | not in Brick 1.4 | brick:Room_Air_Temperature_Sensor | OK | 0.50 | para:Room_Air_Temperature | Dar Cairo | auto | Dar Cairo | para:Room_Air_Temperature | Dar Cairo |  | no |  | nearest SSC: brick:Room_Air_Temperature_Sensor (j=0.67)
VAV | point |  | DmprPos | 245 | 246 | QNL_VAV_1F_S11_001.DmprPos | Damper Position | % | analog | Damper Position | historian description | [6 empty] | brick:Damper_Position_Sensor | 0.67 | 74 | class name | brick:Damper_Position_Command | 0.67 | OK | brick:Damper_Position_Command | OK | 0.67 | brick:Damper_Position_Sensor | Dar Cairo | auto | Dar Cairo | brick:Damper_Position_Sensor | Dar Cairo |  | no |  | nearest SSC: brick:Damper_Position_Status (j=0.67)
VAV | point |  | DuctAirFlow | 245 | 246 | QNL_VAV_1F_S11_001.DuctAirFlow | Duct Air Flow | l/s | analog | Duct Air Flow | historian description | [6 empty] | brick:Air_Flow_Sensor | 0.50 | 23 | class name | brick:Supply_Air_Flow_Sensor | 0.40 | OK | brick:Air_Flow_Alarm | OK | 0.50 |  |  | needs-you: confirm the Dar Cairo candidate | Dar Cairo | brick:Air_Flow_Sensor | Dar Cairo |  | no |  | nearest SSC: brick:Return_Air_Flow_Sensor (j=0.5)
VAV | point |  | EffectiveSP | 245 | 246 | QNL_VAV_1F_S11_001.EffectiveSP | Effective Temperature Setpoint | °C | analog | Effective Temperature Setpoint | historian description | Setpoint | [5 empty] | brick:Cooling_Temperature_Setpoint | 0.50 | 52 | class name | para:HRW_Heating_Temperature_Setpoint | 0.40 | OK | brick:Effective_Air_Temperature_Setpoint | OK | 0.75 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Effective_Air_Temperature_Setpoint | Brick 1.4 |  | no |  | nearest SSC: brick:Temperature_Setpoint (j=0.67)
VAV | point |  | RmTemp | 44 | 246 | QNL_VAV_1F_S11_004.RmTemp | Room/Space Temperature | °C | analog | Room/Space Temperature | historian description | [6 empty] | para:Room_Air_Temperature | 0.50 | 52 | class name | brick:Temperature_Sensor | 0.25 | not in Brick 1.4 | brick:Room_Air_Temperature_Sensor | OK | 0.40 |  |  | needs-you: confirm the Dar Cairo candidate | Brick 1.4 exact | brick:Room_Air_Temperature_Sensor | Brick 1.4 |  | yes | 11 | exact: brick:Room_Air_Temperature_Sensor