## Virtual meters
QNL - virtual meter decisions
Why each meter class is in the ontology, or is not. Sheet state 2026-09-09: 1,453 space-tier virtual meters.
Meter class | Tiers | Meters | Status | Reason
para:Utility_Meter | Building | 1 | Built | Measures the incoming municipal supply. QNL_TotalEnergy.Energy is a live physical meter on the same supply - both are kept, because the gap between an imported reading and a calculated roll-up is losses and unmetered load.
para:SPWR_Meter | Building + Floor | 6 | Built | Small power (sockets and receptacles), not solar. Ticked on the client's own hand-built matrix. QNL has 0 small-power tags and its 17 SMDB tags are all .TripCtr trip counters carrying no power, so these render empty until a small-power circuit is metered. Kept at client direction.
para:Common_Util_Meter | Building + Floor | 6 | Built | Common-area utilities. Depends on MDB, MV, MFM and MCC equipment. Kept at client direction 2026-09-09; which boards feed common areas needs the electrical schedule, which the client does not yet have.
para:CHW_Meter | Building + Floor + Room | 360 | Built | Chilled water thermal load. Real inputs exist, and para:contributionFraction on all 299 VAVs and CAVs is what lets an AHU's load be apportioned down to the rooms it serves. Points take para:KiloWt / para:KiloWt-HR, never unit:KiloW, so a building demand roll-up cannot add chilled-water kW to electrical kW.
para:HVAC_Meter | Building + Floor + Room | 360 | Built | HVAC electrical load. Real inputs exist across AHU and pump power tags.
para:LTG_Meter | Building + Floor + Room | 360 | Built | Lighting electrical load. NO ENERGY INPUT TODAY - QNL's lighting circuits publish On/Off status and no kW or kWh - so all 360 render empty until a lighting energy tag exists. Kept at client direction 2026-09-09: the calculation will be looked at in future.
brick:Electrical_Meter | Building + Floor + Room | 360 | Built | Total electrical roll-up, summing across UPS, panels and generator. Belongs at every tier, unlike Utility.
para:UPS_Meter | Building | 0 | REMOVED 2026-09-09 | A UPS meter sums UPS load and QNL publishes no UPS datapoint. Its only UPS evidence is two room names and one false-positive IO tag (QNL_CHW_HEX.PmpStageUpspd, 'Pump Stage Up Speed'). Would have rendered an empty tile. 1 meter, 9 rows removed.
para:HW_Meter | Building + Floor | 0 | REMOVED 2026-09-09 | Measures DOMESTIC hot water. The equipment exists - the historian carries a calorifier - but it publishes only two alarms and a supply temperature: no power, no energy, no flow, so there is nothing a thermal meter can sum. The calorifier is also outside the agreed selected-datapoint scope. These 6 meters had been summing nothing since the day they were generated. 49 rows removed.
brick:Water_Meter | - | 0 | Not built | No potable-water point exists anywhere in the sheet, so the meter would have no input at all.
para:Occupant-Wellbeing_Meter | - | 0 | Not built | Needs CO2, TVOC, PM, lux, noise or occupancy points. QNL has none of them.
TOTAL space-tier virtual meters |  | 1453 |  | One meter per (class x space). Matches the ontology exactly.