## Virtual meters
SSC - virtual meter decisions
Why each meter class is in the ontology, or is not. Sheet state 2026-09-09: 695 space-tier virtual meters, plus the equipment-tier families.
Meter class | Tiers | Meters | Status | Reason
para:Utility_Meter | Building | 1 | Built | Measures the incoming municipal supply. Inputs: SSC_MV_InACB, SSC_ELEC_MFM_MV_OG_I3.kW/.kWh and SSC_EnergyConsumptionCalc.kW.
para:SPWR_Meter | Building + Floor | 5 | Built | Small power (sockets and receptacles), not solar. 200 SMDB power/energy tags are the candidate inputs; which boards feed small power awaits the electrical schedule, which the client does not yet have. Kept at client direction.
para:Common_Util_Meter | Building + Floor | 5 | Built | Common-area utilities, drawing on the same 12 SMDB boards, same pending schedule. Depends on MDB, MV, MFM and MCC equipment, which SSC has. Kept at client direction.
para:CHW_Meter | Building + Floor + Room | 171 | Built | Chilled water thermal load. Inputs: SSC_CHWConsumption.KWh plus 20 thermal points on 5 AHUs, 11 FCUs and 4 CHW pumps. para:contributionFraction on all 108 VAVs apportions each AHU's load to the rooms it serves - though only 61 of 166 rooms are VAV-served, so the room tier is real for those and empty for the rest.
para:HVAC_Meter | Building + Floor + Room | 171 | Built | HVAC electrical load. Inputs: 22 AHU kW/kWh, 8 CHW pump and 49 MCC power tags.
para:LTG_Meter | Building + Floor + Room | 171 | Built | Lighting electrical load. NO ENERGY INPUT AT ALL - SSC's 55 SSC_LCPB_* lighting circuits are every one an On/Off status with no kW or kWh - so all 171 render empty until a lighting energy tag exists. Built at client direction to match QNL, which is in the same position.
brick:Electrical_Meter | Building + Floor + Room | 171 | Built | Total electrical roll-up. Inputs: 100 SMDB kW, 100 SMDB MWh and 110 MV tags.
para:UPS_Meter | Building | 0 | REMOVED 2026-09-09 | A UPS meter sums UPS load and SSC publishes no UPS datapoint. Would have rendered an empty tile. 1 meter, 9 rows removed. Note the rooms named UPS keep their own room-tier meters - those are a different thing and were untouched.
para:HW_Meter | - | 0 | Never built; declaration removed 2026-09-09 | Measures DOMESTIC hot water. SSC's heating is ELECTRIC - 5 AHU heater commands and 14 CRAC heater statuses - and there is no hot-water loop and not one hot-water tag in 5,751 IO rows. No meter was ever generated, but the sheet still carried a dangling para:HW_Meter class declaration with nothing under it; that row was removed.
Cooling load, AHU and FCU coils and CHW pumps | Equipment | 18 | Built (delivered, restructured 2026-09-09) | 36 cooling load points on 16 cooling valves and 4 CHW booster pumps. Delivered by the client behind an intermediate meter entity; that node was removed so the points hang directly off the coil valve or pump that meters them, and they were retyped to para:Cooling_Thermal_* so cooling and heating are distinguishable.
Heating load, AHU heating coils | Equipment | 5 | Added 2026-09-09 | SSC's AHUs heat electrically, so the coil's heat output is real thermal power worth metering. 10 points on the 5 brick:Heating_Coil entities. NO INPUT YET: the only heating point is a percent command with no nameplate rating, so these are containers until the AHU heater kW arrives from the datasheets - percent x rating is the whole formula. Tokens HEATPWR_KWT_CALC / HEATPWR_KWHT_CALC are derived, not confirmed: Dar Cairo has no heating token at all.
Electrical load, FCUs, motors and CHW pumps | Equipment | 25 | Built (delivered, restructured 2026-09-09) | 46 electrical points delivered by the client behind an intermediate meter entity. Those nodes were removed so every meter point in the sheet hangs off the equipment it measures, leaving one convention instead of two.
TOTAL space-tier virtual meters |  | 695 |  | One meter per (class x space). Matches the ontology exactly.
Equipment-tier metered assets |  | 48 |  | Counted separately - these are host assets carrying load points, not space meters, so the two totals are not addable.