## START HERE
RDC asset register, checked against the BMS floor-plan screens
This workbook holds the RDC section of the Controllable Asset Registry and nothing else. The HQ, QNL and SSC sections were dropped, as asked.
What was done
Every RDC BMS screen draws a dotted leader from each unit widget to a small grey dot inside the room it serves. The leaders turn square corners, so they were followed corner by corner and the dot at the end read off the plan by eye. The tracer only says where to look; the room was named by reading the screen, never by inference.
47 screens, across the North, South and Utility buildings and the walkway between them. 1,033 unit widgets were found on them and 440 of those leaders reached a dot.
The columns this pass added
J ROOM PER BMS SCREEN the room the leader ends in, as the screen names it
K BMS SCREEN which screen it was read from
L BMS SCREEN vs DRAWINGS SAME / DIFF / CONVENTION / CHECK / OPEN
M WHY what a reviewer needs in order to judge the row
SAME the screen and column D agree
DIFF they name different rooms - the rows worth your time
CONVENTION the same room number written two ways: the register writes a first-floor room N-1143 where the screen writes N-143, and abbreviates differently (Conf / Conference, TC3 / Tissue Culture 3). Not a disagreement about which room, but the ontology has to use one spelling.
CHECK read from the screen, but the dot sits on a wall between two rooms, or in open floor carrying a name but no wall. Worth a second look.
OPEN no reading. Either no screen covers the unit, or the leader could not be followed, or the dot landed somewhere the screen does not name. Column M says which, per row.
What it found
305 of 1759 rows carry a reading; 1454 are still open.
90 SAME, 49 DIFF, 12 CONVENTION, 154 CHECK.
215 rows are filled green across A:K - every DIFF, CONVENTION and CHECK.
The largest single finding: SB-AHU8031 to 8035 and 8037 all carry COMPUTER RESEARCH LAB S-1112 in the register, and all six leaders - on two different screens, GF-5 and GF-7 - run into Mech S-0136. Six units sharing one room where the screens put them in the plant room reads as a filled-down cell rather than six readings.
Equipment on the screens that the register does not carry
The register has no EF rows at all. Nine exhaust fans were read off the screens - SB-EF-8041 to 8044 and UB-EF-8642 to 8646 - and there is no row to put them on. NB-EF-8553, NB-EF-8554 and the ERU units on the second-floor screens are absent for the same reason.
Three CAV/CEV pairs (7590/7591, 7610/7611, 7760/7761) have a CEV row and no CAV row. Those readings are recorded against the CEV half.
Two things to know about the join
The screens label constant-volume terminals CAV and the register labels them AT - one CAV row against 510 AT rows. Rows joined across that say so in column M.
A double-height space is drawn on both its levels. NB-VAV4050-VEV4051 and NB-VAV4060-VEV4061 appear on the first-floor screen but are ground floor units in the register, and the register agrees with the reading.
A blank in column J is not an oversight. A guessed room reads exactly like a read one once it is in the sheet, and nobody can tell them apart afterwards - so where the screen does not settle the room, column J is left empty and column M says why.

## Controllable Asset Registry
Controllable Asset Registry
Tag No. | Equipment Type | Inluded/ Not Inlcuded | ROOM NAME AS PER DRAWINGS |  | ROOM NAME PER VAV / FCU LIST (WHERE DIFFERENT) | ROOM PER BMS SCREEN | BMS SCREEN | BMS SCREEN vs DRAWINGS | WHY
RDC_NB_AHU8511 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-2 | OPEN | as NB-AHU-8513 - the penthouse space carries no room name
RDC_NB_AHU8512 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_2F_AHU8513 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_AHU8514 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-2 | OPEN | as NB-AHU-8513 - the penthouse space carries no room name
RDC_NB_2F_AHU8515 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-2 | OPEN | as NB-AHU-8513 - the penthouse space carries no room name
RDC_NB_2F_AHU8516 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-2 | OPEN | the dot lands west of Emer. Elec. N-2106 in penthouse floor the screen does not name
RDC_NB_2F_AHU8517 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_AHU8518 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-4 | OPEN | the dot lands in the second-floor penthouse space, which this screen prints no room name for; only Normal Elec. N-2107, Emer. Elec. N-2108 and IDF N-2110 are named on it
RDC_NB_2F_AHU8519 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-4 | OPEN | as NB-AHU-8518 - the penthouse space carries no room name
RDC_NB_2F_AHU8520 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-4 | OPEN | as NB-AHU-8518 - the penthouse space carries no room name
RDC_NB_2F_AHU8521 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_AHU8011 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_AHU8012 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_AHU8021 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_AHU8022 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 |  |  | South Penthouse S-2101 | South Building/SF/SF-1 | SAME
RDC_SB_2F_AHU8023 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 |  |  |  | South Building/SF/SF-1 | CHECK | one of the same cluster of dots
RDC_SB_2F_AHU8024 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 |  |  | South Penthouse S-2101 | South Building/SF/SF-2 | SAME
RDC_SB_2F_AHU8025 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 |  |  | South Penthouse S-2101 | South Building/SF/SF-2 | SAME
RDC_SB_2F_AHU8026 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_AHU8031 | AHU | Not Included | COMPUTER RESEARCH LAB S-1112 |  |  | Mech S-0136 | South Building/GF/GF-5 | DIFF | the screen puts SB-AHU8031 in Mech S-0136; the register says COMPUTER RESEARCH LAB S-1112
RDC_SB_GF_AHU8032 | AHU | Not Included | COMPUTER RESEARCH LAB S-1112 |  |  | Mech S-0136 | South Building/GF/GF-5 | DIFF | the screen puts SB-AHU8032 in Mech S-0136; the register says COMPUTER RESEARCH LAB S-1112
RDC_SB_GF_AHU8033 | AHU | Not Included | COMPUTER RESEARCH LAB S-1112 |  |  | Mech S-0136 | South Building/GF/GF-5 | DIFF | the screen puts SB-AHU8033 in Mech S-0136; the register says COMPUTER RESEARCH LAB S-1112
RDC_SB_GF_AHU8034 | AHU | Not Included | COMPUTER RESEARCH LAB S-1112 |  |  | Mech S-0136 | South Building/GF/GF-5 | DIFF | the screen puts SB-AHU8034 in Mech S-0136; the register says COMPUTER RESEARCH LAB S-1112
RDC_SB_GF_AHU8035 | AHU | Not Included | COMPUTER RESEARCH LAB S-1112 |  |  | MECH S-0136 | South Building/GF/GF-7 | DIFF | the screen puts SB-AHU8035 in MECH S-0136; the register says COMPUTER RESEARCH LAB S-1112
RDC_SB_GF_AHU8036 | AHU | Not Included | COMPUTER RESEARCH LAB S-1112 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_AHU8037 | AHU | Not Included | COMPUTER RESEARCH LAB S-1112 |  |  | Cyber Server S-0138 | South Building/GF/GF-6 | DIFF | the screen puts SB-AHU8037 in Cyber Server S-0138; the register says COMPUTER RESEARCH LAB S-1112 - the dot sits on the room's right-hand wall
RDC_SB_GF_AHU8041 | AHU | Not Included | UPS ROOM S-0145 |  |  |  | South Building/GF/GF-6 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_GF_AHU8042 | AHU | Not Included | UPS ROOM S-0145 |  |  | Corridor S-0143 | South Building/GF/GF-6 | DIFF | the screen puts SB-AHU8042 in Corridor S-0143; the register says UPS ROOM S-0145 - the dot is in the corridor below the room name
RDC_UB_AHU8601 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-2 | SAME
RDC_UB_AHU8602 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-2 | SAME
RDC_UB_AHU8603 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-1 | SAME
RDC_UB_AHU8604 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-1 | SAME
RDC_UB_AHU8605 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-1 | SAME
RDC_UB_AHU8606 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-1 | SAME
RDC_UB_AHU8607 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-1 | SAME
RDC_UB_AHU8608 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-1 | SAME
RDC_UB_AHU8609 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-2 | SAME
RDC_NB_GF_VAV4001 | VAV | Included | Store N-0201 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4005_EV4006 | EV | Not Included | STAIR 02 N-0 ST02 |  |  |  | North Building/GF/GF-2 | OPEN | no leader could be followed away from the widget
RDC_NB_GF_VAV4040 | VAV | Not Included | Air Quality High Bay N-0215A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4050_VEV4051 | VEV | Not Included | CSP High Bay N-0215B |  |  | CSP High Bay N-0215B | North Building/GF/GF-2 | SAME
RDC_NB_GF_VAV4060_VEV4061 | VEV | Not Included | Machine Shop N-0215C |  |  | Machine Shop N-0215C | North Building/GF/GF-2 | SAME
RDC_NB_GF_VAV4070A_VEV4073A | VAV | Not Included | Open High Bay Lab N-0215D |  |  | Open High Bay Lab N-0215D | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4070B_VEV4073B | VAV | Not Included | Open High Bay Lab N-0215D |  |  |  | North Building/GF/GF-1 | OPEN | as NB-VAV4081A-VEV4083A - no leader could be followed away from the widget
RDC_NB_GF_VAV4071A_VEV4074A | VAV | Not Included | Open High Bay Lab N-0215D |  |  |  | North Building/FF/FF-1 | CHECK | read on the first floor screen; double-height space
RDC_NB_GF_VAV4071B_VEV4074B | VAV | Not Included | Open High Bay Lab N-0215D |  |  |  | North Building/FF/FF-1 | CHECK | read on the first floor screen; double-height space
RDC_NB_GF_VAV4072A_VEV4075A | VAV | Not Included | Open High Bay Lab N-0215D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4072B_VEV4075B | VAV | Not Included | Open High Bay Lab N-0215D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4080A_VEV4082A | VAV | Not Included | Desal High Bay Lab N-0215E |  |  | Desal High Bay Lab N-0215E | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4080B_VEV4082B | VAV | Not Included | Desal High Bay Lab N-0215E |  |  |  | North Building/GF/GF-1 | OPEN | as NB-VAV4081A-VEV4083A - no leader could be followed away from the widget
RDC_NB_GF_VAV4081A_VEV4083A | VAV | Not Included | Desal High Bay Lab N-0215E |  |  |  | North Building/GF/GF-1 | OPEN | the leader could not be followed clear of the widget - this unit is drawn in alarm, boxed in red, and the box border runs where the leader leaves
RDC_NB_GF_VAV4081B_VEV4083B | VAV | Not Included | Desal High Bay Lab N-0215E |  |  | Desal High Bay Lab N-0215E | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4090_VEV4091 | VEV | Not Included | Support Lab N-0215F |  |  |  | North Building/GF/GF-1 | CHECK | the dot sits near the boundary with Desal High Bay Lab N-0215E above it
RDC_NB_GF_VAV4100_EV4101 | EV | Not Included | Emergency Elec. Room N-0225 |  |  | Emergency Elec. Room N-0225 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4105_EV4106 | EV | Not Included | Normal Electrical Room N-0225 |  |  | Normal Elec. Room N-0226 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4110_EV4111 | EV | Included | Conference Room N-0227 |  |  | Conference Room N-0227 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4115_EV4116 | EV | Included | Office N-0228 |  |  | Office N-0228 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4120_EV4121 | EV | Included | Office N-0229 |  |  | Office N-0229 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4125_EV4126 | EV | Included | Office N-0230 |  |  | Office N-0230 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4130_EV4131 | EV | Included | Office N-0231 |  |  | Office N-0231 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4135_EV4136 | EV | Included | Office N-0232 |  |  | Office N-0232 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4140_EV4141 | EV | Included | Conference Room N-0233 |  |  |  | North Building/GF/GF-1 | OPEN | the dot sits exactly on the wall between Conf. Room N-0233 and Storage Room N-0237 and could be either
RDC_NB_GF_VAV4145_EV4146 | EV | Included | Office N-0234 |  |  | Office N-0234 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4165_EV4166 | EV | Included | Office N-0236 |  |  | Office N-0236 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4180_VEV4181 | VEV | Not Included | Test Room N-0240A |  |  |  | North Building/GF/GF-2 | OPEN | the walk ended east of Service Corridor N-0207 in floor the screen does not name
RDC_NB_GF_VAV4190_VEV4192 | VEV | Not Included | CSP Lab N-0240B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4191 | VAV | Not Included | CSP Lab N-0240B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4200_VEV4201 | VEV | Not Included | Test Room 1 N-0240C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4210 | VAV | Not Included | Desalination Lab N-0240D |  |  |  | North Building/GF/GF-1 | CHECK | the dot is in open floor carrying the Desal Lab N-0240D name but no wall separates it from Corridor N-0246 below
RDC_NB_GF_VAV4211 | VAV | Not Included | Desalination Lab N-0240D |  |  |  | North Building/GF/GF-1 | OPEN | its leader converges with NB-VAV4210, NB-VEV4213A and NB-VEV4213B on one point; nothing on the screen says which owns it
RDC_NB_GF_VAV4212 | VAV | Not Included | Desalination Lab N-0240D |  |  |  | North Building/GF/GF-1 | OPEN | as NB-VAV4211 - four leaders share one endpoint
RDC_NB_GF_VAV4225 | VAV | Included | Office N-0247 |  |  | Office N-0247 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4230 | VAV | Included | Office N-0248 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4235 | VAV | Included | Office 05 -8WS- N-0250 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4240 | VAV | Included | Office 04 N-0251 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4245 | VAV | Included | Office N-0252 |  |  | Office N-0252 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4250 | VAV | Included | Office N-0253 |  |  | Office N-0253 | North Building/GF/GF-1 | SAME
RDC_NB_GF_VAV4255 | VAV | Included | Office N-0254 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4260 | VAV | Included | Office 05 -8WS- N-0255 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4265 | VAV | Included | Office N-0256 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4270 | VAV | Included | Office N-0257 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4275 | VAV | Included | Office N-0258 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4280 | VAV | Included | Office N-0259 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4285 | VAV | Included | Workstation N-0260 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4290 | VAV | Included | Office 04 N-0261 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4295 | VAV | Included | Office N-0262 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV4300 | VAV | Included | Office N-0263 |  |  |  | North Building/GF/GF-3 | CHECK | the dot sits on the room's left-hand wall
RDC_NB_GF_VAV4305 | VAV | Included | Office N-0264 |  |  |  | North Building/GF/GF-3 | CHECK | the dot sits on the room's left-hand wall
RDC_NB_GF_VAV4310 | VAV | Included | Workstation N-0265 |  |  |  | North Building/GF/GF-3 | OPEN | the dot lands on the outer wall at the bottom of the plan, below Work Station N-0265, and is not inside any room
RDC_NB_GF_VAV4312 | VAV | Included | Breakout N-0265B |  |  |  | North Building/GF/GF-3 | OPEN | as NB-VAV4310 - the dot is on the outer wall below Breakout N-0265B
RDC_NB_GF_VAV5000_EV5002 | EV | Included | Lobby North N-0101 |  |  |  | North Building/GF/GF-7 | OPEN | the dot lands between Exp. Office N-0172 and Store N-0362B with no wall drawn at that point
RDC_NB_GF_VAV5001_EV5003 | EV | Included | Lobby North N-0101 |  |  |  | North Building/GF/GF-7 | OPEN | the dot lands left of Office N-0363 in circulation space the screen does not name
RDC_NB_GF_VAV5010_EV5011 | EV | Included | Conf N-0106 |  |  |  | North Building/GF/GF-7 | OPEN | the dot falls among the angled rooms between Conf N-0106 and JC N-0108 and cannot be assigned to one
RDC_NB_GF_VAV5015_EV5016 | EV | Included | Conference N-0107 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5025 | VAV | Included | Corridor N-0110 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5030_EV5031 | EV | Included | Normal Elec. N-0113 |  |  |  | North Building/GF/GF-7 | OPEN | as NB-VAV5040-EV5041 - the same angled band
RDC_NB_GF_VAV5040_EV5041 | EV | Not Included | Normal Elec. N-0113 |  |  |  | North Building/GF/GF-7 | OPEN | the dot falls in the angled band of small rooms between Vestibule N-0136A and the Elevator; at the size the screen draws them it cannot be assigned to one
RDC_NB_GF_VAV5045_EV5046 | EV | Not Included | Emergency Elec. N-0114 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5050 | VAV | Not Included | Analytical Core Lab 1 N-0114A |  |  |  | North Building/GF/GF-5 | CHECK | the dot is below the room name in open lab floor
RDC_NB_GF_VAV5051 | VAV | Not Included | Analytical Core Lab 1 N-0114A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5054 | VAV | Not Included | Clean Lab N-0114B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5060_CEV5061 | CEV | Not Included | Clean Lab N-0114B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5070 | VAV | Not Included | Dirty Lab N-0114C |  |  |  | North Building/GF/GF-5 | DIFF | the screen puts NB-VAV5070 in Serv Core N-0136; the register says Dirty Lab N-0114C - the dot is in the band below Cold Room N-0114E carrying the Serv Core name
RDC_NB_GF_VAV5080_VEV5081 | VEV | Not Included | Bio Analyt N-0114D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5090 | VAV | Not Included | Air Quality N-0114F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5091 | VAV | Not Included | Air Quality N-0114F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5100_EV5101 | EV | Included | Office N-0115 |  |  | Office N-0115 | North Building/GF/GF-5 | SAME
RDC_NB_GF_VAV5105 | VAV | Included | Office N-0116 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5110 | VAV | Included | Office N-0117 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5115 | VAV | Included | Office N-0118 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5120 | VAV | Included | Office N-0119 |  |  | Office N-0119 | North Building/GF/GF-5 | SAME
RDC_NB_GF_VAV5125 | VAV | Included | Office N-0120 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5130 | VAV | Included | Office N-0121 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5135 | VAV | Included | Office N-0122 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5140 | VAV | Included | Office N-0123 |  |  | Office N-0123 | North Building/GF/GF-5 | SAME
RDC_NB_GF_VAV5145 | VAV | Included | Office N-0124 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5150 | VAV | Included | Office N-0125 |  |  | Office N-0125 | North Building/GF/GF-5 | SAME
RDC_NB_GF_VAV5152 | VAV | Included | Office N-0126 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5155 | VAV | Included | Office N-0127 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5156 | VAV | Included | Office 04 N-0129 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5165_EV5166 | EV | Included | Corridor N-0134 |  |  | Serv Core N-0136 | North Building/GF/GF-5 | DIFF | the screen puts NB-VAV5165-EV5166 in JC N-0132; the register says Corridor N-0134 - the dot is left of the JC N-0132 name in circulation space
RDC_NB_GF_VAV5180 | VAV | Not Included | Analytical Core Lab 2 N-0140A |  |  |  | North Building/GF/GF-6 | CHECK | the dot sits on the room's upper wall
RDC_NB_GF_VAV5181 | VAV | Not Included | Analytical Core Lab 2 N-0140A |  |  |  | North Building/GF/GF-6 | CHECK | the dot is inside the room below its upper wall
RDC_NB_GF_VAV5190 | VAV | Not Included | Furnace Room N-0140B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5200 | VAV | Not Included | Prep Lab N-0140C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5210 | VAV | Not Included | Sputter Room N-0140D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5220 | VAV | Not Included | MBE Evap Room N-0140E |  |  |  | North Building/GF/GF-6 | CHECK | the dot sits on the room's upper wall, east end
RDC_NB_GF_VAV5230 | VAV | Not Included | MBE Evap Room N-0140E |  |  |  | North Building/GF/GF-6 | OPEN | the dot lands at the top of the band east of MBB EVAP Room N-0140E where the screen prints no room name
RDC_NB_GF_VAV5250_VEV5251 | VEV | Included | MBE Evap Room N-0140E |  |  |  | North Building/GF/GF-6 | OPEN | the dot lands just west of Office N-0158 in circulation space the screen does not name
RDC_NB_GF_VAV5260_VEV5261 | VEV | Not Included | PLD Room N-0140J |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5270A | VAV | Not Included | Organic Chemistry Lab N-0140K |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5270B | VAV | Not Included | Org Chem N-0140K |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5295_EV5296 | EV | Included | Conference Room N-0149 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5300 | VAV | Included | Corridor N-0150 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5305 | VAV | Included | Office N-0151 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5310 | VAV | Included | Office N-0152 |  |  | Office N-0152 | North Building/GF/GF-6 | SAME
RDC_NB_GF_VAV5315 | VAV | Included | Open Office N-0153 |  |  |  | North Building/GF/GF-6 | CHECK | the dot is in the open office area near its left edge
RDC_NB_GF_VAV5325 | VAV | Included | Office N-0155 |  |  |  | North Building/GF/GF-6 | CHECK | the dot sits on the room's left-hand wall
RDC_NB_GF_VAV5330 | VAV | Included | Office N-0156 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5335 | VAV | Included | Office N-0157 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5340 | VAV | Included | Office N-0158 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5345 | VAV | Included | Office N-0159 |  |  |  | North Building/GF/GF-6 | CHECK | the dot sits on the wall between Office N-0159 and Office N-0161
RDC_NB_GF_VAV5355 | VAV | Included | Office N-0161 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5360 | VAV | Included | Office N-0162 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5365 | VAV | Included | Office N-0163 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5370 | VAV | Included | Office N-0164 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5380 | VAV | Included | Office N-0166 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5385 | VAV | Included | Office N-0167A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5390 | VAV | Included | Office 04 N-0168 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5395 | VAV | Included | Exp. Office N-0169 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5400 | VAV | Included | Reception Area N-0170 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5405 | VAV | Included | Exp. Office N-0172 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5410_EV5411 | EV | Included | Conf Room N-0173 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV5415 | VAV | Included | Office 04 N-0174 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6000_EV6001 | EV | Included | Conf Room N-0301 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6010_EV6011 | EV | Included | Conf N-0304 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6025_EV6026 | EV | Not Included | Normal Elec. N-0310 |  |  |  | North Building/GF/GF-7 | DIFF | the screen puts NB-VAV6025-EV6026 in IDF N-0311; the register says Normal Elec. N-0310 - the dot sits just right of the room name
RDC_NB_GF_VAV6130_EV6131 | EV | Included | Store N-0315 |  |  |  | North Building/GF/GF-8 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_GF_VAV6135 | VAV | Included | Store N-0316 |  |  | Store N-0316 | North Building/GF/GF-8 | SAME
RDC_NB_GF_VAV6140 | VAV | Included | Workstation N-0317 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6145 | VAV | Included | Office N-0318 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6150 | VAV | Included | Office N-0319 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6155 | VAV | Included | Workstation N-0320 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6160 | VAV | Included | Office N-0321 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6170 | VAV | Included | Office N-0323 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6175 | VAV | Included | Workstation N-0324 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6180 | VAV | Included | Office N-0325 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6185_EV6186 | EV | Included | Office N-0326 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6190_EV6191 | EV | Not Included | Normal Elec. N-0328 |  |  |  | North Building/GF/GF-8 | CHECK | the dot is inside the room below its name
RDC_NB_GF_VAV6195 | VAV | Included | Store N-0329 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6200_EV6201 | EV | Included | Conf N-0330 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6205_EV6206 | EV | Included | Conf N-0331 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6210 | VAV | Included | Corr. +N-033B N-0332C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6220_EV6221 | EV | Not Included | Emergency Elec. N-0333 |  |  |  | North Building/GF/GF-8 | CHECK | the dot sits on the room's left-hand wall
RDC_NB_GF_VAV6240_EV6241 | EV | Not Included | Emergency Electrical N-0350A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6285_EV6286 | EV | Included | Conf N-0358 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6295_EV6296 | EV | Included | Conference N-0360 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6300 | VAV | Included | Store N-0362B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6305 | VAV | Included | Office N-0363 |  |  |  | North Building/GF/GF-7 | DIFF | the screen puts NB-VAV6305 in Conference Room N-0364A; the register says Office N-0363 - the dot sits on the room's left-hand wall
RDC_NB_GF_VAV6310 | VAV | Included | Office N-0364 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6315_EV6316 | EV | Included | Conf Room N-0364A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6320 | VAV | Included | Corridor N-0365 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6325 | VAV | Included | Office N-0366 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6330 | VAV | Included | Office 04 N-0367 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6335 | VAV | Included | Office N-0368 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6340 | VAV | Included | Office N-0369 |  |  |  | North Building/GF/GF-9 | CHECK | the dot sits on the wall between Office N-0366 and Office N-0369
RDC_NB_GF_VAV6345 | VAV | Included | Office N-0370 |  |  |  | North Building/GF/GF-9 | CHECK | the dot is inside the room near its left wall
RDC_NB_GF_VAV6350 | VAV | Included | Office N-0371 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6355 | VAV | Included | Workstation N-0372 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6360 | VAV | Included | Office N-0374 |  |  |  | North Building/GF/GF-9 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_GF_VAV6365 | VAV | Included | Office N-0375 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6370 | VAV | Included | Office N-0376 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6375 | VAV | Included | Office N-0377 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6380 | VAV | Included | Workstation N-0378 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6390 | VAV | Included | Office N-0379 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6395 | VAV | Included | Office N-0380 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6400 | VAV | Included | Workstation N-0381 |  |  |  | North Building/GF/GF-9 | CHECK | the dot is in the open work station area left of Office N-0383
RDC_NB_GF_VAV6405 | VAV | Included | Office N-0382 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV6410 | VAV | Included | Office N-0383 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7000 | VAV | Included | Vestibule Staging N-0401 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7020A | VAV | Not Included | NMR Lab N-0404A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7020B | VAV | Not Included | NMR Lab N-0404A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7021A | VAV | Not Included | NMR Lab N-0404A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7021B | VAV | Not Included | NMR Lab N-0404A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7030_VEV7031 | VEV | Not Included | CONTROL ROOM N-0404B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7040 | VAV | Not Included | Service Equipm. Room N-0404C |  |  |  | North Building/GF/GF-10 | DIFF | the screen puts NB-VAV7040 in Control Room N-0404B; the register says Service Equipm. Room N-0404C - the dot is inside the room near its lower edge
RDC_NB_GF_VAV7050_VEV7051 | VEV | Not Included | EM Prep 1 - MAT N-0404D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7060_VEV7061 | VEV | Not Included | EM Prep 2 - BIO N-0404E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7070A | VAV | Not Included | Surf Analysis Lab N-0404F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7070B | VAV | Not Included | Surf Analysis Lab N-0404F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7071A | VAV | Not Included | Surf Analysis Lab N-0404F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7071B | VAV | Not Included | Surf Analysis Lab N-0404F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7080 | VAV | Included | Exp. Office N-0410 |  |  |  | North Building/GF/GF-10 | CHECK | the dot sits just inside the room's upper left corner
RDC_NB_GF_VAV7085 | VAV | Included | Office N-0411 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7090 | VAV | Included | Office N-0412 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7095 | VAV | Included | Office N-0413 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7100 | VAV | Included | Office N-0414 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7105 | VAV | Included | Office N-0415 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7110 | VAV | Included | Office N-0416 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7115 | VAV | Included | Office N-0417 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7120 | VAV | Included | Office N-0418 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7125_EV7126 | EV | Not Included | Normal Elec. Room N-0420 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7130 | VAV | Included | Office N-0421 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7135 | VAV | Included | Office N-0422 |  |  |  | North Building/GF/GF-10 | CHECK | the dot sits on the room's upper wall
RDC_NB_GF_VAV7140_EV7141 | EV | Included | Conference N-0423 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7145 | VAV | Included | Office N-0425 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7155 | VAV | Included | Office N-0427 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7165 | VAV | Included | Office N-0429 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7175 | VAV | Included | Office 05-15-WS N-0431 |  |  | Corridor N-0432 | North Building/GF/GF-10 | DIFF | the screen puts NB-VAV7175 in Corridor N-0432; the register says Office 05-15-WS N-0431 - the dot is in the corridor rather than a room off it
RDC_NB_GF_VAV7176 | VAV | Included | Office 05-15-WS N-0431 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7180 | VAV | Included | Corridor N-0432 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7185_EV7186 | EV | Not Included | Emer. Elec. Room N-0433 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7195 | VAV | Included | Office 04 N-0436 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7205 | VAV | Included | Office 04 N-0438 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7215_EV7216 | EV | Included | Conference Room N-0440 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7220_CEV7221 | CEV | Included | Service Corridor N-0441 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7230_VEV7231 | VEV | Not Included | Inter Lab N-0442A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7240_VEV7241A | VAV | Not Included | Optical Lab N-0442B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7250_VEV7251 | VEV | Included | CONF N-0442C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7260_VEV7261 | VEV | Not Included | SEM 1 Room N-0442D |  |  |  | North Building/GF/GF-11 | OPEN | the dot lands at the top of A/L 1 N-0442H on the wall it shares with Corridor N.0451
RDC_NB_GF_VAV7270_VEV7271 | VEV | Not Included | SERV 1 N-0442E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7280_VEV7281 | VEV | Not Included | Confocal 2 Room N-0442F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7290_VEV7291 | VEV | Not Included | SEM 2 N-0442G |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7300 | VAV | Not Included | Air Lock 1 N-0442H |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7310_VEV7311 | VEV | Not Included | SEM 3 N-0442J |  |  |  | North Building/GF/GF-11 | CHECK | the dot sits just inside the room's upper left corner
RDC_NB_GF_VAV7320_VEV7321 | VEV | Not Included | SEM 4 N-0442K |  |  |  | North Building/GF/GF-11 | OPEN | the dot lands between Sem 3 N-0442J and A/L 1 N-0442H with no wall drawn at that point
RDC_NB_GF_VAV7330_VEV7331 | VEV | Not Included | SEM 5 N-0442L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7340_VEV7341 | VEV | Not Included | SERV 2 N-0442M |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7350_VEV7351 | VEV | Not Included | SEM Lab N-0442N |  |  |  | North Building/GF/GF-11 | CHECK | the dot sits on the room's upper wall
RDC_NB_GF_VAV7360_VEV7361 | VEV | Not Included | SEM Lab N-0442p |  |  |  | North Building/GF/GF-11 | CHECK | the dot sits on the room's upper wall
RDC_NB_GF_VAV7370_VEV7371 | VEV | Not Included | A/L 2 N-0442R |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7385 | VAV | Included | Office N-0444 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7390 | VAV | Included | Office 04 N-0445 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7395 | VAV | Included | Workstation N-0446 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7400 | VAV | Included | Office N-0447 |  |  |  | North Building/GF/GF-11 | CHECK | the dot sits on the room's left-hand wall
RDC_NB_GF_VAV7405 | VAV | Included | Office N-0448 |  |  |  | North Building/GF/GF-11 | CHECK | the dot sits on the room's left-hand wall
RDC_NB_GF_VAV7410 | VAV | Included | Office N-0449 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7415 | VAV | Included | Office N-0450 |  |  |  | North Building/GF/GF-11 | CHECK | the dot is inside the room near its left wall
RDC_NB_GF_VAV7425 | VAV | Included | Office 05-8-WKS N-0452 |  |  |  | North Building/GF/GF-11 | CHECK | the dot is in the open Work Station N-0452 area
RDC_NB_GF_VAV7430 | VAV | Included | Office N-0453 |  |  |  | North Building/GF/GF-11 | CHECK | the dot sits on the room's left-hand wall
RDC_NB_GF_VAV7435 | VAV | Included | Office N-0454 |  |  |  | North Building/GF/GF-11 | CHECK | a second dot in the same room, west end
RDC_NB_GF_VAV7440 | VAV | Included | Office N-0455 |  |  |  | North Building/GF/GF-11 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_GF_VAV7445 | VAV | Included | Office 04 N-0456 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7460 | VAV | Included | Office 05-8-WKS N-0457 |  |  | Workstation N-0457 | North Building/GF/GF-11 | DIFF | the screen puts NB-VAV7460 in Corridor N.0451; the register says Office 05-8-WKS N-0457 - the dot is in the corridor rather than in a room off it
RDC_NB_GF_VAV7465 | VAV | Included | Office N-0458 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7470 | VAV | Included | Office N-0459 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7475 | VAV | Included | Office N-0460 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7480 | VAV | Included | Office N-0461 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7485 | VAV | Included | Office 05-8-WKS N-0462 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7490_EV7495 | EV | Included | Confer N-0463 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7496 | VAV | Included | Office 04 N-0464 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7498 | VAV | Included | Office N-0465 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV7499 | VAV | Included | Office 04 N-0466 |  |  |  | North Building/GF/GF-11 | CHECK | the dot sits inside the room near its left wall
RDC_SB_1F_VAV0506 | VAV | Included | Conf. S-1110 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0507 | VAV | Not Included | Computer Research Lab-4 S-1112 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0508 | VAV | Included | Conf S-1113 |  |  |  | South Building/FF/FF-6 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV0509 | VAV | Included | NCIR Office S-1115 |  |  |  | South Building/FF/FF-6 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV0510 | VAV | Included | Workstation S-1115A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0511 | VAV | Included | NCIR Office S-1116 |  |  |  | South Building/FF/FF-5 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV0512 | VAV | Included | NCIR Office S-1117 |  |  |  | South Building/FF/FF-5 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV0513 | VAV | Included | NCIR Office S-1118 |  |  |  | South Building/FF/FF-5 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV0514 | VAV | Included | NCIR Office S-1119 |  |  | Sc.Comp.Office3 S-1119 | South Building/FF/FF-5 | CONVENTION | the dot is inside the room near its right wall
RDC_SB_1F_VAV0518 | VAV | Included | Office S-1161 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0519 | VAV | Included | Office S-1162 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0520 | VAV | Included | Office S-1163 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0521 | VAV | Included | Office S-1164 |  |  |  | South Building/FF/FF-6 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV0522 | VAV | Included | Office S-1165 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0523 | VAV | Included | Office S-1166 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0526 | VAV | Included | Office S-1171 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0527 | VAV | Included | Office S-1172 |  |  |  | South Building/FF/FF-6 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV0528 | VAV | Included | Office S-1173 |  |  |  | South Building/FF/FF-6 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV0529 | VAV | Included | Corridor S-1174 |  |  |  | South Building/FF/FF-6 | CHECK | the dot is in the corridor rather than a room off it
RDC_SB_1F_VAV0530 | VAV | Included | Situation Room S-1175 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0531 | VAV | Not Included | Immersive Viz Lab S-1176 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0532 | VAV | Included | Conference Room S-1177 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV0533 | VAV | Included | Telepresence S-1179 |  |  |  | South Building/FF/FF-6 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV0538 | VAV | Included | Workstation S-1151A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1501 | VAV | Included | Workstation S-1119A |  |  |  | South Building/FF/FF-5 | CHECK | the dot is in the open workstation area
RDC_SB_1F_VAV1502 | VAV | Included | NCIR Office S-1120 |  |  |  | South Building/FF/FF-5 | CHECK | a second dot in the same room
RDC_SB_1F_VAV1503 | VAV | Included | NCIR Office S-1121 |  |  |  | South Building/FF/FF-5 | CHECK | the dot is inside the room near its right wall
RDC_SB_1F_VAV1505 | VAV | Included | SC. Comp Office 2 S-1123 |  |  |  | South Building/FF/FF-5 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV1506 | VAV | Included | SC. Comp Office 3 S-1124 |  |  |  | South Building/FF/FF-5 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV1507 | VAV | Included | Workstation S-1124A |  |  |  | South Building/FF/FF-7 | CHECK | the dot sits on the area's left-hand edge
RDC_SB_1F_VAV1508 | VAV | Included | Scientific Comp. Office 1 S-1125 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1509 | VAV | Included | Scientific Comp. Office S-1126 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1510 | VAV | Included | ALT Office 2 S-1127 |  |  |  | South Building/FF/FF-7 | OPEN | the dot sits between ALT Office 2 S-0127 and Scientific Comp. Office1 S-0125 and could be either
RDC_SB_1F_VAV1511 | VAV | Included | ALT Office 3 S-1128 |  |  |  | South Building/FF/FF-7 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV1512 | VAV | Included | Workstation S-1128A |  |  |  | South Building/FF/FF-7 | CHECK | the dot is in the open workstation area
RDC_SB_1F_VAV1513 | VAV | Included | ALT Office 1 S-1129 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1514 | VAV | Included | ALT Office S-1130 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1515 | VAV | Included | Distub. Syst Office 1 S-1131 |  |  |  | South Building/FF/FF-7 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV1516 | VAV | Included | Distub. Syst Office S-1132 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1517 | VAV | Included | Workstation S-1132A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1518 | VAV | Included | Distub. Syst Office S-1133 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1519 | VAV | Included | Distub. Syst Office S-1134 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1520 | VAV | Not Included | Data Analytic Office S-1135 |  |  |  | South Building/FF/FF-7 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV1521 | VAV | Not Included | Data Analytic Office S-1136 |  |  |  | South Building/FF/FF-7 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV1522 | VAV | Included | Workstation S-1136A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1523 | VAV | Not Included | Data Analytic Office S-1137 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1524 | VAV | Not Included | Data Analytic Office S-1138 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1525 | VAV | Included | Office S-1139 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1526 | VAV | Included | Office S-1140 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1527 | VAV | Included | Conference Room S-1141 |  |  |  | South Building/FF/FF-7 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV1528 | VAV | Included | Office S-1142 |  |  |  | South Building/FF/FF-7 | DIFF | the screen puts SB-VAV1528 in Workstation S-0136A; the register says Office S-1142 - the dot is below and left of the workstation name
RDC_SB_1F_VAV1529 | VAV | Included | Office S-1144 |  |  |  | South Building/FF/FF-7 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV1530 | VAV | Included | Office S-1145 |  |  |  | South Building/FF/FF-7 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV1531 | VAV | Included | Office S-1146 |  |  |  | South Building/FF/FF-7 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV1532 | VAV | Included | Workstation S-1146A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1533 | VAV | Included | Office S-1148 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1534 | VAV | Included | Office S-1149 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1536 | VAV | Included | Office S-1150 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1539 | VAV | Included | Video Conf. Room S-1154 |  |  |  | South Building/FF/FF-5 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV1540 | VAV | Included | Conf S-1159 |  |  |  | South Building/FF/FF-5 | CONVENTION | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV1542 | VAV | Included | Office S-1182 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1543 | VAV | Included | Workstation S-1182A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1544 | VAV | Included | Office S-1182C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1545 | VAV | Included | Office S-1182D |  |  |  | South Building/FF/FF-5 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV1546 | VAV | Included | Office S-1182E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1547 | VAV | Included | Office S-1182F |  |  |  | South Building/FF/FF-5 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV1548 | VAV | Included | Office S-1183 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1549 | VAV | Included | Workstation S-1183A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1550 | VAV | Included | Office S-1184 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1551 | VAV | Included | Social Comp Office S-1185 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1552 | VAV | Included | Social Comp Office S-1186 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1553 | VAV | Included | Workstation S-1186A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1554 | VAV | Included | Social Comp Office S-1187 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1555 | VAV | Included | Social Comp Office S-1188 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1556 | VAV | Included | Cyber Sec Office S-1189 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1557 | VAV | Included | Cyber Sec Office S-1190 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1558 | VAV | Included | Workstation S-1190A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1559 | VAV | Included | Office S-1191 |  |  |  | South Building/FF/FF-7 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV1560 | VAV | Included | Cyber Sec Office S-1192 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV1561 | VAV | Included | Cyber Sec Office S-1193 |  |  |  | South Building/FF/FF-7 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV2501 | VAV | Included | Lobby S-1201 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2502 | VAV | Included | Lobby S-1202 |  |  |  | South Building/FF/FF-2 | OPEN | the walk ended above the building outline, outside the plan
RDC_SB_1F_VAV2503 | VAV | Included | Lobby S-1202 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2504 | VAV | Included | Lobby S-1202 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2505 | VAV | Included | Lobby S-1202 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2506 | VAV | Included | Lobby S-1202 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2508 | VAV | Included | Female Prayer S-1207 |  |  |  | South Building/FF/FF-2 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV2509 | VAV | Included | Open Plan S-1210 |  |  |  | South Building/FF/FF-2 | CHECK | the dot sits on the area's left-hand edge
RDC_SB_1F_VAV2510 | VAV | Not Included | Exc. Dir. Office S-1211 |  |  |  | South Building/FF/FF-2 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV2511 | VAV | Included | Office S-1212 |  |  |  | South Building/FF/FF-2 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV2512 | VAV | Included | Office S-1213 |  |  |  | South Building/FF/FF-2 | OPEN | as SB-VAV2513 - the dot is on the S-0213 / S-0214 wall
RDC_SB_1F_VAV2513 | VAV | Included | Office S-1214 |  |  |  | South Building/FF/FF-2 | OPEN | the dot sits on the wall between Office S-0213 and Office S-0214 and could be either
RDC_SB_1F_VAV2514 | VAV | Included | Office S-1215 |  |  |  | South Building/FF/FF-2 | CHECK | the dot is inside the room near its right wall
RDC_SB_1F_VAV2515 | VAV | Included | Office S-1216 |  |  |  | South Building/FF/FF-2 | OPEN | the dot sits on the wall between Office S-0215 and Office S-0216 and could be either
RDC_SB_1F_VAV2516 | VAV | Not Included | Executive Director Office S-1217 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2517 | VAV | Not Included | Executive Director Office S-1218 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2518 | VAV | Included | Office S-1219 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2519 | VAV | Included | Office S-1220 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2520 | VAV | Included | Office S-1221 |  |  |  | South Building/FF/FF-3 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV2521 | VAV | Included | Office S-1222 |  |  |  | South Building/FF/FF-3 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV2522 | VAV | Included | Office S-1223 |  |  |  | South Building/FF/FF-3 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV2523 | VAV | Included | Office S-1224 |  |  |  | South Building/FF/FF-3 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV2524 | VAV | Included | Office S-1225 |  |  |  | South Building/FF/FF-3 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV2525 | VAV | Included | Office S-1226 |  |  |  | South Building/FF/FF-3 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV2526 | VAV | Included | Open Plan S-1227 |  |  |  | South Building/FF/FF-3 | CHECK | the dot is in the open plan area near its left edge
RDC_SB_1F_VAV2527 | VAV | Not Included | Director Office S-1228 |  |  |  | South Building/FF/FF-3 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV2528 | VAV | Not Included | Director Office S-1230 |  |  |  | South Building/FF/FF-3 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV2529 | VAV | Included | Office S-1231 |  |  |  | South Building/FF/FF-3 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV2530 | VAV | Included | Office S-1232 |  |  |  | South Building/FF/FF-3 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV2531 | VAV | Not Included | Director Office S-1241 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2532 | VAV | Included | Office S-1242 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2533 | VAV | Included | Cooridor S-1246 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2534 | VAV | Included | Meeting Room S-1247 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2535 | VAV | Included | Store S-1248 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2536 | VAV | Not Included | Normal Elec. S-1251 |  |  | Mech. Chasing S-1249 | South Building/FF/FF-3 | DIFF | the screen puts SB-VAV2536 in Mech. Chasing S-0249; the register says Normal Elec. S-1251 - the dot sits on the room's left-hand wall
RDC_SB_1F_VAV2538 | VAV | Included | Office S-1257 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2539 | VAV | Included | Office S-1257B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2540 | VAV | Not Included | Executive Director S-1260 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2541 | VAV | Included | Assistant S-1261 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2542 | VAV | Included | Open Plan S-1263 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2543 | VAV | Included | Office S-1264 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2544 | VAV | Included | Office S-1265 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2545 | VAV | Included | Office S-1266 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2546 | VAV | Included | Office S-1267 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2547 | VAV | Included | Office S-1268 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV2548 | VAV | Included | Office S-1269 |  |  |  | South Building/FF/FF-2 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV2549 | VAV | Included | Office S-1270 |  |  |  | South Building/FF/FF-2 | CHECK | a second dot beside SB-VAV2548
RDC_SB_1F_VAV2550 | VAV | Included | Office S-1271 |  |  |  | South Building/FF/FF-2 | OPEN | as SB-VAV2513 - the dot is on the S-0213 / S-0214 wall
RDC_SB_1F_VAV2551 | VAV | Included | Meeting Room S-1272 |  |  |  | South Building/FF/FF-2 | OPEN | the dot sits between Vestibule S-0206 and Female Ablution S-0208 and could be either
RDC_SB_1F_VAV2552 | VAV | Included | Vestibule S-1273 |  |  | FPC S-1277 | South Building/FF/FF-2 | DIFF | the screen puts SB-VAV2552 in FPC S-0277; the register says Vestibule S-1273 - the dot is inside the room near its left wall
RDC_SB_1F_VAV2553 | VAV | Included | Male Prayer S-1278 |  |  |  | South Building/FF/FF-2 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV3504 | VAV | Included | Open Plan S-1229 |  |  |  | South Building/FF/FF-1 | CHECK | the dot is in the open plan area near its left edge
RDC_SB_1F_VAV3505 | VAV | Included | Open Plan S-1229 |  |  |  | South Building/FF/FF-1 | CHECK | the dot is in the open plan area near its right edge
RDC_SB_1F_VAV3506 | VAV | Included | Office S-1233 |  |  |  | South Building/FF/FF-1 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV3507 | VAV | Included | Office S-1234 |  |  |  | South Building/FF/FF-1 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV3508 | VAV | Included | Office S-1235 |  |  |  | South Building/FF/FF-1 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV3509 | VAV | Not Included | Policy Director Office S-1237 |  |  |  | South Building/FF/FF-1 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV3510 | VAV | Not Included | Policy Executive Director Office S-1240 |  |  |  | South Building/FF/FF-1 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV3511 | VAV | Included | Waiting Area S-1292 |  |  |  | South Building/FF/FF-1 | OPEN | the dot lands between VP R&D S-0285 and Meeting Room S-0288 in floor the screen does not name
RDC_SB_1F_VAV3512 | VAV | Included | Pantry S-1282 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV3513 | VAV | Included | Office S-1283 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV3514 | VAV | Included | Office S-1284 |  |  |  | South Building/FF/FF-1 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV3515 | VAV | Not Included | S-1285 VP R&D |  |  |  | South Building/FF/FF-1 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_1F_VAV3516 | VAV | Included | Meeting Room S-1288 |  |  |  | South Building/FF/FF-1 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV3517 | VAV | Included | Dressing Room S-1290 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV3518 | VAV | Included | Waiting Area S-1292 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV3519 | VAV | Included | Open Plan S-1293 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV3520 | VAV | Included | Office S-1294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV3521 | VAV | Included | Office S-1295 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV3522 | VAV | Included | Conference Room S-1296 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_VAV3523 | VAV | Included | Office S-1299 |  |  |  | South Building/FF/FF-1 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_1F_VAV3524 | VAV | Not Included | Normal Elec. S-1238 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0001 | VAV | Included | Vestibule S-0101 |  |  | Vestbule S-0101 | South Building/GF/GF-4 | SAME
RDC_SB_GF_VAV0002 | VAV | Included | Main Lobby S-0102 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0003 | VAV | Included | Entrance Lobby S-0102 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0007 | VAV | Included | Conference S-0109 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0008 | VAV | Not Included | Computer Research Lab 3 S-0110 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0009 | VAV | Included | Phone Booth S-0111 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0010 | VAV | Included | Phone Booth S-0112 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0011 | VAV | Included | Conference S-0113 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0012 | VAV | Not Included | Computer Research Lab 2 S-0114 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0013 | VAV | Included | Phone Booth S-0115 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0014 | VAV | Included | Phone Booth S-0116 |  |  |  | South Building/GF/GF-5 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_GF_VAV0016 | VAV | Included | Conference S-0118 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0017 | VAV | Not Included | Computer Research Lab 1 S-0119 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0018 | VAV | Included | Restaurant S-0123 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0019 | VAV | Included | Restaurant S-0123 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV0025 | VAV | Included | Alt Recording Sound S-0135 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV1003_VEV1002 | VEV | Not Included | NOC Lab S-0140A |  |  |  | South Building/GF/GF-6 | CHECK | the dot sits just inside the room's upper left corner
RDC_SB_GF_VAV1004 | VAV | Included | Corridor S-0137 / S-0143 |  |  | Dedicated Cyber SOC/NOC Lab S-0141 | South Building/GF/GF-6 | DIFF | the screen puts SB-VAV1004 in Dedicated Cyber SOC/NOC Lab S-0141; the register says Corridor S-0137 / S-0143 - the dot sits on the room's left-hand wall
RDC_SB_GF_VAV1008 | VAV | Included | Cyber Embedded Sys. S-0146 |  |  |  | South Building/GF/GF-6 | OPEN | the dot sits exactly on the corner where Refrig Waste S-0149 and Cyber Embeded Dist System Electrical Lab S-0146 meet and could be either
RDC_SB_GF_VAV2002 | VAV | Included | Conference Room S-0207 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2003 | VAV | Included | Multi Purpose Hall S-0208 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2004 | VAV | Included | Multi Purpose Hall S-0208 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2005 | VAV | Included | Technical Open Plan S-0211 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2006 | VAV | Included | Meeting Room S-0212 |  |  |  | South Building/GF/GF-2 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_GF_VAV2007 | VAV | Included | Office S-0213 |  |  | Office S-0213 | South Building/GF/GF-2 | SAME
RDC_SB_GF_VAV2008 | VAV | Included | Office S-0214 |  |  | Office S-0214 | South Building/GF/GF-2 | SAME
RDC_SB_GF_VAV2009 | VAV | Included | Office S-0215 |  |  | Office S-0215 | South Building/GF/GF-2 | SAME
RDC_SB_GF_VAV2010 | VAV | Included | Office S-0216 |  |  | Office S-0216 | South Building/GF/GF-2 | SAME
RDC_SB_GF_VAV2011 | VAV | Included | Office S-0217 |  |  | Office S-0217 | South Building/GF/GF-2 | SAME
RDC_SB_GF_VAV2012 | VAV | Not Included | Director Office S-0218 |  |  | Director Office S-0218 | South Building/GF/GF-2 | SAME
RDC_SB_GF_VAV2013 | VAV | Included | Office S-0219 |  |  | Office S-0219 | South Building/GF/GF-2 | SAME
RDC_SB_GF_VAV2014 | VAV | Included | Office S-0220 |  |  | Office S-0220 | South Building/GF/GF-2 | SAME
RDC_SB_GF_VAV2015 | VAV | Not Included | Director Office S-0221 |  |  | Director Office S-0221 | South Building/GF/GF-2 | SAME
RDC_SB_GF_VAV2016 | VAV | Not Included | Director Office S-0222 |  |  | Director Office S-0222 | South Building/GF/GF-2 | SAME
RDC_SB_GF_VAV2017 | VAV | Included | Meeting Room S-0223 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2018 | VAV | Included | Print Hub S-0225 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2019 | VAV | Included | Office S-0227 |  |  |  | South Building/GF/GF-2 | CHECK | the dot sits below and right of the room, on its boundary
RDC_SB_GF_VAV2020 | VAV | Included | Open Plan S-0228 |  |  |  | South Building/GF/GF-3 | OPEN | as SB-VAV2021 - the dot is on the same unnamed strip, beside Informal Meeting Room S-0231
RDC_SB_GF_VAV2021 | VAV | Included | Open Plan S-0228 |  |  |  | South Building/GF/GF-3 | OPEN | the dot lands on the left edge of the Director Office S-0229 block, in floor between it and Open Plan S-0228 that the screen does not name
RDC_SB_GF_VAV2022 | VAV | Not Included | Director Office S-0229 |  |  |  | South Building/GF/GF-3 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_GF_VAV2023 | VAV | Included | Office S-0230 |  |  |  | South Building/GF/GF-3 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_GF_VAV2024 | VAV | Not Included | Executive Director Office S-0232 |  |  |  | South Building/GF/GF-3 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_GF_VAV2025 | VAV | Not Included | Executive Director Office S-0233 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2026 | VAV | Included | Office S-0234 |  |  |  | South Building/GF/GF-3 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_GF_VAV2027 | VAV | Included | Office S-0235 |  |  |  | South Building/GF/GF-3 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_GF_VAV2028 | VAV | Included | Office S-0236 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2029 | VAV | Included | Waiting Area S-0251 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2030 | VAV | Included | Office S-0259 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2031 | VAV | Included | Office S-0260 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2032 | VAV | Included | Open Plan S-0269 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2033 | VAV | Included | Store S-0275 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2034 | VAV | Included | Meeting Room S-0274 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2035 | VAV | Included | Pantry S-0270 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2036 | VAV | Not Included | Emergency Elec. Room S-0278 |  |  |  | South Building/GF/GF-3 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_GF_VAV2037 | VAV | Included | Men S-0284 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2038 | VAV | Included | Informal Meeting S-0285 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2039 | VAV | Included | Meeting Room S-0286 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2040 | VAV | Included | Open Plan S-0289 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2041 | VAV | Included | Open Plan S-0289 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2042 | VAV | Included | Corridor S-0273 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2043 | VAV | Included | Women S-0281 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2044 | VAV | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2045 | VAV | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2046 | VAV | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV2047 | VAV | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3001 | VAV | Not Included | Director Office S-0237 |  |  | Director Office S-0237 | South Building/GF/GF-1 | SAME
RDC_SB_GF_VAV3002 | VAV | Included | Office S-0238 |  |  |  | South Building/GF/GF-1 | CHECK | the dot is inside the room near its left wall
RDC_SB_GF_VAV3003 | VAV | Included | Office S-0239 |  |  |  | South Building/GF/GF-1 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_GF_VAV3004 | VAV | Included | Office S-0240 |  |  |  | South Building/GF/GF-1 | CHECK | a second dot in the same room
RDC_SB_GF_VAV3005 | VAV | Included | Office S-0241 |  |  |  | South Building/GF/GF-1 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_GF_VAV3006 | VAV | Included | Office S-0242 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3007 | VAV | Not Included | Director Office S-0243 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3008 | VAV | Included | Open Plan S-0244 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3009 | VAV | Included | Open Plan S-0244 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3010 | VAV | Included | Open Plan S-0244 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3011 | VAV | Included | Meeting Room S-0245 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3012 | VAV | Included | Office S-0246 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3013 | VAV | Included | Office S-0247 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3014 | VAV | Included | Office S-0248 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3015 | VAV | Not Included | Security S-0249 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3016 | VAV | Included | Corridor S-0250 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3017 | VAV | Included | Office S-0251 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3018 | VAV | Included | Corridor S-0251 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3019 | VAV | Included | Corridor S-0251 |  |  |  | South Building/GF/GF-1 | CHECK | the dot is in the corridor, which the screen labels only Corridor at that point
RDC_SB_GF_VAV3020 | VAV | Included | Office S-0252 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3021 | VAV | Included | Office S-0252 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3022 | VAV | Included | Office S-0253 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3023 | VAV | Included | Office S-0253 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3024 | VAV | Included | Office S-0254 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3025 | VAV | Included | Office S-0255 |  |  |  | South Building/GF/GF-1 | CHECK | the dot is inside the room near its left wall
RDC_SB_GF_VAV3026 | VAV | Included | Office S-0256 |  |  |  | South Building/GF/GF-1 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_GF_VAV3027 | VAV | Included | Office S-0257 |  |  |  | South Building/GF/GF-1 | CHECK | a second dot in the same room; SB-VAV3002 also reads here
RDC_SB_GF_VAV3028 | VAV | Included | Office S-0258 |  |  |  | South Building/GF/GF-1 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_GF_VAV3029 | VAV | Included | Open Plan S-0261 |  |  |  | South Building/GF/GF-1 | CHECK | the dot is in the open plan area
RDC_SB_GF_VAV3030 | VAV | Included | Open Plan S-0262 |  |  |  | South Building/GF/GF-1 | CHECK | the dot is in the open plan area near its right edge
RDC_SB_GF_VAV3031 | VAV | Not Included | Server S-0264 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3032 | VAV | Included | Open Plan S-0265 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3033 | VAV | Not Included | Emergency Elec. S-0266 |  |  |  | South Building/GF/GF-1 | CHECK | the dot sits above the room name, left of Normal Elec. S-0267
RDC_SB_GF_VAV3034 | VAV | Included | Vestibule S-0293 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3035 | VAV | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3036 | VAV | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3501 | VAV | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3502 | VAV | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_VAV3503 | VAV | Included | Vestibule S-0293 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4510 | VAV | Included | Corridor N-1202A |  |  |  | North Building/FF/FF-1 | DIFF | the screen puts NB-VAV4510 in Conference Room N-1205; the register says Corridor N-1202A
RDC_NB_1F_VAV4515_EV4516 | EV | Not Included | Emergency Electrical Room N-1203 |  |  |  | North Building/FF/FF-1 | OPEN | its leader ends beside the dot NB-VAV4525-EV4526 also walks to, in Conference Room N-1205. One dot serves one unit and nothing on the screen says which of the two owns it
RDC_NB_1F_VAV4520_EV4521 | EV | Not Included | Normal Electrical Room N-1204 |  |  |  | North Building/FF/FF-1 | DIFF | the screen puts NB-VAV4520-EV4521 in Conference Room N-1205; the register says Normal Electrical Room N-1204 - endpoint is inside the room but the walk ran out before a dot
RDC_NB_1F_VAV4525_EV4526 | EV | Included | Conference Room N-1205 |  |  | Conference Room N-1205 | North Building/FF/FF-1 | SAME
RDC_NB_1F_VAV4530_EV4531 | EV | Included | Office N-1206 |  |  | Office N-1206 | North Building/FF/FF-1 | SAME
RDC_NB_1F_VAV4535_EV4536 | EV | Included | Office N-1207 |  |  | Office N-1207 | North Building/FF/FF-1 | SAME
RDC_NB_1F_VAV4540_EV4541 | EV | Included | Office N-1208 |  |  | Office N-1208 | North Building/FF/FF-1 | SAME
RDC_NB_1F_VAV4545_EV4546 | EV | Included | Office N-1209 |  |  | Office N-1209 | North Building/FF/FF-1 | SAME
RDC_NB_1F_VAV4550_EV4551 | EV | Included | Office N-1210 |  |  | Office N-1210 | North Building/FF/FF-1 | SAME
RDC_NB_1F_VAV4555_EV4556 | EV | Included | Confer Room N-1211 |  |  |  | North Building/FF/FF-1 | OPEN | the walk ran out in open floor south of the office range, in no named room
RDC_NB_1F_VAV4560_EV4561 | EV | Included | Office N-1212 |  |  | Office N-1212 | North Building/FF/FF-1 | SAME
RDC_NB_1F_VAV4565_EV4566 | EV | Included | Conference N-1213 |  |  | Storage Room N-1215 | North Building/FF/FF-1 | DIFF | the screen puts NB-VAV4565-EV4566 in Storage Room N-1215; the register says Conference N-1213 - the dot sits on the room's left-hand wall
RDC_NB_1F_VAV4570_EV4571 | EV | Included | Office 04 N-1214 |  |  | Office N-1214 | North Building/FF/FF-1 | SAME
RDC_NB_1F_VAV4575_EV4576 | EV | Included | Storage N-1215 |  |  |  | North Building/FF/FF-1 | OPEN | the endpoint sits on the wall between Corridor N-1202A and Storage Room N-1215 and could be either
RDC_NB_1F_VAV4580 | VAV | Not Included | Photovoltaic Lab N-1216A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4600 | VAV | Not Included | Testing Room N-1216B |  |  |  | North Building/FF/FF-1 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_1F_VAV4601 | VAV | Not Included | Testing Room N-1216B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4620_VEV4621 | VEV | Not Included | EL Shop N-1216C |  |  |  | North Building/FF/FF-1 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_1F_VAV4630_VEV4631 | VEV | Not Included | GIS N-1216D |  |  | GIS N-1216D | North Building/FF/FF-1 | SAME
RDC_NB_1F_VAV4650 | VAV | Included | Breakout N-1225 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4660 | VAV | Included | Expansion Workstation N-1227 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4665 | VAV | Included | Office N-1228 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4670 | VAV | Included | Office N-1229 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4675 | VAV | Included | Office N-1230 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4680 | VAV | Included | Office N-1231 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4685 | VAV | Included | Workstation N-1232 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4690 | VAV | Included | Office N-1233 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4695 | VAV | Included | Office N-1234 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4700 | VAV | Included | Office N-1235 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4705 | VAV | Included | Office N-1236 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4710 | VAV | Included | Workstation N-1237 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4715 | VAV | Included | Office N-1238 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4720 | VAV | Included | Office N-1239 |  |  |  | North Building/FF/FF-1 | DIFF | the screen puts NB-VAV4720 in Work Station N-1237; the register says Office N-1239 - the dot is in the open work station area right of Office N-1239
RDC_NB_1F_VAV4725 | VAV | Included | Office N-1240 |  |  |  | North Building/FF/FF-1 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_1F_VAV4730 | VAV | Included | Office N-1241 |  |  |  | North Building/FF/FF-1 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_1F_VAV4735 | VAV | Included | Workstation N-1242 |  |  | Work Station N-1242 | North Building/FF/FF-1 | SAME
RDC_NB_1F_VAV4740 | VAV | Included | Exp Office N-1243 |  |  | Office N-1244 | North Building/FF/FF-1 | SAME
RDC_NB_1F_VAV4745 | VAV | Included | Office N-1244 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4900P | VAV | Not Included | Normal Electric N-2102 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV4910P | VAV | Not Included | Emergency Electr N-2103 |  |  | Emer. Elec. N-2104 | North Building/SF/SF-1 | DIFF | the screen puts NB-VAV4910P in Emer. Elec. N-2104; the register says Emergency Electr N-2103 - the dot sits just inside the room's lower edge
RDC_NB_1F_VAV5500 | VAV | Included | Lobby N-1101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5501 | VAV | Included | Lobby N-1101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5510_EV5511 | EV | Included | Conference N-1101A |  |  | Conference Room N-1101A | North Building/FF/FF-5 | SAME
RDC_NB_1F_VAV5515_EV5516 | EV | Not Included | Emergency Electrical Room N-1102 |  |  |  | North Building/FF/FF-5 | OPEN | the dot falls in the same angled band and cannot be assigned to a single room
RDC_NB_1F_VAV5520_EV5521 | EV | Included | Conference N-1106 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5525_EV5526 | EV | Included | Conference N-1107 |  |  |  | North Building/FF/FF-5 | DIFF | the screen puts NB-VAV5525-EV5526 in JC N-1118; the register says Conference N-1107 - the dot is inside the round JC N-1118 room but close to its edge
RDC_NB_1F_VAV5535_EV5536 | EV | Included | Conference N-1112 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5540_EV5541 | EV | Not Included | Normal Electrical Room N-1113 |  |  |  | North Building/FF/FF-5 | OPEN | the dot falls in the narrow angled band of small rooms between Normal Elec. N-1113 and Emergency Elec. N-1102; at the size the screen draws them it cannot be assigned to one
RDC_NB_1F_VAV5550_VEV5551 | VEV | Not Included | PCR N-1115A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5560_VEV5561 | VEV | Not Included | PRE-PCR N-1115B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5570 | VAV | Not Included | Met/Prot Lab N-1115C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5571 | VAV | Not Included | Met/Prot Lab N-1115C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5580_VEV5581 | VEV | Not Included | DNA/RNA N-1115D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5590 | VAV | Not Included | Cell Culture N-1115E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5600_VEV5601 | VEV | Included | Library N-1115H |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5610_VEV5611 | VEV | Not Included | Robotics N-1115J |  |  | Cold Room N-1115F | North Building/FF/FF-3 | DIFF | the screen puts NB-VAV5610-VEV5611 in Cold Room N-1115F; the register says Robotics N-1115J - the dot is in open lab floor near the Cold Room N-1115F name; no wall separates it from Robotics N-1115J to its left
RDC_NB_1F_VAV5620_VEV5622 | VEV | Not Included | Sequence Lab N-1115K |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5621_VEV5623 | VEV | Not Included | Sequence Lab N-1115K |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5630_VEV5631 | VEV | Not Included | Genom Med Lab N-1115K1 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5650 | VAV | Included | Office N-1120 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5655_EV5656 | EV | Included | Store N-1120B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5660 | VAV | Included | Office N-1121 |  |  | Office N-1121 | North Building/FF/FF-3 | SAME
RDC_NB_1F_VAV5665 | VAV | Included | Office N-1122 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5670 | VAV | Included | Office N-1123 |  |  | Office N-1123 | North Building/FF/FF-3 | SAME
RDC_NB_1F_VAV5675 | VAV | Included | Office N-1124 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5680 | VAV | Included | Office N-1125 |  |  | Office N-1125 | North Building/FF/FF-3 | SAME
RDC_NB_1F_VAV5685 | VAV | Included | Corridor N-1126 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5690 | VAV | Included | Office N-1127 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5695 | VAV | Included | Office N-1128 |  |  | Office N-1128 | North Building/FF/FF-3 | SAME
RDC_NB_1F_VAV5700 | VAV | Included | Office N-1129 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5705 | VAV | Included | Office N-1130 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5710 | VAV | Included | Office N-1131 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5715_EV5716 | EV | Included | Conf Rm N-1132 |  |  | Conf. Rm N-1132 | North Building/FF/FF-3 | SAME
RDC_NB_1F_VAV5730_EV5731 | EV | Included | Store N-1135 |  |  | Store N-1135 | North Building/FF/FF-3 | SAME
RDC_NB_1F_VAV5735_EV5736 | EV | Not Included | Normal Elec. N-1136 |  |  |  | North Building/FF/FF-3 | DIFF | the screen puts NB-VAV5735-EV5736 in Corridor N-1138; the register says Normal Elec. N-1136
RDC_NB_1F_VAV5740_EV5741 | EV | Not Included | Emer. Elec. N-1137 |  |  | Emer. Elec. N-1137 | North Building/FF/FF-3 | SAME
RDC_NB_1F_VAV5745 | VAV | Included | Corridor N-1138 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5760_EV5761 | EV | Included | Conf N-1143 |  |  |  | North Building/FF/FF-4 | CONVENTION | the dot sits on the room's right-hand wall
RDC_NB_1F_VAV5770_VEV5771 | VEV | Not Included | Histology N-1144A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5780_VEV5781 | VEV | Not Included | Culture & Gel Rm N-1144B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5790 | VAV | Not Included | Shafallah N-1144C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5792_VEV5793 | VEV | Not Included | Sample Accession N-1144C1 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5794_VEV5795A | VAV | Included | Storage and Archives N-1144C2 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5800_VEV5801 | VEV | Not Included | Pre-PCR N-1144D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5810 | VAV | Not Included | Nano Lab N-1144E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5814 | VAV | Not Included | Nano Lab N-1144E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5835_EV5836 | EV | Included | P/C/S Pantry N-1146 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5840 | VAV | Included | Corridor N-1150 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5845 | VAV | Included | Reception N-1151 |  |  |  | North Building/FF/FF-5 | CHECK | the dot is in open floor carrying the Reception Area N-1151 name
RDC_NB_1F_VAV5850 | VAV | Included | Office 04 N-1151A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5855 | VAV | Included | Office 04 N-1152 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5860 | VAV | Included | Office N-1154 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5865 | VAV | Included | Office N-1155 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5870 | VAV | Included | Exp Office N-1156 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5875 | VAV | Included | Office N-1157 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5880 | VAV | Included | Office N-1158 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5885 | VAV | Included | Office N-1159 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5890 | VAV | Included | Workstation N-1160 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5895 | VAV | Included | Office N-1161 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5900 | VAV | Included | Office N-1162 |  |  |  | North Building/FF/FF-4 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_1F_VAV5905 | VAV | Included | Office N-1163 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5910 | VAV | Included | Office N-1164 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5915 | VAV | Included | Office N-1167 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5920 | VAV | Included | Workstation N-1168 |  |  |  | North Building/FF/FF-4 | CONVENTION | the dot is in the open Work Station N-168 area near its lower edge
RDC_NB_1F_VAV5925 | VAV | Included | Office N-1169 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5930 | VAV | Included | Office N-1170 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5930P | VAV | Not Included | Normal Elec. N-2105 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5935 | VAV | Included | Office N-1166 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5940 | VAV | Included | Workstation N-1165 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV5940P | VAV | Not Included | Emer. Elec. N-2106 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6505_EV6506 | EV | Included | Conference N-1302 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6510_EV6511 | EV | Included | Conference N-1303 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6525_EV6526 | EV | Not Included | Normal Electrical Room N-1310 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6530_VEV6531 | VEV | Not Included | AAV N-1316A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6540 | VAV | Not Included | Tissure Culture 1 N-1316B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6550 | VAV | Not Included | Gene Therapy Lab N-1316C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6551 | VAV | Not Included | Gene Therapy Lab N-1316C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6560_VEV6561 | VEV | Not Included | TC2 N-1316D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6570_VEV6571 | VEV | Included | STORE ROOM N-1316E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6590_VEV6591 | VEV | Not Included | LENTIV N-1316G |  |  |  | North Building/FF/FF-7 | OPEN | the dot lands in the open lab band below Corridor N-315 at a point the screen gives no room name; Gene Therapy Lab N-316C and Analytical Core N-316H are either side of it
RDC_NB_1F_VAV6600_VEV6601 | VEV | Not Included | Analytical Core N-1316H |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6610_VEV6611 | VEV | Not Included | Microscope Room N-1316H |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6620_VEV6621 | VEV | Not Included | Mscopy1 N-1316K |  |  |  | North Building/FF/FF-7 | CONVENTION | the dot sits on the wall between Mscope Room N-316J and N-316K, just inside K
RDC_NB_1F_VAV6630A | VAV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6630B | VAV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6631A | VAV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6631B | VAV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6650 | VAV | Included | Office N-1319 |  |  |  | North Building/FF/FF-6 | CHECK | the dot sits on the room's left-hand wall
RDC_NB_1F_VAV6655 | VAV | Included | Office N-1320 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6660 | VAV | Included | Workstation N-1321 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6665 | VAV | Included | Office N-1322 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6670 | VAV | Included | Office N-1323 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6675 | VAV | Included | Workstation N-1324 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6680 | VAV | Included | Office N-1325 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6685 | VAV | Included | Office N-1326 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6690 | VAV | Included | Exp. Workstation N-1327 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6695 | VAV | Included | Office N-1328 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6700_EV6701 | EV | Not Included | NORMAL ELEC. N-1329 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6705 | VAV | Included | Office N-1330 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6710 | VAV | Included | Office N-1331 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6715 | VAV | Included | Office N-1332 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6720 | VAV | Included | Corridor N-1335 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6725_EV6726 | EV | Not Included | Emer. Elec. N-1336 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6750 | VAV | Not Included | Tissue Culture 1 N-1345A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6760 | VAV | Not Included | Diabetes Lab N-1345B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6761 | VAV | Not Included | Diabetes Lab N-1345B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6800_VEV6801 | VEV | Not Included | Tissue Culture 3 N-1345D |  |  |  | North Building/FF/FF-8 | CONVENTION | as NB-VEV6751 - the dot is on the corridor wall at the top of the room
RDC_NB_1F_VAV6810_VEV6811 | VEV | Not Included | Calc Imaging N-1345E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6820_VEV6821 | VEV | Not Included | Electro Physics N-1345F |  |  |  | North Building/FF/FF-8 | CHECK | as NB-VEV6751 - the dot is on the corridor wall at the top of the room
RDC_NB_1F_VAV6830_VEV6831 | VEV | Not Included | Shared Cold Lab N-1345G |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6840_VEV6841 | VEV | Not Included | Bacterlgy Lab N-1345H |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6850 | VAV | Not Included | Bio-Med Chem Lab 2 N-1345J |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6851 | VAV | Not Included | Bio-Med Chem Lab 2 N-1345J |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6870_EV6871 | EV | Not Included | Emergency Electrical Room N-1353 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6880 | VAV | Included | Reception+N-1355C Storage N-1355 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6885 | VAV | Included | Exp Office N-1355A |  |  |  | North Building/FF/FF-5 | OPEN | the dot sits between Exp. Office N-355A and Conf Rm N-355B and could be either
RDC_NB_1F_VAV6890_EV6891 | EV | Included | Conference Room N-1355B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6895 | VAV | Included | Office 04 N-1356 |  |  |  | North Building/FF/FF-5 | OPEN | the dot falls in the angled band of small rooms on the east wing and cannot be assigned to one
RDC_NB_1F_VAV6900 | VAV | Included | Office N-1357 |  |  | Office N-357 | North Building/FF/FF-9 | SAME
RDC_NB_1F_VAV6905 | VAV | Included | Open Plan N-1358 |  |  |  | North Building/FF/FF-9 | CHECK | the dot is just below the Open Plan N-358 area with Office N-357 to its right
RDC_NB_1F_VAV6910 | VAV | Included | Office N-1359 |  |  | Office N-359 | North Building/FF/FF-9 | SAME
RDC_NB_1F_VAV6915 | VAV | Included | Office N-1360 |  |  | Office N-360 | North Building/FF/FF-9 | SAME
RDC_NB_1F_VAV6920 | VAV | Included | Office N-1360B |  |  | Office N-360B | North Building/FF/FF-9 | SAME
RDC_NB_1F_VAV6925 | VAV | Included | Office N-1361 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6930 | VAV | Included | Office N-1362 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6935 | VAV | Included | Workstation N-1363 |  |  |  | North Building/FF/FF-9 | CONVENTION | the dot sits on the room's right-hand edge
RDC_NB_1F_VAV6940 | VAV | Included | Office N-1364 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6945 | VAV | Included | Office N-1365 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6950 | VAV | Included | Office N-1366 |  |  |  | North Building/FF/FF-9 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_1F_VAV6955 | VAV | Included | Office N-1367 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6960 | VAV | Included | Workstation N-1368 |  |  |  | North Building/FF/FF-9 | CONVENTION
RDC_NB_1F_VAV6965 | VAV | Included | Office N-1369 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6967 | VAV | Included | Office N-1370 |  |  |  | North Building/FF/FF-9 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_1F_VAV6968 | VAV | Included | Workstation N-1371 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6970_EV6971 | EV | Included | PANTRY N-1372 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6972 | VAV | Included | Office N-1374 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6974 | VAV | Included | Office N-1375 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6976 | VAV | Included | Office N-1376 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6978 | VAV | Included | Office N-1377 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6979P | VAV | Not Included | Normal Elec. N-2107 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV6980P | VAV | Not Included | Emer. Elec. N-2108 |  |  | IDF N-2110 | North Building/SF/SF-4 | DIFF | the screen puts NB-VAV6980P in IDF N-2110; the register says Emer. Elec. N-2108 - the dot sits on the room's left-hand wall
RDC_NB_1F_VAV7510_VEV7511 | VEV | Not Included | TC1 N-1404A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7530_VEV7532 | VEV | Not Included | Cell Bio N-1404C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7531_VEV7533 | VEV | Not Included | Cell Bio N-1404C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7540_VEV7541 | VEV | Not Included | Shared Eq Rm N-1404D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7550_VEV7551 | VEV | Not Included | TC2 N-1404E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7560_VEV7561 | VEV | Not Included | Imaging N-1404F |  |  | Imaging N-404F | North Building/FF/FF-10 | SAME
RDC_NB_1F_VAV7570_VEV7571 | VEV | Not Included | Cell Bio Lab2 N-1404G |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7580_VEV7581 | VEV | Not Included | TC3 N-1404H |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7600_VEV7601 | VEV | Not Included | Cell Bio Lab3 N-1404K |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7620 | VAV | Included | Office N-1415 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7625 | VAV | Included | Office N-1416 |  |  |  | North Building/FF/FF-10 | CHECK | the dot sits on the room's lower wall
RDC_NB_1F_VAV7630 | VAV | Included | Office 05 - 2 WKS- N-1407 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7635 | VAV | Included | Office N-1418 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7640 | VAV | Included | Office N-1419 |  |  |  | North Building/FF/FF-10 | CHECK | the dot sits on the room's upper wall
RDC_NB_1F_VAV7645 | VAV | Included | Exp. Workstation N-1420 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7650 | VAV | Included | Office N-1421 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7655 | VAV | Included | Office N-1422 |  |  |  | North Building/FF/FF-10 | OPEN | the dot sits on the wall between Office N-421 and Office N-422 and could be either
RDC_NB_1F_VAV7660 | VAV | Included | Office 05 - 2 WKS- N-1401 |  |  | Workstation N-1423 | North Building/FF/FF-10 | DIFF | the screen puts NB-VAV7660 in Workstation N-423; the register says Office 05 - 2 WKS- N-1401
RDC_NB_1F_VAV7665_EV7666 | EV | Not Included | Normal Elec. N-1425 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7670 | VAV | Included | Office N-1426 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7675 | VAV | Included | Office N-1428 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7680_EV7681 | EV | Included | Conf N-1429 |  |  |  | North Building/FF/FF-10 | CONVENTION
RDC_NB_1F_VAV7685 | VAV | Included | Office N-1433 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7690 | VAV | Included | Office N-1435 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7695 | VAV | Included | Office N-1437 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7700_EV7701 | EV | Not Included | Emer. Elec. N-1438 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7705 | VAV | Included | Office 05 - 24 WKS + N-1441 Room N-1442 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7710 | VAV | Included | Workstation N-1442 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7730_VEV7731 | VEV | Not Included | Microscope 2 N-1450A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7740_VEV7741 | VEV | Not Included | LN2 Stor N-1450B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7750_VEV7751 | VEV | Not Included | Flow Cyto N-1450C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7770_VEV7771 | VEV | Not Included | Qurnt N-1450E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7780_VEV7781 | VEV | Not Included | iPS-TC N-1450F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7800_VEV7801 | VEV | Not Included | IPS TISSUE CULTURE N-1450J |  |  | IPS Tissue Culture N-450J | North Building/FF/FF-11 | SAME
RDC_NB_1F_VAV7810_VEV7811 | VEV | Not Included | TC1 N-1450L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7820_VEV7822 | VEV | Not Included | STEM/PCR Open Lab N-1450M |  |  |  | North Building/FF/FF-11 | OPEN | the dot lands in the gap between TC1 N-450L and TC2 N-450N, in floor the screen does not name
RDC_NB_1F_VAV7821_VEV7823 | VEV | Not Included | STEM/PCR Open Lab N-1450M |  |  | STEM/PCR Open Lab N-450M | North Building/FF/FF-11 | SAME
RDC_NB_1F_VAV7830_VEV7831 | VEV | Not Included | TC2 N-1450N |  |  |  | North Building/FF/FF-11 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_1F_VAV7840_EV7841 | EV | Included | Conf N-1458 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7845_EV7846 | EV | Included | Conf N-1459 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7850 | VAV | Included | Office N-1459A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7860 | VAV | Included | Exp. Workstation N-1461 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7865 | VAV | Included | Workstation N-1461A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7870 | VAV | Included | Office N-1462 |  |  |  | North Building/FF/FF-11 | CHECK | the dot sits on the room's left-hand wall
RDC_NB_1F_VAV7875 | VAV | Included | Office N-1463 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7880 | VAV | Included | Office N-1464 |  |  |  | North Building/FF/FF-11 | CHECK | the dot sits inside the room near its right wall
RDC_NB_1F_VAV7885 | VAV | Included | Office N-1465 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7890 | VAV | Included | Workstation N-1466 |  |  |  | North Building/FF/FF-11 | CONVENTION | the dot sits on the room's right-hand edge
RDC_NB_1F_VAV7895 | VAV | Included | Office N-1467 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7900 | VAV | Included | Office N-1468 |  |  |  | North Building/FF/FF-11 | CHECK | the dot sits between Office N-1468 and Office N-470 with no wall drawn at that point
RDC_NB_1F_VAV7905 | VAV | Included | Office N-1469 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7910 | VAV | Included | Office N-1470 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7915 | VAV | Included | Workstation N-1471 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7920 | VAV | Included | Office N-1472 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7925 | VAV | Included | Office N-1473 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7930 | VAV | Included | Office N-1474 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7935 | VAV | Included | Office N-1475 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7940 | VAV | Included | Workstation N-1476 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7945 | VAV | Included | Office N-1477 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7950 | VAV | Included | Office N-1478 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7955 | VAV | Included | Office N-1479 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7960 | VAV | Included | Office N-1480 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7975P | VAV | Not Included | Normal Elec. N-2111 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VAV7980P | VAV | Not Included | Emer. Elec. N-2112 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU4910 | FCU | Included | Stair 1 N-1ST01 |  |  |  | North Building/FF/FF-1 | OPEN | as NB-FCU4916 - same unnamed area beside Stair 1 N-1ST01
RDC_NB_1F_FCU4914 | FCU | Not Included | Mech/ FPC N- L1 A2.1 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU4915 | FCU | Not Included | MDF N-1201 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU4916 | FCU | Included | Stair 1 N-1ST01 |  |  |  | North Building/FF/FF-1 | OPEN | endpoint falls between the Stair 1 N-1ST01 label and the stair graphic; the room polygon there is not drawn closed
RDC_NB_1F_FCU4917 | FCU | Included | Stair N-1ST02 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU5983 | FCU | Not Included | IDF N-1140 |  |  |  | North Building/FF/FF-3 | CHECK | the dot sits close to the JC N-1139 / IDF N-1140 wall
RDC_NB_1F_FCU5984 | FCU | Not Included | ROBOTICS N-115J |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU5985 | FCU | Included | Corridor N-1142 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU5986 | FCU | Included | Corridor N-1142 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU5987 | FCU | Included | Stair 3 N-L1 A2.3 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU5993 | FCU | Included | Conference Room N-L0 A2.2 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU5994 | FCU | Included | Conference Room N-L0 A2.2 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU6988 | FCU | Included | Service Corridor N-1337 |  |  | Service Corridor N-337 | North Building/FF/FF-8 | SAME
RDC_NB_1F_FCU6989 | FCU | Included | Service Corridor N-1337 |  |  | Service Corridor N-337 | North Building/FF/FF-8 | SAME
RDC_NB_1F_FCU6990 | FCU | Not Included | Mech/ FPC N-L1 A2.3 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU6991 | FCU | Not Included | Mech/ FPC N-L1 A2.3 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU6992 | FCU | Included | Stair 4 N-L1 A2.3 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU7790 | FCU | Included | Stair 6 N-1ST06 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU7984 | FCU | Included | Stair 6 N-1ST06 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU7985 | FCU | Not Included | IDF N-1424 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU7986 | FCU | Not Included | IDF N-1424 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU7987 | FCU | Included | Service Corridor N-1446 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU7988 | FCU | Included | Service Corridor N-1446 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU7989 | FCU | Included | Stair 5 N-1ST05 |  |  |  | North Building/FF/FF-10 | OPEN | the dot lands in the unnamed lobby strip west of Stair 5 N-0ST05
RDC_NB_2F_FCU4918 | FCU | Not Included | IDF N-2104 |  |  |  | North Building/SF/SF-2 | CHECK | the dot sits on the room's left-hand wall
RDC_NB_2F_FCU4919 | FCU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-2 | OPEN | as NB-AHU-8513 - the penthouse space carries no room name
RDC_NB_2F_FCU5988 | FCU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-2 | OPEN | as NB-AHU-8513 - the penthouse space carries no room name
RDC_NB_2F_FCU5989 | FCU | Included | Stair 2 N-2ST02 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_FCU5990 | FCU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-2 | OPEN | as NB-AHU-8513 - the penthouse space carries no room name
RDC_NB_2F_FCU6993 | FCU | Not Included | Mechanical (AHU 8516) |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_FCU6994 | FCU | Not Included | Normal Elec. N-2105 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_FCU6995 | FCU | Not Included | IDF N-2110 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_FCU6996 | FCU | Not Included | IDF N-2110 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_FCU7991 | FCU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-3 | OPEN | as NB-ERU8537 - the penthouse space carries no room name
RDC_NB_2F_FCU7992 | FCU | Not Included | NORTH BUILDING PENT HOUSE N-2101 |  |  |  | North Building/SF/SF-3 | OPEN | as NB-ERU8537 - the penthouse space carries no room name
RDC_NB_GF_FCU4911 | FCU | Not Included | MDF Room N-0206A |  |  |  | North Building/GF/GF-4 | CHECK | this screen is a second view of the same area as North Building/GF/GF-3; the dot sits on the room's left-hand wall
RDC_NB_GF_FCU4912 | FCU | Not Included | MDF Room N-0206A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU4913 | FCU | Included | Store N-0201 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU4920 | FCU | Not Included | Emergency Electrical Landing Room N-0205 |  |  |  | North Building/GF/GF-2 | OPEN | no leader could be followed away from the widget
RDC_NB_GF_FCU5980 | FCU | Not Included | Serv Core N-0136 |  |  |  | North Building/GF/GF-5 | CHECK | the dot is in the open Serv Core N-0136 band
RDC_NB_GF_FCU5981 | FCU | Not Included | Serv Core N-0136 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU5982 | FCU | Included | Stair 3 N-OST03 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU5991 | FCU | Included | Vestibule N-0103 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU5992 | FCU | Included | Vestibule N-0102 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU6981 | FCU | Not Included | IDF N-0133 |  |  |  | North Building/GF/GF-5 | CHECK | a second dot beside NB-FCU6982, same wall
RDC_NB_GF_FCU6982 | FCU | Not Included | Mech/FPC N-0128 |  |  | IDF N-0133 | North Building/GF/GF-5 | DIFF | the screen puts NB-FCU6982 in IDF N-0133; the register says Mech/FPC N-0128 - the dot sits just outside the room's left wall
RDC_NB_GF_FCU6983 | FCU | Included | Service Corridor N-0344 |  |  | Service Corridor N-0344 | North Building/GF/GF-9 | SAME
RDC_NB_GF_FCU6984 | FCU | Included | Service Corridor N-0344 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU6985 | FCU | Not Included | IDF N-0311 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU6986 | FCU | Not Included | IDF N-0311 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU6987 | FCU | Included | Stair 4 N-0ST04 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU7981 | FCU | Not Included | SURF ANALYSIS LAB N-0404F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU7982 | FCU | Not Included | Mech PFC N-0434 |  |  |  | North Building/GF/GF-10 | OPEN | the dot lands below Normal Elec. Room N-0420 and right of IDF N-0419 in floor the screen does not name
RDC_NB_GF_FCU7983 | FCU | Included | Stair 5 N-0ST05 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_SB_Walkway_FCU9001 | FCU | Included | Pedestrian Walkway between North & South Buildings |  |  | Pedestrian Walkway B/W North & South | South Building/WALKWAY/WW-1 | SAME
RDC_NB_SB_Walkway_FCU9002 | FCU | Included | Pedestrian Walkway between North & South Buildings |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_SB_Walkway_FCU9003 | FCU | Included | Pedestrian Walkway between North & South Buildings |  |  | Pedestrian Walkway B/W North & South | South Building/WALKWAY/WW-1 | SAME
RDC_NB_SB_Walkway_FCU9004 | FCU | Included | Pedestrian Walkway between North & South Buildings |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_SB_Walkway_FCU9005 | FCU | Included | Pedestrian Walkway between North & South Buildings |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_FCU0501 | FCU | Included | STAIR-02 S-1 ST02 |  |  |  | South Building/FF/FF-4 | OPEN | the walk ended in blank space west of the Stair 2 S-ST02 wall, outside any drawn room
RDC_SB_1F_FCU0502 | FCU | Not Included | UPS ROOM S-1107D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_FCU0503 | FCU | Not Included | UPS ROOM S-1107D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_FCU1501 | FCU | Not Included | IDF ROOM S-1156 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_FCU1502 | FCU | Not Included | IDF ROOM S-1156 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_FCU1503 | FCU | Included | STAIR-01 1ST01 |  |  |  | South Building/FF/FF-7 | OPEN | the dot sits between Stair S-ST01 and Conference Room S-0141 and could be either
RDC_SB_1F_FCU2501 | FCU | Included | STAIR-03 1ST03 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_FCU2502 | FCU | Not Included | IDF ROOM S-1244 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_FCU2503 | FCU | Not Included | IDF ROOM S-1244 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_FCU2504 | FCU | Not Included | UPS ROOM S-1276 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_FCU2505 | FCU | Not Included | UPS ROOM S-1276 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_FCU3501 | FCU | Included | STAIR-04 1ST04 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU0201 | FCU | Not Included | South Penthouse S-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU0202 | FCU | Not Included | South Penthouse S-2101 |  |  | South Penthouse S-2101 | South Building/SF/SF-1 | SAME
RDC_SB_2F_FCU0203 | FCU | Not Included | South Penthouse S-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU0204 | FCU | Not Included | South Penthouse S-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU0205 | FCU | Not Included | Normal Elec. S-2103 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU0206 | FCU | Not Included | Normal Elec. S-2103 |  |  | South Penthouse S-2101 | South Building/SF/SF-1 | DIFF | the screen puts SB-FCU0206 in South Penthouse S-2101; the register says Normal Elec. S-2103
RDC_SB_2F_FCU0207 | FCU | Not Included | Emerg. Elec. S-2104 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU0208 | FCU | Not Included | Emerg. Elec. S-2104 |  |  | South Penthouse S-2101 | South Building/SF/SF-1 | DIFF | the screen puts SB-FCU0208 in South Penthouse S-2101; the register says Emerg. Elec. S-2104
RDC_SB_2F_FCU1201 | FCU | Not Included | IDF S-2102 |  |  |  | South Building/SF/SF-1 | CHECK | the dot sits on the room's left-hand wall
RDC_SB_2F_FCU1202 | FCU | Not Included | IDF S-2102 |  |  |  | South Building/SF/SF-1 | DIFF | the screen puts SB-FCU1202 in South Penthouse S-2101; the register says IDF S-2102 - the dot is in the open penthouse below IDF S-2102
RDC_SB_2F_FCU2201 | FCU | Not Included | South Penthouse S-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU2202 | FCU | Not Included | South Penthouse S-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU2203 | FCU | Not Included | South Penthouse S-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU2204 | FCU | Not Included | Emerg. Elec. S-2105 |  |  | Emergency Elec. S-2105 | South Building/SF/SF-2 | SAME
RDC_SB_2F_FCU2205 | FCU | Not Included | Emerg. Elec. S-2105 |  |  | South Penthouse S-2101 | South Building/SF/SF-2 | DIFF | the screen puts SB-FCU2205 in South Penthouse S-2101; the register says Emerg. Elec. S-2105
RDC_SB_2F_FCU2206 | FCU | Not Included | Normal Elec. S-2106 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU2207 | FCU | Not Included | Normal Elec. S-2106 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU2208 | FCU | Not Included | IDF S-2107 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU2209 | FCU | Not Included | IDF S-2107 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_2F_FCU2210 | FCU | Not Included | South Penthouse S-2101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_FCU0001 | FCU | Included | STAIR-02 S-02T02 |  |  |  | South Building/GF/GF-4 | CHECK | the dot sits on the stair's left-hand wall
RDC_SB_GF_FCU1001 | FCU | Not Included | QTEL ROOM S-0132 |  |  |  | South Building/GF/GF-5 | CHECK | the dot sits on the room's right-hand wall
RDC_SB_GF_FCU1002 | FCU | Not Included | QTEL ROOM S-0132 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_FCU1003 | FCU | Not Included | IDF ROOM S-0133 |  |  |  | South Building/GF/GF-5 | DIFF | the screen puts SB-FCU1003 in ALT Recording Sound S-0135; the register says IDF ROOM S-0133 - the dot sits on the room's left-hand wall
RDC_SB_GF_FCU1004 | FCU | Not Included | IDF ROOM S-0133 |  |  |  | South Building/GF/GF-5 | DIFF | the screen puts SB-FCU1004 in ALT Recording Sound S-0135; the register says IDF ROOM S-0133 - a second dot beside SB-FCU1003
RDC_SB_GF_FCU1005 | FCU | Not Included | EC MDF ROOM S-0134 |  |  | EC MDF S-0134 | South Building/GF/GF-5 | SAME
RDC_SB_GF_FCU1006 | FCU | Not Included | EC MDF ROOM S-0134 |  |  | EC MDF S-0134 | South Building/GF/GF-5 | SAME
RDC_SB_GF_FCU1007 | FCU | Not Included | MECHANICAL ROOM S-0136 |  |  | Mech S-0136 | South Building/GF/GF-5 | SAME
RDC_SB_GF_FCU1008 | FCU | Included | STAIR-01 S-01T01 |  |  | Stair 1 S-0ST01 | South Building/GF/GF-6 | SAME
RDC_SB_GF_FCU2001 | FCU | Included | STAIR-03 S-0ST03 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_FCU2002 | FCU | Not Included | AV ROOM S-0210 |  |  | AV S-0210 | South Building/GF/GF-2 | SAME
RDC_SB_GF_FCU2003 | FCU | Not Included | AV ROOM S-0210 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_FCU2004 | FCU | Not Included | IDF ROOM S-0271 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_FCU2005 | FCU | Not Included | IDF ROOM S-0271 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_GF_FCU3001 | FCU | Included | STAIR-04 S-0ST04 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8001 | FCU | Included | GENERAL STORAGE ROOM U-0129 | ahu-8601 |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8002 | FCU | Included | SHOP U-0135 | ahu-8601 |  | Shop U-0135 | Utility Building/GF | SAME
RDC_UB_GF_FCU8003 | FCU | Included | MAIL ROOM U-0128 |  |  |  | Utility Building/GF | CHECK | the dot sits on the room's right-hand wall
RDC_UB_GF_FCU8004 | FCU | Included | GENERAL STORAGE U-0108 | ahu-8601 |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8005 | FCU | Included | RECYCLING ROOM U-0109 | ahu-8601 |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8006 | FCU | Included | CYLINDER STORAGE U-0105 |  |  |  | Utility Building/GF | DIFF | the screen puts UB-FCU8006 in Dispensing U-0104; the register says CYLINDER STORAGE U-0105 - the dot sits on the room's left-hand wall
RDC_UB_GF_FCU8007 | FCU | Not Included | LN2 DISPENSER U-0104 | ahu-8601 |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8008 | FCU | Included | FLAMMABLE STORAGE U-0103 | ahu-8601 |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8009 | FCU | Included | FLAMMABLE WASTE STORAGE U-0102 | ahu-8601 |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8010 | FCU | Not Included | BMS ROOM U-0117 | ahu-8601 |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8011 | FCU | Included | BREAK ROOM U-0118 | ahu-8601 |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8012 | FCU | Included | OFFICE SPACE U-0119 | ahu-8601 |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8013 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 | ahu-8601 |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8014 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 | ahu-8601 |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8502 | FCU | Included | SHIPPING AND RECEIVING U-0130 |  |  |  | Utility Building/GF | OPEN | the dot lands beside the loading Dock, which the screen labels only Dock and gives no room number
RDC_UB_GF_FCU8503 | FCU | Included | SHIPPING AND RECEIVING U-0130 |  |  |  | Utility Building/GF | OPEN | as UB-FCU8502 - the dot is beside the unnumbered Dock
RDC_UB_GF_FCU8504 | FCU | Included | SHIPPING AND RECEIVING L0 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8505 | FCU | Included | SHIPPING AND RECEIVING L0 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8512 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8513 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_GF_FCU8514 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  |  | Pump Room U-0121 | Utility Building/GF | DIFF | the screen puts UB-FCU8514 in Pump Room U-0121; the register says WET/MECH/FIRE ROOM U-0120
RDC_UB_GF_FCU8515 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_MF_FCU8501 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_MF_FCU8506 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-2 | SAME
RDC_UB_MF_FCU8507 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_MF_FCU8508 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_MF_FCU8509 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_UB_MF_FCU8510 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-2 | SAME
RDC_UB_MF_FCU8511 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  | Mechanical U-101 | Utility Building/MF-2 | SAME
RDC_SB_L0_AT-1001 | AT | Included | Corridor S-0137 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-1002 | AT | Not Included | Computer Lab S-0139 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_EV-1001 | EV | Not Included | Computer Lab S-0139 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-1003 | AT | Not Included | NOC S-0140A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_EV-1002 | EV | Not Included | NOC S-0140A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-1004 | AT | Not Included | Dedicated Cyber SOC/NOC Lab S-0141 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-1005 | AT | Not Included | Normal & Emergency Elec. Landing S-0142 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-1006 | AT | Included | Corridor S-0137 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-1007 | AT | Not Included | UPS S-0145 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_EV-1003 | EV | Not Included | UPS S-0145 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-1008 | AT | Not Included | Cyber/Embedded/Dist System Electrical Lab S-0146 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-1009 | AT | Included | Service Dock S-0151 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4005 | AT | Not Included | Electrical N-0202 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4035 | AT | Included | Corridor N-0207A |  |  |  | North Building/GF/GF-1 | CHECK | the dot sits near the boundary with Corridor N-0207A to its left; the screen calls this unit CAV4035 and the register calls it AT - joined on the number, which is an assumption
RDC_NB_GF_AT-4100 | AT | Not Included | Emergency Elec. Room N-0225 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4105 | AT | Not Included | Normal Electrical Room N-0225 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4110 | AT | Included | Conference Room N-0227 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4115 | AT | Included | Office N-0228 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4120 | AT | Included | Office N-0229 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4125 | AT | Included | Office N-0230 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4130 | AT | Included | Office N-0231 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4135 | AT | Included | Office N-0232 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4140 | AT | Included | Conference Room N-0233 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4145 | AT | Included | Office N-0234 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4165 | AT | Included | Office N-0236 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4170 | AT | Included | Storage Room N-0237 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4225 | AT | Included | Office N-0247 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4230 | AT | Included | Office N-0248 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4235 | AT | Included | Workstation N-0250 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4240 | AT | Included | Office N-0251 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4245 | AT | Included | Office N-0252 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4250 | AT | Included | Office N-0253 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4255 | AT | Included | Office N-0254 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4260 | AT | Included | Workstation N-0255 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4265 | AT | Included | Office N-0256 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4270 | AT | Included | Office N-0257 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4275 | AT | Included | Office N-0258 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4280 | AT | Included | Office N-0259 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4285 | AT | Included | Workstation N-0260 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4290 | AT | Included | Office N-0261 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4295 | AT | Included | Office N-0262 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4300 | AT | Included | Office N-0263 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4305 | AT | Included | Office N-0264 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4310 | AT | Included | Workstation N-0265 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_CEV-4031 | CEV | Included | Service Corridor N-0207 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-4028 | EV | Not Included | MDF ROOM N-0206A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-4236 | EV | Included | Office 05 -8WS- N-0250 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-4261 | EV | Included | Office 05 -8WS- N-0255 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-4286 | EV | Included | Office 05 -8WS- N-0260 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-4311 | EV | Included | WORKSTATION N-0265 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-4041 | VEV | Not Included | Air Quality High Bay N-0215A |  |  |  | North Building/GF/GF-3 | CHECK | the dot sits on the room's left-hand wall
RDC_NB_GF_FEV-4193 | FEV | Not Included | CSP Lab N-0240B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-4194 | FEV | Not Included | CSP Lab N-0240B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-4213A | VEV | Not Included | Desalination Lab N-0240D |  |  |  | North Building/GF/GF-1 | OPEN | as NB-VAV4211 - four leaders share one endpoint
RDC_NB_GF_VEV-4213B | VEV | Not Included | Desalination Lab N-0240D |  |  |  | North Building/GF/GF-1 | OPEN | as NB-VAV4211 - four leaders share one endpoint
RDC_NB_GF_FEV-4214 | FEV | Not Included | Desalination Lab N-0240D |  |  |  | North Building/GF/GF-1 | OPEN | the walk ended below the plan among the widget labels, not in any room
RDC_NB_GF_FEV-4215 | FEV | Not Included | Desalination Lab N-0240D |  |  |  | North Building/GF/GF-1 | OPEN | as NB-FEV4214 - the walk never entered the plan
RDC_NB_GF_FEV-4216 | FEV | Not Included | Desal Lab N-0240D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0003 | AT | Included | Entrance Lobby S-0102 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0006 | AT | Not Included | Normal Elec. S-0107 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0007 | AT | Included | Conf S-0109 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0008 | AT | Not Included | Computer Research Lab 3 S-0110 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0009 | AT | Included | Phone Booth S-0111 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0010 | AT | Included | Phone Booth S-0112 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0011 | AT | Included | Conference Room S-0113 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0012 | AT | Not Included | Computer Research Lab 2 S-0114 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0013 | AT | Included | Phone Booth S-0115 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0014 | AT | Included | Phone Booth S-0116 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0015 | AT | Included | Corridor S-0117 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0016 | AT | Included | Conf S-0118 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0017 | AT | Not Included | Computer Research Lab 1 S-0119 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0018 | AT | Included | Restaurant S-0123 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0019 | AT | Included | Restaurant S-0123 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0020 | AT | Included | Storage S-0120B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0021 | AT | Included | Vestibule S-0125 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0022 | AT | Included | Men S-0126 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0023 | AT | Included | Women S-0127 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0024 | AT | Not Included | NORM. ELEC. S-0129 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0025 | AT | Included | Alt Recording/Sound S-0135 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4001 | AT | Included | Store N-0201 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4312 | AT | Included | Breakout N-0265B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-4315 | AT | Included | Vestibule N-0270A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5025 | AT | Included | Corridor N-0110 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5100 | AT | Included | Office N-0115 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5105 | AT | Included | Office N-0116 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5110 | AT | Included | Office N-0117 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5115 | AT | Included | Office N-0118 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5120 | AT | Included | Office N-0119 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5125 | AT | Included | Office N-0120 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5130 | AT | Included | Office N-0121 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5135 | AT | Included | Office N-0122 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5140 | AT | Included | Office N-0123 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5145 | AT | Included | Office N-0124 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5150 | AT | Included | Office N-0125 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5152 | AT | Included | Office N-0126 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5155 | AT | Included | Office N-0127 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5156 | AT | Included | Office 04 N-0129 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5160 | AT | Included | MENS ROOM N-0130 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5165 | AT | Included | Corridor N-0134 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5280 | AT | Included | Store N-0146 |  |  | Serv Core N-0136 | North Building/GF/GF-5 | DIFF | the screen puts NB-CAV5280 in JC N-0132; the register says Store N-0146 - a second dot beside NB-VAV5165-EV5166
RDC_NB_GF_AT-5290 | AT | Included | Pantry N-0148 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5295 | AT | Included | Conference Room N-0149 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5300 | AT | Included | Corridor N-0150 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5305 | AT | Included | Office N-0151 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5310 | AT | Included | Office N-0152 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5315 | AT | Included | Open Office N-0153 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5320 | AT | Included | Office N-0154 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5325 | AT | Included | Office N-0155 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5330 | AT | Included | Office N-0156 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5335 | AT | Included | Office N-0157 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5340 | AT | Included | Office N-0158 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5345 | AT | Included | Office N-0159 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5350 | AT | Included | Open Office N-0160 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5355 | AT | Included | Office N-0161 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5360 | AT | Included | Office N-0162 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5365 | AT | Included | Office N-0163 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5370 | AT | Included | Office N-0164 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5375 | AT | Included | Open Office N-0165 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5380 | AT | Included | Office N-0166 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5385 | AT | Included | Office N-0167A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5390 | AT | Included | Office 04 N-0168 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5415 | AT | Included | Office 04 N-0174 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-4316 | EV | Included | Vestibule N-0270A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-5026 | EV | Included | Corridor N-0110 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-5161 | EV | Included | Womens+N-0130A+N-0132 JC N-0130 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-5163 | EV | Not Included | IDF N-0133 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-5291 | EV | Included | Pantry N-0148 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-5052A | VEV | Not Included | Analytical Core Lab 1 N-0114A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-5052B | VEV | Not Included | Analytical Core Lab 1 N-0114A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5053 | FEV | Not Included | Analytical Core Lab 1 N-0114A |  |  |  | North Building/GF/GF-5 | CHECK | as NB-VAV5050 - open lab floor under that name
RDC_NB_GF_VEV-5055 | VEV | Not Included | Analytical Core Lab 1 N-0114A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5062 | FEV | Not Included | Clean Lab N-0114B |  |  |  | North Building/GF/GF-5 | OPEN | the dot lands in the open lab band north of Serv Core N-0136 where no room name is printed
RDC_NB_GF_VEV-5071 | VEV | Not Included | Dirty Lab N-0114C |  |  |  | North Building/GF/GF-5 | CHECK | the dot is below the room name in open lab floor
RDC_NB_GF_FEV-5072 | FEV | Not Included | Dirty Lab N-0114C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5073 | FEV | Not Included | Dirty Lab N-0114C |  |  |  | North Building/GF/GF-5 | CHECK | as NB-VEV5071 - open lab floor under that name
RDC_NB_GF_FEV-5074 | FEV | Not Included | Dirty Lab N-0114C |  |  |  | North Building/GF/GF-5 | OPEN | the dot lands between Dirty Lab N-0114C and Analyt Core N-0114A in floor the screen does not name
RDC_NB_GF_FEV-5082 | FEV | Not Included | Bio Analyt N-0114D |  |  |  | North Building/GF/GF-5 | OPEN | as NB-FEV5095B - open lab floor between Bio Analyt N-0114D and Cold Room N-0114E with no name
RDC_NB_GF_FEV-5083 | FEV | Not Included | Bio Analyt N-0114D |  |  |  | North Building/GF/GF-5 | OPEN | as NB-FEV5095B - the same unnamed strip
RDC_NB_GF_VEV-5092 | VEV | Not Included | Air Quality N-0114F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5093 | FEV | Not Included | Air Quality N-0114F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5094 | FEV | Not Included | Air Quality N-0114F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5095A | FEV | Not Included | Air Quality N-0114F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5095B | FEV | Not Included | Bio Analyt N-0114D |  |  |  | North Building/GF/GF-5 | OPEN | the dot lands just above the Cold Room N-0114E box in open lab floor the screen does not name
RDC_NB_GF_VEV-5182A | VEV | Not Included | Analyt Core-2 N-0140A |  |  |  | North Building/GF/GF-6 | OPEN | the dot lands below Analyt Core N-0140A in floor the screen does not name
RDC_NB_GF_VEV-5182B | VEV | Not Included | Analyt Core-2 N-0140A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5183 | FEV | Not Included | Analytical Core Lab 2 N-0140A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-5192a | VEV | Not Included | Furnace Room N-0140B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-5192b | VEV | Not Included | Furnace Room N-0140B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5203 | FEV | Not Included | Prep Lab N-0140C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-5211 | VEV | Not Included | Sputter Room N-0140D |  |  | MBE EVAP Room N-0140E | North Building/GF/GF-6 | DIFF | the screen puts NB-VEV5211 in MBB EVAP Room N-0140E; the register says Sputter Room N-0140D - the dot sits on the room's upper wall
RDC_NB_GF_VEV-5221 | VEV | Not Included | MBE/Evap Room N-0140E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5222 | FEV | Not Included | Evap Room N-0140E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5223 | FEV | Not Included | Evap Room N-0140E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-5231 | VEV | Not Included | ALD Room N-0140F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_CEV-5241 | CEV | Not Included | Air Lock N-0140G |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5271 | FEV | Not Included | Org Chem N-0140K |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5272 | FEV | Not Included | Org Chem N-0140K |  |  |  | North Building/GF/GF-6 | CHECK | the dot sits on the lab's upper wall, the leader arriving from the corridor above
RDC_NB_GF_FEV-5273 | FEV | Not Included | Org Chem N-0140K |  |  |  | North Building/GF/GF-6 | OPEN | the dot sits on the wall between ORG Chem N-0140K and MBB EVAP Room N-0140E and could be either
RDC_NB_GF_FEV-5274 | FEV | Not Included | Org Chem N-0140K |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5275 | FEV | Not Included | Org Chem N-0140K |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5276 | FEV | Not Included | Org Chem N-0140K |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-5277 | FEV | Not Included | Org Chem N-0140K |  |  |  | North Building/GF/GF-6 | OPEN | the dot lands in open floor between ORG Chem N-0140K and Open Office N-0160 that carries no name
RDC_SB_L0_AT-0001 | AT | Included | Vestibule S-0101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0002 | AT | Included | Employee Entry Lobby S-0102 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0004 | AT | Included | Corridor S-0104 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0005 | AT | Included | Men S-0105 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_A1.2_AT-2001 | AT | Included | High-Density Room S-0206 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_A1.3_AT-2001 | AT | Included | WOMEN S-0205 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5005 | AT | Included | Vestibule N-0105 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5010 | AT | Included | Conf N-0106 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5015 | AT | Included | Conference N-0107 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5020 | AT | Included | Mens + Vestibule + N-0109 N-0108 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5030 | AT | Included | Confr Room N-0112 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5040 | AT | Not Included | Normal Elec. N-0113 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5045 | AT | Not Included | Emergency Elec. N-0114 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5395 | AT | Included | Exp. Office N-0169 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5400 | AT | Included | Reception Area N-0170 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5405 | AT | Included | Exp. Office N-0172 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5410 | AT | Included | Conf Room N-0173 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5000 | AT | Included | Lobby North N-0101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-5001 | AT | Included | Lobby North N-0101 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6000 | AT | Included | Conf Room N-0301 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6005 | AT | Included | Vestibule N-0302 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6010 | AT | Included | Conf N-0304 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6015 | AT | Included | Men N-0306 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6020 | AT | Included | Vestibule N-0308 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6025 | AT | Not Included | Normal Elec. N-0310 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6240 | AT | Not Included | Emergency Electrical N-0350A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6300 | AT | Included | Store N-0362B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6305 | AT | Included | Office N-0363 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6310 | AT | Included | Office N-0364 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6315 | AT | Included | Conf Room N-0364A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-6316 | EV | Included | Conf Room N-0364A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-5021 | EV | Included | Mens + Vestibule + N-0109 N-0108 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-5035 | EV | Included | Confr Room N-0112 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-6016 | EV | Included | Men N-0306 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-6127 | EV | Not Included | IDF N-0311 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2002 | AT | Included | Conference Room S-0207 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2003 | AT | Included | Multi Purpose Hall S-0208 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2004 | AT | Included | Multi Purpose Hall S-0208 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2006 | AT | Included | Meeting Room S-0212 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2007 | AT | Included | Office S-0213 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2008 | AT | Included | Office S-0214 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2009 | AT | Included | Office S-0215 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2010 | AT | Included | Office S-0216 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2011 | AT | Included | Office S-0217 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2012 | AT | Not Included | Director Office S-0218 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2013 | AT | Included | Office S-0219 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2014 | AT | Included | Office S-0220 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2015 | AT | Not Included | Director Office S-0221 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2016 | AT | Not Included | Director Office S-0222 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2017 | AT | Included | Meeting Room S-0223 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2018 | AT | Included | PANTRY S-0226 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2019 | AT | Included | Office S-0227 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2020 | AT | Included | Informal Meeting S-0231 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2021 | AT | Included | Open Plan S-0228 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2022 | AT | Not Included | Director Office S-0229 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2023 | AT | Included | Office S-0230 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2024 | AT | Not Included | Executive Director Office S-0232 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2025 | AT | Not Included | Executive Director Office S-0233 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2026 | AT | Included | Office S-0234 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2027 | AT | Included | Office S-0235 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2028 | AT | Included | Office S-0236 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2029 | AT | Included | Waiting Area S-0251 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2030 | AT | Included | Office S-0259 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2031 | AT | Included | Office S-0260 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2032 | AT | Included | Open Plan S-0269 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2033 | AT | Included | CORRIDOR S-0273 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2034 | AT | Included | Meeting Room S-0274 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2035 | AT | Not Included | MECH S-0272 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2036 | AT | Not Included | Emergency Elec. Room S-0278 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2037 | AT | Included | Men S-0284 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2038 | AT | Included | Informal Meeting S-0285 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2039 | AT | Included | Meeting Room S-0286 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2040 | AT | Included | Open Plan S-0289 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2041 | AT | Included | Open Plan S-0289 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2042 | AT | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2043 | AT | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2044 | AT | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2045 | AT | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2046 | AT | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-2047 | AT | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0115 | AT | Included | Office S-0233A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0116 | AT | Included | Office S-0232A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0117 | AT | Included | Open Plan S-0228 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0118 | AT | Included | Open Plan S-0228B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0120 | AT | Included | Open Plan S-0228A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0122 | AT | Included | Office S-0211A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0123 | AT | Included | Office S-0211B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0124 | AT | Included | Technical Open Plan S-0211 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6130 | AT | Included | Store N-0315 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6135 | AT | Included | Store N-0316 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6140 | AT | Included | Workstation N-0317 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6145 | AT | Included | Office N-0318 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6150 | AT | Included | Office N-0319 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6155 | AT | Included | Workstation N-0320 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6160 | AT | Included | Office N-0321 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6170 | AT | Included | Office N-0323 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6175 | AT | Included | Workstation N-0324 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6180 | AT | Included | Office N-0325 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6185 | AT | Included | Office N-0326 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7000 | AT | Included | Vestibule / Staging N-0401 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6195 | AT | Included | Store N-0329 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6190 | AT | Not Included | Normal Elec. N-0328 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6200 | AT | Included | Conf N-0330 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7005 | AT | Included | WOMEN N-0402 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6220 | AT | Not Included | Emergency Elec. N-0333 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6205 | AT | Included | Conference N-0331 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6285 | AT | Included | Conference N-0358 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7380 | AT | Not Included | Pipe Chase N-0443B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6210 | AT | Included | Corridor N-0332C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6280 | AT | Included | Pantry N-0356 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6295 | AT | Included | Conference N-0360 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6320 | AT | Included | Corridor N-0365 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6325 | AT | Included | Office N-0366 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6330 | AT | Included | Office 04 N-0367 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6335 | AT | Included | Office N-0368 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6340 | AT | Included | Office N-0369 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6345 | AT | Included | Office N-0370 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6350 | AT | Included | Office N-0371 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6355 | AT | Included | Workstation N-0372 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6360 | AT | Included | Office N-0374 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6365 | AT | Included | Office N-0375 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6370 | AT | Included | Office N-0376 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6375 | AT | Included | Office N-0377 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6380 | AT | Included | Workstation N-0378 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6390 | AT | Included | Office N-0379 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6395 | AT | Included | Office N-0380 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6400 | AT | Included | Workstation N-0381 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6405 | AT | Included | Office N-0382 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-6410 | AT | Included | Office N-0383 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7385 | AT | Included | Office N-0444 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7390 | AT | Included | Office 04 N-0445 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-6141 | EV | Included | Workstation N-0317 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-6156 | EV | Included | Workstation N-0320 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-6176 | EV | Included | Workstation N-0324 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-6281 | EV | Included | Pantry N-0356 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-6356 | EV | Included | Office 05-8-WKS N-0372 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-6381 | EV | Included | Office 05-8-WKS N-0378 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-6401 | EV | Included | Office 05-8-WKS N-0381 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-7006 | EV | Included | WOMEN N-0402 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-7381 | EV | Not Included | Pipe Chase N-0443B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-6053 | VEV | Not Included | Open Lab 1 N-0310C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-6061 | VEV | Not Included | Lab Support 3 N-0310D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-6071 | VEV | Not Included | Lab Support 4 N-0310E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-6081 | VEV | Not Included | Lab Support 5 N-0310F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-6091 | VEV | Not Included | Lab Support 6 N-0310G |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VAV-6080 | VAV | Not Included | Lab Support 5 N-0310F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FCU6997 | FCU | Not Included | Lab Sup 2 N-0310B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3001 | AT | Not Included | Director Office S-0237 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3002 | AT | Included | Office S-0238 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3003 | AT | Included | Office S-0239 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3004 | AT | Included | Office S-0240 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3005 | AT | Included | Office S-0241 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3006 | AT | Included | Office S-0242 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3007 | AT | Not Included | Director Office S-0243 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3010 | AT | Included | Open Plan S-0244 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3011 | AT | Included | Meeting Room S-0245 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3012 | AT | Included | Office S-0246 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3013 | AT | Included | Office S-0247 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3014 | AT | Included | Office S-0248 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3015 | AT | Not Included | Security S-0249 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3016 | AT | Included | Corridor S-0250 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3017 | AT | Included | Office S-0251 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3018 | AT | Included | Corridor S-0251B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3019 | AT | Included | Corridor S-0251B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3020 | AT | Included | Office S-0252 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3021 | AT | Included | Office S-0252 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3022 | AT | Included | Office S-0253 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3023 | AT | Included | Office S-0253 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3024 | AT | Included | Office S-0254 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3025 | AT | Included | Office S-0255 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3026 | AT | Included | Office S-0256 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3027 | AT | Included | Office S-0257 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3028 | AT | Included | Office S-0258 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3031 | AT | Not Included | IT Server S-0264 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3032 | AT | Included | Open Plan S-0265 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3033 | AT | Not Included | Emergency Elec. S-0266 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3034 | AT | Included | Reception / Vestibule S-0293 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3035 | AT | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-3036 | AT | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0101 | AT | Included | Office S-0244A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0102 | AT | Included | Office S-0244B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0103 | AT | Included | Office S-0244C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0104 | AT | Included | Office S-0244D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0105 | AT | Included | Office S-0244E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0107 | AT | Included | Office S-0262A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0108 | AT | Included | Office S-0262B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0109 | AT | Included | Office S-0262C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0110 | AT | Included | Office S-0262H |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0111 | AT | Included | Office S-0262E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0112 | AT | Included | Office S-0262F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0113 | AT | Included | Office S-0262G |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_L0_AT-0114 | AT | Included | Office S-0262D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7080 | AT | Included | Exp. Office N-0410 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7085 | AT | Included | Office N-0411 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7095 | AT | Included | Office N-0413 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7100 | AT | Included | Office N-0414 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7110 | AT | Included | Office N-0416 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7115 | AT | Included | Office N-0417 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7125 | AT | Not Included | NORMAL ELEC. ROOM N-0420 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7130 | AT | Included | Office N-0421 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7135 | AT | Included | Office N-0422 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7140 | AT | Included | Conference N-0423 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7145 | AT | Included | Office N-0425 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7155 | AT | Included | Office N-0427 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7165 | AT | Included | Office N-0429 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7180 | AT | Included | Corridor N-0432 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7185 | AT | Not Included | Emer. Elec. Room N-0433 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7195 | AT | Included | OFFICE N-0436 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7205 | AT | Included | Office 04 N-0438 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7215 | AT | Included | CONFERENCE ROOM N-0440 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7395 | AT | Included | Workstation N-0446 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7400 | AT | Included | Office N-0447 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7405 | AT | Included | Office N-0448 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7410 | AT | Included | Office N-0449 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7415 | AT | Included | Office N-0450 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7425 | AT | Included | Workstation N-0452 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7430 | AT | Included | Office N-0453 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7435 | AT | Included | Office N-0454 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7440 | AT | Included | Office N-0455 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7445 | AT | Included | Office N-0456 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7460 | AT | Included | Workstation N-0457 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7465 | AT | Included | Office N-0458 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7470 | AT | Included | Office N-0459 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7475 | AT | Included | Office N-0460 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7480 | AT | Included | Office N-0461 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7485 | AT | Included | WORKSTATION N-0462 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7490 | AT | Included | Confer N-0463 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7496 | AT | Included | Office N-0464 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7498 | AT | Included | Office N-0465 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7499 | AT | Included | Office N-0466 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7090-N1 | AT | Included | Office N-0412 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7090-N2 | AT | Included | Office N-0412A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7105-N1 | AT | Included | Office N-0415 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7105-N2 | AT | Included | Office N-0415A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7120-N1 | AT | Included | Office N-0418 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7120-N2 | AT | Included | Office N-0418A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7120-N3 | AT | Included | Office N-0430A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7120-N4 | AT | Included | Office N-0430B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7120-N5 | AT | Included | Office N-0430C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7120-N6 | AT | Included | Office N-0430D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7120-N7 | AT | Included | Office N-0430E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7120-N8 | AT | Included | Office N-0430F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_AT-7120-N9 | AT | Included | Corridor N-0418A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-7091 | EV | Included | Office N-0412A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-7106 | EV | Included | Office N-0415A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-7121 | EV | Included | Office 05-4-WS N-0418 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-7122 | EV | Not Included | IDF Room N-0419 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-7396 | EV | Included | Office 05-8-WKS N-0446 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-7426 | EV | Included | Office 05-8-WKS N-0452 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-7461 | EV | Included | Office 05-8-WKS N-0457 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_EV-7486 | EV | Included | Office 05-8-WKS N-0462 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-7022A | VEV | Not Included | NMR Lab N-0404A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-7022B | VEV | Not Included | NMR Lab N-0404A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-7023A | VEV | Not Included | NMR Lab N-0404A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-7023B | VEV | Not Included | NMR Lab N-0404A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-7024A | VEV | Not Included | NMR Lab N-0404A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-7024B | VEV | Not Included | NMR Lab N-0404A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-7052 | FEV | Not Included | EM Prep 1 - MAT N-0404D |  |  |  | North Building/GF/GF-10 | DIFF | the screen puts NB-FEV7052 in Service Equipment Room N-0404C; the register says EM Prep 1 - MAT N-0404D - the dot is in the open room below its name
RDC_NB_GF_FEV-7053 | FEV | Not Included | EM Prep 1 - MAT N-0404D |  |  |  | North Building/GF/GF-10 | DIFF | the screen puts NB-FEV7053 in Service Equipment Room N-0404C; the register says EM Prep 1 - MAT N-0404D - a second dot beside NB-FEV7052
RDC_NB_GF_FEV-7062 | FEV | Not Included | EM Prep 2 - BIO N-0404E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-7072A | VEV | Not Included | Surf Analysis Lab N-0404F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-7072B | VEV | Not Included | Surf Analysis Lab N-0404F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-7073 | VEV | Not Included | Surf Analysis Lab N-0404F |  |  |  | North Building/GF/GF-10 | CHECK | the dot is below the room name in open lab floor
RDC_NB_GF_FEV-7074 | FEV | Not Included | Surf Analysis Lab N-0404F |  |  |  | North Building/GF/GF-10 | OPEN | the dot lands high in the open lab band above EM Prep 2 BIO N-0404E and Surf Analysis Lab N-0404F, where the screen prints no name
RDC_NB_GF_FEV-7075 | FEV | Not Included | Surf Analysis Lab N-0404F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_FEV-7232 | FEV | Not Included | Inter Lab N-0442A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-7241B | VEV | Not Included | Optical Lab N-0442B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_GF_VEV-7301 | VEV | Not Included | AL 1 N-0442H |  |  |  | North Building/GF/GF-11 | OPEN | as NB-VAV7260-VEV7261 - the dot is on the same corridor wall and could belong to either side
RDC_NB_GF_FCU7993 | FCU | Included | Stair 5 N-0ST05 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1504 | AT | Included | Corridor S-1122 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1507 | AT | Included | Workstation S-1124A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1508 | AT | Included | Scientific Comp. Office 1 S-1125 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1509 | AT | Included | Scientific Comp. Office S-1126 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1510 | AT | Included | ALT Office 2 S-1127 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1511 | AT | Included | ALT Office 3 S-1128 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1512 | AT | Included | Workstation S-1128A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1513 | AT | Included | ALT Office 1 S-1129 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1514 | AT | Included | ALT Office S-1130 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1515 | AT | Included | Distub. Syst Office 1 S-1131 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1516 | AT | Included | Distub. Syst Office S-1132 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1517 | AT | Included | Workstation S-1132A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1518 | AT | Included | Distub. Syst Office S-1133 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1519 | AT | Included | Distub. Syst Office S-1134 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1520 | AT | Not Included | Data Analytic Office S-1135 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1521 | AT | Not Included | Data Analytic Office S-1136 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1522 | AT | Included | Workstation S-1136A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1523 | AT | Not Included | Data Analytic Office S-1137 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1524 | AT | Not Included | Data Analytic Office S-1138 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1525 | AT | Included | Office S-1139 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1526 | AT | Included | Office S-1140 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1527 | AT | Included | Conference Room S-1141 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1528 | AT | Included | Office S-1142 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1529 | AT | Included | Office S-1144 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1530 | AT | Included | Office S-1145 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1531 | AT | Included | Office S-1146 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1532 | AT | Included | Workstation S-1146A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1533 | AT | Included | Office S-1148 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1534 | AT | Included | Office S-1149 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1535 | AT | Included | Pantry S-1149A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1536 | AT | Included | Office S-1150 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1537 | AT | Not Included | Normal Elec. S-1147 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1542 | AT | Included | Office S-1182 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1546 | AT | Included | Office S-1182E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1548 | AT | Included | Office S-1183 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1549 | AT | Included | Workstation S-1183A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1550 | AT | Included | Office S-1184 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1551 | AT | Included | Social Comp Office S-1185 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1552 | AT | Included | Social Comp Office S-1186 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1553 | AT | Included | Workstation S-1186A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1554 | AT | Included | Social Comp Office S-1187 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1555 | AT | Included | Social Comp Office S-1188 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1556 | AT | Included | Cyber Sec Office S-1189 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1557 | AT | Included | Cyber Sec Office S-1190 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1558 | AT | Included | Workstation S-1190A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1559 | AT | Included | Office S-1191 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1560 | AT | Included | Cyber Sec Office S-1192 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1561 | AT | Included | Cyber Sec Office S-1193 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0538 | AT | Included | Workstation S-1151A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-4660 | AT | Included | Expansion Workstation N-1227 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-4665 | AT | Included | Office N-1228 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-4680 | AT | Included | Office N-1231 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-4690 | AT | Included | Office N-1233 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-4705 | AT | Included | Office N-1236 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-4720 | AT | Included | Office N-1239 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-4730 | AT | Included | Office N-1241 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-4745 | AT | Included | Office N-1244 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-4500 | EV | Not Included | MDF N-1201 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_CEV-4502 | CEV | Included | Corridor N-1202 |  |  |  | North Building/FF/FF-1 | DIFF | the screen puts NB-CEV4502 in Level 0 Open High Bay Lab N-0215D; the register says Corridor N-1202 - the dot sits on the lab's lower wall; double-height space read on the first floor screen
RDC_NB_1F_EV-4661 | EV | Included | Office 05 - 8 WKS- N-1227 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-4686 | EV | Included | Office 05 - 8 WKS- N-1232 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-4711 | EV | Included | Office 05 - 8 WKS- N-1237 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-4736 | EV | Included | Office 05 - 8 WKS- N-1242 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-4602 | VEV | Not Included | Testing Room N-1216B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-4603 | FEV | Not Included | Testing Room N-1216B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-4604 | FEV | Not Included | Testing Room N-1216B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-4605 | FEV | Not Included | Testing Room N-1216B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-4606 | FEV | Not Included | Testing Room N-1216B |  |  |  | North Building/FF/FF-1 | CHECK | the dot sits on the wall between EL Shop N-1216C and Testing Room N-1216B, just inside Testing Room
RDC_NB_1F_FEV-4622 | FEV | Not Included | EL Shop N-1216C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_CAV-4581B | CAV | Not Included | Photovoltaic Lab N-1216A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-4585A | VEV | Not Included | Photovoltaic Lab N-1216A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-4585B | VEV | Not Included | Photovoltaic Lab N-1216A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-4586A | VEV | Not Included | Photovoltaic Lab N-1216A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-4586B | VEV | Not Included | Photovoltaic Lab N-1216A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-4587 | FEV | Not Included | Photovoltaic Lab N-1216A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-4588 | FEV | Not Included | Photovoltaic Lab N-1216A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FCU2004 | FCU | Included | Corridor N-1202 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0501 | AT | Included | Lobby S-1102 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0502 | AT | Included | Vestibule S-1105 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0503 | AT | Included | Women S-1106B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0504 | AT | Included | Vestibule S-1107 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0505 | AT | Not Included | EMERGENCY Elec. S-1107B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0515 | AT | Included | Corridor S-1122 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0516 | AT | Included | Pantry S-1158 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0517 | AT | Not Included | Normal Elec. S-1160 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0524 | AT | Included | Women S-1169 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0525 | AT | Included | Men S-1170 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0534 | AT | Included | CORRIDOR S-1180 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0535 | AT | Included | Cooridor S-1180 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1541 | AT | Included | Cooridor S-1181 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0506 | AT | Included | Conf. S-1110 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0507 | AT | Not Included | Computer Research Lab-4 S-1112 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0508 | AT | Included | Conf S-1113 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0509 | AT | Included | NCIR OFFICE S-1115 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0510 | AT | Included | Workstation S-1115A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0511 | AT | Included | NCIR Office S-1116 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0512 | AT | Included | NCIR Office S-1117 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0513 | AT | Included | NCIR Office S-1118 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0514 | AT | Included | NCIR Office S-1119 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0518 | AT | Included | Office S-1161 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0519 | AT | Included | Office S-1162 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0520 | AT | Included | Office S-1163 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0521 | AT | Included | Office S-1164 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0522 | AT | Included | Office S-1165 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0523 | AT | Included | Office S-1166 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0526 | AT | Included | Office S-1171 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0527 | AT | Included | Office S-1172 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0528 | AT | Included | Office S-1173 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0529 | AT | Included | Corridor S-1174 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0530 | AT | Included | Situation Room S-1175 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0531 | AT | Not Included | Immersive Viz Lab S-1176 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0532 | AT | Included | Conference Room S-1177 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0533 | AT | Included | Telepresence S-1179 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1501 | AT | Included | Workstation S-1119A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1502 | AT | Included | NCIR Office S-1120 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1503 | AT | Included | NCIR Office S-1121 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1505 | AT | Included | SC. Comp Office 2 S-1123 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1506 | AT | Included | SC. Comp Office 3 S-1124 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1539 | AT | Included | Video Conf. Room S-1154 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1540 | AT | Included | Conf S-1159 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1543 | AT | Included | Workstation S-1182A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1544 | AT | Included | Office S-1182C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1545 | AT | Included | Office S-1182D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-1547 | AT | Included | Office S-1182F |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5650 | AT | Included | Office N-1120 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5655 | AT | Included | Store N-1120B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5660 | AT | Included | Office N-1121 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5665 | AT | Included | Office N-1122 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5670 | AT | Included | Office N-1123 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5675 | AT | Included | Office N-1124 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5680 | AT | Included | Office N-1125 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5685 | AT | Included | Corridor N-1126 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5690 | AT | Included | Office N-1127 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5695 | AT | Included | Office N-1128 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5700 | AT | Included | Office N-1129 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5705 | AT | Included | Office N-1130 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5710 | AT | Included | Office N-1131 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5715 | AT | Included | Conf Rm N-1132 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5730 | AT | Included | Store N-1135 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5735 | AT | Not Included | Normal Elec. N-1136 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5740 | AT | Not Included | Emer. Elec. N-1137 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5745 | AT | Included | Corridor N-1138 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5760 | AT | Included | Conf N-1143 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5835 | AT | Included | P/C/S Pantry N-1146 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5840 | AT | Included | Corridor N-1150 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5860 | AT | Included | Office N-1154 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5865 | AT | Included | Office N-1155 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5870 | AT | Included | Exp Office N-1156 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5875 | AT | Included | Office N-1157 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5880 | AT | Included | Office N-1158 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5885 | AT | Included | Office N-1159 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5890 | AT | Included | Workstation N-1160 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5895 | AT | Included | Office N-1161 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5900 | AT | Included | Office N-1162 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5905 | AT | Included | Office N-1163 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5910 | AT | Included | Office N-1164 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5915 | AT | Included | Office N-1167 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5920 | AT | Included | Workstation N-1168 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5925 | AT | Included | Office N-1169 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5930 | AT | Included | Office N-1170 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5935 | AT | Included | Office N-1166 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5940 | AT | Included | Workstation N-1165 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-5720 | AT | Included | Men N-1134 |  |  |  | North Building/FF/FF-3 | OPEN | the dot sits on the wall between Normal Elec. Room N-1136 and Emer. Elec. N-1137 and could be either
RDC_NB_1F_AT-5750 | AT | Included | Store N-1141 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-4640 | AT | Included | Women N-1221 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-4650 | AT | Included | Breakout N-1225 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-5686 | EV | Included | Corridor N-1126 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-5721 | EV | Included | Men N-1134 |  |  |  | North Building/FF/FF-3 | OPEN | the dot sits on the wall between Normal Elec. Room N-1136 and Emer. Elec. N-1137 and could be either
RDC_NB_1F_EV-5747 | EV | Not Included | IDF N-1140 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-4641 | EV | Included | Women N-1221 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-5891 | EV | Included | Office 05 - 8 WKS- North N-1160 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-5921 | EV | Included | Office 05 - 8 WKS- N-1168 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-5941 | EV | Included | Office 05 - 8 WKS- N-1165 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-5624 | FEV | Not Included | Sequence Lab N-1115K |  |  | Robotics N-1115J | North Building/FF/FF-3 | DIFF | the screen puts NB-FEV5624 in Robotics N-1115J; the register says Sequence Lab N-1115K
RDC_NB_1F_VEV-5572 | VEV | Not Included | Met/Prot Lab N-1115C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-5573A | VEV | Not Included | Met/Prot Lab N-1115C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-5573B | VEV | Not Included | Met/Prot Lab N-1115C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-5574 | FEV | Not Included | Met/Prot Lab N-1115C |  |  | PRe-PCR N-1115B | North Building/FF/FF-3 | DIFF | the screen puts NB-FEV5574 in PRe-PCR N-1115B; the register says Met/Prot Lab N-1115C
RDC_NB_1F_FEV-5575 | FEV | Not Included | Met/Prot Lab N-1115C |  |  | Cell Culture N-1115E | North Building/FF/FF-3 | DIFF | the screen puts NB-FEV5575 in Cell Culture N-1115E; the register says Met/Prot Lab N-1115C
RDC_NB_1F_VEV-5591 | VEV | Not Included | Cell Culture N-1115E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-5772 | FEV | Not Included | Histology N-1144A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-5791 | VEV | Not Included | Shafallah N-1144C |  |  | Culture & Gel Rm N-1144B | North Building/FF/FF-4 | DIFF | the screen puts NB-VEV5791 in Culture & Gel Rm N-144B; the register says Shafallah N-1144C - the dot is above the room name in open lab floor
RDC_NB_1F_VEV-5795B | VEV | Included | Storage and Archives N-1144C2 |  |  | PRE-PCR N-1144D | North Building/FF/FF-4 | DIFF | the screen puts NB-VEV5795B in PRE-PCR N-144D; the register says Storage and Archives N-1144C2 - the dot is above the PRE-PCR N-144D name in open lab floor
RDC_NB_1F_FEV-5796 | FEV | Not Included | Shafallah N-1144C |  |  | PRE-PCR N-1144D | North Building/FF/FF-4 | DIFF | the screen puts NB-FEV5796 in PRE-PCR N-144D; the register says Shafallah N-1144C - as NB-VEV5795B - the dot is in the open floor carrying that name
RDC_NB_1F_VEV-5811A | VEV | Not Included | Nano Lab N-1144E |  |  |  | North Building/FF/FF-4 | CHECK | the dot sits inside the room near its right-hand edge
RDC_NB_1F_VEV-5811B | VEV | Not Included | Nano Lab N-1144E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-5812 | FEV | Not Included | Nano Lab N-1144E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-5813 | FEV | Not Included | Nano Lab N-1144E |  |  |  | North Building/FF/FF-4 | OPEN | the dot lands at the top of the open lab band below Corridor N-150 where the screen prints no room name
RDC_NB_1F_VEV-5821 | VEV | Not Included | Nano Lab N-1144E |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2501 | AT | Included | Lobby S-1201 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2507 | AT | Included | Female S-1204 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2502 | AT | Included | Lobby S-1202 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2503 | AT | Included | Lobby S-1202 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2504 | AT | Included | Lobby S-1202 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2505 | AT | Included | Lobby S-1202 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2506 | AT | Included | Lobby S-1202 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2508 | AT | Included | Female Prayer S-1207 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2509 | AT | Included | Open Plan S-1210 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2510 | AT | Not Included | Exc. Dir. Office S-1211 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2511 | AT | Included | Office S-1212 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2512 | AT | Included | Office S-1213 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2513 | AT | Included | Office S-1214 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2514 | AT | Included | Office S-1215 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2515 | AT | Included | Office S-1216 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2516 | AT | Not Included | Executive Director Office S-1217 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2517 | AT | Not Included | Executive Director Office S-1218 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2518 | AT | Included | Office S-1219 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2519 | AT | Included | Office S-1220 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2520 | AT | Included | Office S-1221 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2521 | AT | Included | Office S-1222 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2522 | AT | Included | Office S-1223 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2523 | AT | Included | Office S-1224 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2524 | AT | Included | Office S-1225 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2525 | AT | Included | Office S-1226 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2526 | AT | Included | Open Plan S-1227 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2527 | AT | Not Included | Director Office S-1228 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2528 | AT | Not Included | Director Office S-1230 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2529 | AT | Included | Office S-1231 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2530 | AT | Included | Office S-1232 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2531 | AT | Not Included | Director Ofice S-1241 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2532 | AT | Included | Office S-1242 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2533 | AT | Included | Cooridor S-1246 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2534 | AT | Included | Meeting Room S-1247 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2535 | AT | Included | Store S-1248 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2536 | AT | Not Included | Normal Elec. S-1251 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2538 | AT | Included | Office S-1257 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2539 | AT | Included | Office S-1257B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2540 | AT | Not Included | Executive Director S-1260 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2541 | AT | Included | Assistant S-1261 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2542 | AT | Included | Open Plan S-1263 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2543 | AT | Included | Office S-1264 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2544 | AT | Included | Office S-1265 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2545 | AT | Included | Office S-1266 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2546 | AT | Included | Office S-1267 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2547 | AT | Included | Office S-1268 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2548 | AT | Included | Office S-1269 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2549 | AT | Included | Office S-1270 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2550 | AT | Included | Office S-1271 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2551 | AT | Included | Meeting Room S-1272 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2552 | AT | Included | Vestibule S-1273 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-2553 | AT | Included | Male Prayer S-1278 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-4260 | AT | Included | Office 05 -8WS- N-0255 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6650 | AT | Included | Office N-1319 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6655 | AT | Included | Office N-1320 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6660 | AT | Included | Workstation N-1321 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6665 | AT | Included | Office N-1322 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6670 | AT | Included | Office N-1323 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6675 | AT | Included | Workstation N-1324 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6680 | AT | Included | Office N-1325 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6685 | AT | Included | Office N-1326 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6690 | AT | Included | Exp. Workstation N-1327 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6695 | AT | Included | Office N-1328 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6700 | AT | Not Included | NORMAL ELEC. N-1329 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6705 | AT | Included | Office N-1330 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6710 | AT | Included | Office N-1331 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6715 | AT | Included | Office N-1332 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6720 | AT | Included | Corridor N-1335 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6725 | AT | Not Included | Emer. Elec. N-1336 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6740 | AT | Included | Men N-1340 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7500 | AT | Included | Women N-1403 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6900 | AT | Included | Office N-1357 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6905 | AT | Included | Open Plan N-1358 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6910 | AT | Included | Office N-1359 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6915 | AT | Included | Office N-1360 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6920 | AT | Included | Office N-1360B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6925 | AT | Included | Office N-1361 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6930 | AT | Included | Office N-1362 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6935 | AT | Included | Workstation N-1363 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6940 | AT | Included | Office N-1364 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6945 | AT | Included | Office N-1365 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6950 | AT | Included | Office N-1366 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6955 | AT | Included | Office N-1367 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6960 | AT | Included | Workstation N-1368 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6965 | AT | Included | Office N-1369 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6967 | AT | Included | Office N-1370 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6968 | AT | Included | Workstation N-1371 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6970 | AT | Included | PANTRY N-1372 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7865 | AT | Included | Workstation N-1461A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6372 | AT | Included | Office N-1374 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6374 | AT | Included | Office N-1375 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6376 | AT | Included | Office N-1376 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-6378 | AT | Included | Office N-1377 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-6661 | EV | Included | Workstation N-1321 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-6676 | EV | Included | Workstation N-1324 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-6691 | EV | Included | Exp. Workstation N-1327 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-6741 | EV | Included | Men N-1340 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-7501 | EV | Included | Women N-1403 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-6936 | EV | Included | Workstation N-1363 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-6961 | EV | Included | Workstation N-1368 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-6969 | EV | Included | Workstation N-1371 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-6541 | VEV | Not Included | TC1 N-1316B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-6552 | VEV | Not Included | Gene Therapy Lab N-1316C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-6553 | VEV | Not Included | Gene Therapy Lab N-1316C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6554 | FEV | Not Included | Gene Therapy Lab N-1316C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6555 | FEV | Not Included | Gene Therapy Lab N-1316C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_CEV-6581 | CEV | Not Included | TC3 N-1316F |  |  |  | North Building/FF/FF-7 | CHECK | the dot sits on the room's right-hand wall
RDC_NB_1F_FEV-6602 | FEV | Not Included | Analytical Core N-1316H |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6632 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6633 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6634 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6635 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6636 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6637 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6638 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6639 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6731 | FEV | Included | SERIVICE CORRRIDOR N-1337 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-6751 | VEV | Not Included | TC1 N-1345A |  |  |  | North Building/FF/FF-8 | CHECK | the dot sits on the wall between Service Corridor N-337 and the lab below it; the leader arrives from the corridor side
RDC_NB_1F_VEV-6762 | VEV | Not Included | Diabetes Lab / Open Lab N-1345B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_VEV-6763 | VEV | Not Included | Diabetes Lab / Open Lab N-1345B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6764 | FEV | Not Included | Diabetes Lab / Open Lab N-1345B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6765 | FEV | Not Included | Diabetes Lab / Open Lab N-1345B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6766 | FEV | Not Included | Diabetes Lab / Open Lab N-1345B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_CEV-6791 | CEV | Not Included | TC2 N-1345C |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6852 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6853 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6854 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J |  |  |  | North Building/FF/FF-8 | OPEN | the dot lands in open lab floor east of Diabetes Lab Open Lab N-345B that carries no room name
RDC_NB_1F_FEV-6855 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6856 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6857 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-6858 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J |  |  |  | North Building/FF/FF-8 | OPEN | the dot lands just below the Service Corridor N-337 wall in a cell the screen does not name
RDC_NB_1F_FEV-6859 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3501 | AT | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3502 | AT | Included | Lobby S-0294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3503 | AT | Included | Reception S-0293 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3504 | AT | Included | Open Plan S-1229 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3505 | AT | Included | Open Plan S-1229 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3506 | AT | Included | Office S-1233 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3507 | AT | Included | Office S-1234 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3508 | AT | Included | Office S-1235 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3509 | AT | Not Included | Policy Director Office S-1237 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3510 | AT | Not Included | Policy Executive Director Office S-1240 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3511 | AT | Included | CORRIDOR S-1280 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3512 | AT | Included | Pantry S-1282 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3513 | AT | Included | Office S-1283 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3514 | AT | Included | Office S-1284 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3515 | AT | Not Included | S-1285 VP R&D |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3516 | AT | Included | Meeting Room S-1288 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3517 | AT | Included | Dressing Room S-1290 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3518 | AT | Included | Waiting Area S-1292 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3520 | AT | Included | Office S-1294 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3521 | AT | Included | Office S-1295 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3522 | AT | Included | Conference Room S-1296 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3523 | AT | Included | Office S-1299 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-3524 | AT | Not Included | Normal Elec. S-1238 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0207 | AT | Included | Open Plan S-1293A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0208 | AT | Included | Open Plan S-1293 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0201A | AT | Not Included | Policy Executive Director Office S-1240 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0201B | AT | Included | Open Plan S-1229 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_SB_1F_AT-0206 | AT | Not Included | Policy Executive Director Office S-1240 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7620 | AT | Included | Office N-1415 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7625 | AT | Included | Office N-1416 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7630 | AT | Included | Office 05 - 2 WKS- N-1407 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7635 | AT | Included | Office N-1418 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7640 | AT | Included | Office N-1419 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7645 | AT | Included | Exp. Workstation N-1420 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7650 | AT | Included | Office N-1421 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7655 | AT | Included | Office N-1422 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7660 | AT | Included | Office 05 - 2 WKS- N-1401 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7665 | AT | Not Included | Normal Elec. N-1425 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7670 | AT | Included | Office N-1426 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7675 | AT | Included | Office N-1428 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7680 | AT | Included | Conf N-1429 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7685 | AT | Included | Office N-1433 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7690 | AT | Included | Office N-1435 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7695 | AT | Included | Office N-1437 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7700 | AT | Not Included | Emer. Elec. N-1438 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7705 | AT | Included | Expansion WORKstation N-1442 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7710 | AT | Included | Office 05 - 24 WKS + N-1441 Room N-1442 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7840 | AT | Included | Conf N-1458 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7845 | AT | Included | Conf N-1459 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7850 | AT | Included | Office N-1459A |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7860 | AT | Included | Exp. Workstation N-1461 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7870 | AT | Included | Office N-1462 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7875 | AT | Included | Office N-1463 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7880 | AT | Included | Office N-1464 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7885 | AT | Included | Office N-1465 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7890 | AT | Included | Workstation N-1466 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7895 | AT | Included | Office N-1467 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7900 | AT | Included | Office N-1468 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7905 | AT | Included | Office N-1469 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7910 | AT | Included | Office N-1470 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7915 | AT | Included | Workstation N-1471 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7920 | AT | Included | Office N-1472 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7925 | AT | Included | Office N-1473 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7930 | AT | Included | Office N-1474 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7935 | AT | Included | Office N-1475 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7940 | AT | Included | Workstation N-1476 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7945 | AT | Included | Office N-1477 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7950 | AT | Included | Office N-1478 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7955 | AT | Included | Office N-1479 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_AT-7960 | AT | Included | Office N-1480 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-7631 | EV | Included | Office 05 - 2 WKS- N-1407 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-7646 | EV | Included | Exp. Workstation N-1420 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-7661 | EV | Included | Office 05 - 2 WKS- N-1401 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-7663 | EV | Not Included | IDF N-1424 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-7711 | EV | Included | Workstation N-1442 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-7712 | EV | Included | Workstation N-1442 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-7861 | EV | Included | Office 05 - 9 WKS N-1461 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_EV-7916 | EV | Included | Office 05 - 8 WKS N-1471 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_CEV-7521 | CEV | Not Included | Isotope N-1404B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-7522 | FEV | Not Included | Isotope N-1404B |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_CEV-7591 | CEV | Not Included | HY Room N-1404J |  |  |  | North Building/FF/FF-10 | CONVENTION | the dot sits just inside the room's upper right corner; the screen shows this as a pair (NB-CAV7590-CEV7591) and the register carries only one half of it, so the reading is recorded against that half; the screen calls this unit CAV7590 and the register calls it AT - joined on the number, which is an assumption
RDC_NB_1F_CEV-7581 | CEV | Not Included | TC3 N-1404H |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-7602 | FEV | Not Included | CELL BIO LABS N-1404K |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_CEV-7611 | CEV | Not Included | TC1 N-1404L |  |  |  | North Building/FF/FF-10 | DIFF | the screen puts NB-CAV7610-CEV7611 in Imaging N-404F; the register says TC1 N-1404L
RDC_NB_1F_CEV-6831 | CEV | Not Included | SHARED COLD LAB N-1345G |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_CEV-7761 | CEV | Not Included | A/L N-1450D |  |  |  | North Building/FF/FF-11 | CONVENTION | the screen shows this as a pair (NB-CAV7760-CEV7761) and the register carries only one half of it, so the reading is recorded against that half; the screen calls this unit CAV7760 and the register calls it AT - joined on the number, which is an assumption
RDC_NB_1F_CEV-7791 | CEV | Not Included | A/L N-1450G |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_1F_FEV-7824 | FEV | Not Included | STEM/PCR Open Lab N-1450M |  |  |  | North Building/FF/FF-11 | OPEN | as NB-VAV7820-VEV7822 - the dot is in the unnamed gap between TC1 N-450L and TC2 N-450N
RDC_NB_2F_AT-4900 | AT | Not Included | Normal Electric N-2102 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_AT-4910 | AT | Not Included | Emergency Electr N-2103 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_EV-4920 | EV | Not Included | IDF N-2104 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_AT-5930 | AT | Included | Office 04 N-1170 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_AT-5940 | AT | Included | Office 05 - 8 WKS- N-1165 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_AT-6979 | AT | Not Included | Normal Elec. N-2107 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_AT-6980 | AT | Not Included | Emer. Elec. N-2108 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_EV-6981 | EV | Not Included | IDF N-2110 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_AT-7975 | AT | Not Included | Normal Elec. N-2111 |  |  |  |  | OPEN | no BMS screen reading for this unit
RDC_NB_2F_AT-7980 | AT | Not Included | Emer. Elec. N-2112 |  |  |  |  | OPEN | no BMS screen reading for this unit