## Claude Log (hidden)
Turn # | Date | User Request | Action Taken | Details | Outcome
1 | 2026-08-28 | Asked how to batch-upload many equipment images so setpoint columns can be added to every row of every Asset Registry sheet; noted varied setpoint types (supply/return, occupied/unoccupied, cooling/heating). | Inspected structure of all 4 registry sheets; recommended image batching approach and proposed a 10-column setpoint schema. | Sheets share layout: row 1 banner, row 2 headers A-E (Tag No., Equipment Type, Included, Room Name, Zones Served), data from row 3. Row counts: HQ 776, SSC 126, QNL 453, RDC 1761. No columns written yet. | Awaiting user confirmation of column schema before writing headers.
2 | 2026-08-28 | Sent 3 HQ BMS screenshots (FCU Summary, VAV Summary, AHU Summary) and said images will be provided one building at a time, starting with HQ. | Added 12 setpoint/temperature columns (F:Q) to all 4 registry sheets; populated HQ AHU, FCU and VAV rows from the screenshots. | Columns F-Q: Supply Air Temp, Return Air Temp, Supply Air Temp SP, Return Air Temp SP, Room Temp, Room Unit SP, Occ SP Cooling, Occ SP Heating, Unocc SP Cooling, Unocc SP Heating, Occupancy Status, Source/Notes. Matched by tag lookup (not row offset) because VAV block mixes tag formats (VAV0001 vs VAV/12/09) and VAV0010 is absent. Tag mapping confirmed: AHU12_0001=AHU/12/01, AHUB_0003=AHU/B/03, FCU0103=0050-FCU-0103, VAV0001=0050-VAV-0001. '***' on screen written literally (Siemens 'not displayable'); 'NA' written where point not configured. AHU screen showed ACTUAL supply/return air temps only - setpoint columns off-screen right, so H/I left blank. | HQ: 26/26 AHU actual temps, 22/132 FCU, 24/616 VAV populated. Open items: (1) confirm whether AHU actual temps belong in F/G or if setpoint screen is needed; (2) VAV/G/07 has ASC tag 0050-VAV-0607 - no matching registry tag, row SKIPPED, needs user decision (possibly VAV0010); (3) need many more screenshots to cover remaining 110 FCU and 592 VAV rows.
3 | 2026-08-28 | Sent 5 RDC BMS screenshots (UB AHU, NB AHU, SB AHU, SB/NB FCU, UB FCU) and requested new columns Outside, Exhaust and Discharge for the RDC building only. | Added Occupied SP + Unoccupied SP (R:S) to all 4 sheets and Outside/Exhaust/Discharge Air Temp (T:V) to RDC only. Populated all 37 RDC AHU rows. Deliberately did NOT populate the 2 FCU screens. | R/S added to all sheets because RDC FCU screens report a single Occupied/Unoccupied BAS setpoint (no cool/heat split) - filing those into the existing Occ SP Cooling/Heating columns would mislabel them. T/U/V RDC-only per request. AHU rows 3-13 NB (Outside+Discharge), 14-30 SB (Outside+Exhaust+Return+Discharge), 31-39 UB (Return+Discharge). Row alignment validated by cross-checking each unit's RUNNING/STOP state against its fan-speed % - all 37 consistent. 'NA' written where the screen showed N/A. CHWS/chilled-water supply+return temps visible on all 3 AHU screens were NOT captured (no column for chilled water; would corrupt the air-temp columns). | 37/37 RDC AHU rows populated and verified (rows 3, 14, 31, 39 spot-read). BLOCKED: the 2 FCU screens (UB FCU ~30 rows, SB FCU ~27 rows) were not entered - angled phone photos of 20-column tables gave inconsistent row-to-value alignment on re-reading, and unlike the AHU screens there is no independent field to cross-check against. Requested straight-on screen captures. Also flagged: FCU-2004 exists twice in registry (RDC_SB_GF_FCU2004 r880 and RDC_NB_1F_FCU2004 r1419), and the SB FCU screen groups FCUs as 'FCU-2004 & FCU-2005' on shared rows - mapping needs user confirmation.
4 | 2026-08-28 | Sent 11 BMS screenshots described as RDC, and said RDC would come in 2 batches; asked to continue after an interrupted run. | Identified the images as QNL (not RDC). Added Eff./Cooling/Heating SP columns (W:Y) to QNL and populated 246 of 248 QNL VAV rows across all 11 screens. | Images were Honeywell / 'Qatar National Library' / QNL FDM - RDC is Siemens/RDC-SERVER1 - so they were written to QNL Asset Registry (also the active sheet). Added W/X/Y because QNL reports Eff. Temp SP, Cooling SP and Heating SP with no occupancy qualifier; using existing Occ. SP Cooling/Heating would have added a qualifier not present in the source. Mapping: SA Temp->F, RA Temp->G, RM Temp & KNX Room Temp->J, RM Temp SP & KNX Room Temp SP->K, Eff/Cool/Heat->W/X/Y. Tag translation VAV/B/S11/001 -> VAV_B_S11_001; all 246 lookups matched with zero misses. Pages partition cleanly with no VAV appearing on two screens - used as a structural cross-check. Screens covered: Type-01 P1-P8, Type-02 P1, Type-03 x2. | 246/248 QNL VAVs populated, no error values. Verified by full-column scan plus 4 spot rows (308, 251, 394, 362). Uncovered: VAV0001 (r155) and VAV_B_S13_005 (r358) - not present on any screen. CAVEAT FLAGGED TO USER: values are eye-transcribed from angled phone photos of ~25-column tables and need a spot-check pass; unlike the RDC AHU screens there was no independent field to validate row alignment against. Still outstanding: RDC FCU screens (2 batches promised), QNL AHU/FCU/CAV rows, all SSC rows, RDC FCU-2004 duplicate, chilled-water columns.
6 | 2026-08-28 | Shared prior-chat context and said another QNL batch is coming; asked me to review state and confirm readiness. | Re-read QNL header schema (A1:Y3) and the Claude Log to re-establish context. No data changes made. | Confirmed QNL columns in place: F/G Supply+Return Air Temp, H/I Supply+Return Air Temp SP, J/K Room Temp + Room Unit SP, L-O Occ/Unocc Cooling+Heating SP, P Occupancy Status, Q Source/Notes, R/S Occupied+Unoccupied SP, W/X/Y Eff./Cooling/Heating SP. QNL equipment: 15 AHU, 137 FCU, 248 VAV (246 populated), 51 CAV. Number format 0.00 already applied to F:Y. | Ready and waiting for the next QNL image batch. Open items unchanged: QNL AHU/FCU/CAV rows, VAV0001 (r155) and VAV_B_S13_005 (r358) uncovered, RDC FCU screens, RDC FCU-2004 duplicate, all SSC rows, chilled-water columns undecided.
7 | 2026-08-28 | Sent an 11-screen QNL batch covering CAV and FCU summary pages. | Transcribed all 11 screens and populated every QNL FCU row (137) and CAV row (51). Also filled Source/Notes (col Q) with the originating screen name for each row. | Screens: CAV Typical P1 (22 rows), CAV Typical P2 (19), CAV Type-01 P1 (3), CAV Type-02 P1 (7); FCU Type-01 P1 (29), P2 (29), P3 (20), FCU Type-02 (3), FCU Type-03 Basement (22), FCU Type-03 Zone04/Upper (19), FCU Type-04 (15). Field mapping by screen variant: SA Temp->F, RA Temp->G, SA Temp SP->H, RA Temp SP->I, RM Temp / KNX Room Temp->J, RM Temp SP / KNX Room Temp SP->K, Eff. Temp SP->W, Cooling SP->X, Heating SP->Y. Tag translation FCU/1F/014->FCU_1F_014 and CAV/B/S13/006->CAV_B_S13_006. Honeywell '??????' (value not displayable) written literally - 18 such cells. Row alignment on the FCU screens validated by cross-checking Fan Speed Cmd against Fan Status (STOP<->STOP, LOW/MEDIUM/HIGH<->RUNNING); only FCU/1F/041 mismatched, which is a genuine fault state shown on screen, not a read error. | QNL now: 137/137 FCU, 51/51 CAV, 246/248 VAV populated; zero error values. STRUCTURAL CONFIRMATION: the 7 FCU screens summed to exactly 137 rows and the 4 CAV screens to exactly 51 - matching registry counts with no duplicates and no unmatched tags, so these screens cover the full QNL FCU and CAV population. Verified by full A3:Y453 scan plus rendered-text read of 9 sample rows (all showing 0.00 format). Still outstanding: all 15 QNL AHU rows (no AHU screen sent), VAV0001 (r155) and VAV_B_S13_005 (r358), RDC FCU screens, RDC FCU-2004 duplicate, all 126 SSC rows, chilled-water columns undecided.
8 | 2026-08-28 | Pointed out that the two RDC FCU screens (Utility Building, South Building) had never been extracted, and re-sent them. | Resolved the row-alignment ambiguity that had blocked these screens by asking the user to confirm two anchor values, then wrote all 56 RDC FCU rows. | Mapping: Room Temper.->J, Room Unit Setpoint->K, Occupancy Status->P, Occupied BAS Setpt->R, Unoccup. BAS Setpt->S. Utility Building 29 rows (RDC_UB_GF_FCU8001-8014/8502-8515 rows 883-904, RDC_UB_MF_FCU8501-8511 rows 905-911). South Building 27 rows (RDC_SB_1F_ rows 836-847, RDC_SB_GF_ rows 868-882). ALIGNMENT: the angled photos allowed two readings offset by one row - critically Reading A had FCU-8013 (WET/MECH/FIRE ROOM) at HIGH/100% valve while Reading B had it OFF/0%, i.e. opposite maintenance conclusions. The usual fan-OFF/valve-0/UNOCCUPIED coupling could not break the tie because FCU-8012 runs SCHEDULER/SCADA where OFF-while-OCCUPIED is valid. Asked the user to confirm 2 anchors; they confirmed FCU-8013 = HIGH/100% and FCU-3001 = 25.4/26.9, both selecting Reading A with no offset. Paired-unit cells ('FCU-2004 & FCU-2005') on the South screen are merged across two sub-rows, first sub-row to the lower tag number. Used 'NA' rather than '***' for Siemens not-available, matching the user's own HQ column L edits this turn. | 56/56 rows written, zero unmatched tags, zero error cells; verified by rendered-text read of 8 sample rows spanning both screens. RESOLVED the long-standing RDC FCU-2004 duplicate: the South Building screen's FCU-2004 is RDC_SB_GF_FCU2004 (row 880), NOT RDC_NB_1F_FCU2004 (row 1419), which remains unpopulated. FLAGGED for user: FCU-8012 Room Unit SP 13.40 and FCU-2501/2504 Room Unit SP 35.20/34.90 are extreme vs neighbours (~21-25) - possible faulty or overridden room units, worth a site check. Also noted the user deleted HQ columns H:I and N:P this turn, so the HQ schema no longer matches QNL/RDC - may need reconciling. Still outstanding: 15 QNL AHU rows, QNL VAV0001 (r155) and VAV_B_S13_005 (r358), all SSC rows, chilled-water columns undecided.

## HQ Asset Registry
Controllable Asset Registry
Tag No. | Equipment Type | Inluded/ Not Inlcuded | ROOM NAME AS PER DRAWINGS | ZONES SERVED | Supply Air Temp (°C) | Return Air Temp (°C) | Occ. SP Cooling (°C) | Occ. SP Heating (°C) | Unocc. SP Cooling (°C) | Unocc. SP Heating (°C)
AHU12_0001 | AHU | Not Included | HQ RF | VAV/9/4.3 legal consult / VAV/9/40 Legal Archieve/ VAV/9/38 BMO ARCHIEVE/ VAV/9/39 CORRIDOR…. | 14.2 | 22.55
AHU12_0002 | AHU | Not Included | HQ RF | VAV/11/4 EXEC. DIR. CORR. F.-UP 11.015/ VAV/11/6 SHEIKHA WING CORRIDOR 11.601 / VAV/11/2 EXEC. DIR. COOR.F.-UP 11.013…. | 17.23 | 22.79
AHU12_0003 | AHU | Not Included | HQ RF |  | 17.23 | 22.79
AHU12_0004 | AHU | Not Included | HQ RF | VAV/9/6 BMO EXEC. ASSIST. 9.016/ VAV/9/10 BMO EXEC. SEC. 9.020 / VAV/11/08 LEGAL ADVISOR 11.018… | 15.52 | 23.41
AHU12_0006 | AHU | Not Included | HQ RF | Sheikha Wing multi purpose room 10.002 | 17.57 | 26.01
AHU12_0007 | AHU | Not Included | HQ RF | VAV/12/01 SHEIKHA WING LOBBY 11.201 / VAV/12/09/ SHEIKHA WING MEETING ROOM 11.204 / VAV/12/03 SHEIKHA ENSUITE 11.202 ... | 15.42 | 22.87
AHU12_0008 | AHU |  | HQ RF |  | 19.15 | 22.34
AHU12_0009 | AHU |  | HQ RF |  | 14.09 | 24.33
AHU12_0010 | AHU | Not Included | HQ RF | Auditorium lvl . 9 / Visitor Center Corridor 08.202 | 12.05 | 21.94
AHU2_0001 | AHU | Not Included | SPA PLANT ROOM 2.302 | SPA MALE TREATMENT 3 2.202 / SPA MALE TREATMENT 2 2.203 / SPA MALE TREATMENT 1 2.204 / SPA CHANGING ROOM 2.213 / SPA FM TREATMENT 2.212…. | 19.93 | 25.01
AHU5_0001 | AHU | Not Included | PLANT ROOM 5.301 | VAV/5/55 CORRIDOR / VAV/5/41 VP EDU MEMBER OF EDU 5.201 / VAV/5/42 VP EDU CHP EXEC SEC 5.211…. With common zones with AHU5_0002 | 16.74 | 22.12
AHU5_0002 | AHU | Not Included | PLANT ROOM 5.301 | VAV/5/56 CORRIDOR / VAV/5/46->48 VP EDU MEMBER OF EDU 5.308/ VAV/5/50 VP EDU ENSUIT 5.210…. With common zones with AHU5_0001 | 16.74 | 22.12
AHU9_0001 | AHU | Not Included | PLANT ROOM 9.111 | VAV/9/30 BOD EXECUTIVE 9.036 / VAV/9/32 BOD SECRETARY 9.037 / VAV/9/24 CORRIDOR…. | 17.18 | 22.05
AHU9_0002 | AHU | Not Included | PLANT ROOM 9.111 | VAV/10/48-49 10.101 Consultant Space / VAV/10/27 10.029 Sh. Serv. Dir. Tr. & Gu. Serv. / VAV/10/30 10.031 Communic. Dir. Comm. Designer…. | 14.1 | 24.9
AHU9_0003 | AHU | Not Included | AHU ROOM 9.109 |  | 10.8 | 23.22
AHUB_0001 | AHU | Not Included | B.001 | VAV/G/48->51 CONFERENCE ROOM B1.021 / VAV/G/31 G.036 PR & MARKET STAFF / VAV/G/32 G.035 PR MARKET MANAGER… / VAV/1/29 01.027 FINANCE AUDITOR/ VAV/1/28 01.026 PROF. STAFF AUDITOR…. / VAV/2/49 02.101A OFFICE SPACE / VAV/2/39 02.010 SUPP. SERV. ADMINIST. / VAV/2/31 02.102 CONSULTANT SPACE OTHERS ... | 17.53 | 23.22
AHUB_0002 | AHU | Not Included | B.001 |  | 17.53 | 23.22
AHUB_0003 | AHU | Not Included | B.006 | VAV/G/7 PR&MARKET STAFF G.013 / VAV/G/08 VISITOR CENTER OFFICE G.014 / VAV/1/42->45 STAFF LOUNGE 1.101… | 17.22 | 22.92
AHUB_0004 | AHU | Not Included | B.006 |  | 17.22 | 22.92
AHUB_0005 | AHU | Not Included | B.016 | VAV/G/16 PR&MARKET SECRETART G.022/ VAV/G/19 CIRCULATION / CAC/G/17 PR &MARKET STAFF G.023/ VAV/2/14 SUPP. SERV. ADMINIST 2.031 / VAV/2/13 SUPP. SERV. SECRETARY 2.030…. | 17.37 | 23.02
AHUB_0006 | AHU | Not Included | B.016 |  | 17.37 | 23.02
AHUB_0007 | AHU | Not Included | B.022 | VAV/G/53 & 54 G.108 CONSULTANT SPACE TRAINEES / VAV/G/42 G.025 FINANCE CASHIER/ VAV/G/45 E-TOWER LOBBY... | 17.65 | 22.17
AHUB_0008 | AHU | Included | B.001 | Auditorium G.102 | 17.22 | 21.77
AHUB_0009 | AHU | Not Included | B.019 | B1.114 FILING STORAGE / B1.021 FILING STORAGE / B1.113 SHEIKHA LOBBY SECURITY ROOM / B1.121 MAINTENANCE ROOM / B1.022 PLAT ROOM … | 16.6 | 23.21
AHUB_0010 | AHU | Not Included | B.019 | VAV/1/81&68 STAFF CAFETERIA 1.701/ VAV/1/60 FOOD HEAT UP 1.702/ VAV/1/67 STAFF CAFETERIA 1.701 | 14.47 | 22.03
AHUB_0011 | AHU | Not Included | B.019 | VAV/B/4->6 SUPP. SPACE MAIL ROOM B1.110 / BAB/B/07 SUPPORT SPACE STATIONARY B1.109/ VAV/1/63->66 MAIN LOBBY… | 16.46 | 21.72
FCU0001 | FCU | Not Included | IDF ROOM B.512
FCU0002 | FCU | Not Included | SECURITY CONTROL B.003
FCU0003 | FCU | Not Included | DOCK MASTER OFFICE B.107
FCU0004 | FCU | Not Included | HH SECURITY B.113
FCU0005 | FCU | Not Included | MALE TOILET B.401
FCU0006 | FCU | Not Included | ROOM B.122
FCU0007 | FCU | Not Included | ROOM B.123
FCU0008 | FCU | Not Included | ROOM B.014
FCU0009 | FCU | Not Included | ROOM B.014
FCU0010 | FCU | Not Included | ROOM B.124
FCU0011 | FCU | Included | CHAUFFEUR ROOM B.117
FCU0012 | FCU | Not Included | IDF ROOM G.531
FCU0013 | FCU | Not Included | IDF ROOM G.531
FCU0014 | FCU | Not Included | IDF ROOM G.512
FCU0015 | FCU | Included | NURSERY CONSULT. G.031
FCU0016 | FCU | Included | COPY PRINT G.017
FCU0017 | FCU | Not Included | CONTROL CENTER G.005
FCU0018 | FCU | Not Included | VESTIBULE G.511
FCU0019 | FCU | Not Included | IDF ROOM 1.531
FCU0020 | FCU | Not Included | IDF ROOM 1.531
FCU0021 | FCU | Not Included | IDF ROOM 1.512
FCU0022 | FCU | Included | PRINT COPY 1.112
FCU0023 | FCU | Not Included | IDF ROOM 2.531
FCU0024 | FCU | Not Included | IDF ROOM 2.531
FCU0025 | FCU | Not Included | TERRACE 2.701
FCU0026 | FCU | Not Included | TERRACE 2.701
FCU0027 | FCU | Not Included | TERRACE 2.701
FCU0028 | FCU | Included | PRINT COPY 2.103
FCU0029 | FCU | Not Included | SPA LOUNGE BAR 2.207
FCU0030 | FCU | Not Included | SPA LOUNGE BAR 2.207
FCU0031 | FCU | Not Included | SPA FITNESS STUDIO 2.208
FCU0032 | FCU | Not Included | SPA FITNESS STUDIO 2.208
FCU0033 | FCU | Not Included | SPA FITNESS STUDIO 2.208
FCU0034 | FCU | Not Included | SPA OFFICE 2.209
FCU0035 | FCU | Not Included | STAFF FEMALE WC 2.210
FCU0036 | FCU | Not Included | SPA. FM BEAUTY SALON 2.211
FCU0037 | FCU | Not Included | SPA. FM BEAUTY SALON 2.211
FCU0038 | FCU | Not Included | SPA FM TREATMENT 2.212
FCU0039 | FCU | Not Included | SPA CHANGING ROOM 2.213
FCU0040 | FCU | Not Included | SPA CHANGING ROOM 2.213
FCU0041 | FCU | Not Included | SPA FM TREATMENT 2.214
FCU0042 | FCU | Not Included | SPA FM TREATMENT 2.215
FCU0043 | FCU | Not Included | SPA FM RELAXATION 2.216
FCU0044 | FCU | Not Included | SPA FM RELAXATION 2.216
FCU0045 | FCU | Not Included | SPA MALE RELAXATION 2.201
FCU0046 | FCU | Not Included | SPA MALE RELAXATION 2.201
FCU0047 | FCU | Not Included | SPA MALE RELAXATION 2.201
FCU0048 | FCU | Not Included | SPA MALE TREATMENT 3 2.202
FCU0049 | FCU | Not Included | SPA MALE TREATMENT 2 2.203
FCU0050 | FCU | Not Included | SPA MALE TREATMENT 1 2.204
FCU0051 | FCU | Not Included | MALE CHANGING ROOM 2.205
FCU0052 | FCU | Not Included | MALE CHANGING ROOM 2.205
FCU0053 | FCU | Not Included | SPA ENTRANCE 2.206
FCU0054 | FCU | Not Included | SPA LOBBY 2.603
FCU0055 | FCU | Not Included | SPA LOBBY 2.603
FCU0056 | FCU | Not Included | IDF ROOM 2.512
FCU0057 | FCU | Not Included | SPA PLANT ROOM 2.302
FCU0058 | FCU | Not Included | SPA PLANT ROOM 2.302
FCU0059 | FCU | Not Included | IDF ROOM 3.531
FCU0060 | FCU | Not Included | IDF ROOM 3.531
FCU0061 | FCU | Not Included | IDF ROOM 3.512
FCU0062 | FCU | Included | COPY/PRINT 3.203
FCU0063 | FCU | Included | PRINT COPY 3.103
FCU0064 | FCU | Not Included | CORRIDOR BRIDGE 3.63
FCU0065 | FCU | Not Included | CORRIDOR BRIDGE 3.63
FCU0066 | FCU | Not Included | CORRIDOR BRIDGE 3.63
FCU0067 | FCU | Not Included | NORTH EAST ZONE
FCU0068 | FCU | Not Included | NORTH EAST ZONE
FCU0069 | FCU | Not Included | NORTH EAST ZONE
FCU0070 | FCU | Not Included | NORTH EAST ZONE
FCU0071 | FCU | Not Included | IDF ROOM 04.531
FCU0072 | FCU | Not Included | IDF ROOM 04.531
FCU0073 | FCU | Not Included | IDF ROOM 04.512
FCU0074 | FCU | Included | PRINT COPY 05.202
FCU0075 | FCU | Not Included | GSM ROOM 05.214
FCU0076 | FCU | Not Included | GSM ROOM 05.214
FCU0077 | FCU | Not Included | VP ADM TERRACE 04.701
FCU0078 | FCU | Not Included | VP ADM TERRACE 04.701
FCU0079 | FCU | Not Included | VP ADM TERRACE 04.701
FCU0080 | FCU | Not Included | VP ADM TERRACE 04.701
FCU0081 | FCU | Not Included | TERRACE 04.702
FCU0082 | FCU | Not Included | TERRACE 04.703
FCU0083 | FCU | Not Included | TERRACE 04.702
FCU0084 | FCU | Included | PRINT COPY 04.110
FCU0085 | FCU | Not Included | IDF ROOM 5.531
FCU0086 | FCU | Not Included | IDF ROOM 5.531
FCU0087 | FCU | Not Included | IDF ROOM 5.512
FCU0088 | FCU | Included | PRINT COPY 5.103
FCU0089 | FCU | Not Included | BRIDGE 06.604
FCU0090 | FCU | Not Included | BRIDGE 06.604
FCU0091 | FCU | Not Included | BRIDGE 06.604
FCU0092 | FCU | Not Included | BRIDGE 5.602
FCU0093 | FCU | Not Included | BRIDGE 5.602
FCU0094 | FCU | Not Included | BRIDGE 5.602
FCU0095 | FCU | Not Included | BRIDGE 5.602
FCU0096 | FCU | Not Included | IDF ROOM 06.531
FCU0097 | FCU |  | NOT FOUND ON THE DRAWING OR SCHEDULE
FCU0098 | FCU | Not Included | IDF ROOM 06.512
FCU0099 | FCU | Not Included | BRIDGE 07.602
FCU0100 | FCU | Not Included | BRIDGE 07.602
FCU0101 | FCU | Not Included | BRIDGE 07.602
FCU0102 | FCU | Included | PRINT COPY 06.104
FCU0103 | FCU | Included | PRINT COPY 06.208 |  |  |  | 21 | NA | 21 | NA
FCU0104 | FCU | Not Included | IDF ROOM 7.531 |  |  |  | NA | NA | NA | NA
FCU0105 | FCU | Not Included | IDF ROOM 7.531 |  |  |  | NA | NA | NA | NA
FCU0106 | FCU | Not Included | IDF ROOM 7.512 |  |  |  | NA | NA | NA | NA
FCU0107 | FCU | Included | PRINT COPY 7.101 |  |  |  | 21 | NA | 21 | NA
FCU0108 | FCU | Included | PRINT COPY 7.104 |  |  |  | 21 | NA | 21 | NA
FCU0109 | FCU | Not Included | IDF ROOM 8.512 |  |  |  | NA | NA | NA | NA
FCU0110 | FCU | Not Included | IDF ROOM 9.531 |  |  |  | NA | NA | NA | NA
FCU0111 | FCU | Not Included | IDF ROOM G.512
FCU0112 | FCU | Not Included | IDF ROOM 9.512 |  |  |  | NA | NA | NA | NA
FCU0113 | FCU | Not Included | IDF ROOM 10.531 |  |  |  | NA | NA | NA | NA
FCU0114 | FCU | Not Included | STAFF LOUNGE STORAGE 1.114
FCU0115 | FCU | Not Included | IDF ROOM 10.512 |  |  |  | NA | NA | NA | NA
FCU0116 | FCU | Included | PRINT COPY 10.038 |  |  |  | 21 | NA | 21 | NA
FCU0117 | FCU | Included | PRINT COPY 10.014 |  |  |  | 21 | NA | 21 | NA
FCU0118 | FCU | Included | TRANSLATOR ROOM 10.111 |  |  |  | NA | NA | NA | NA
FCU0119 | FCU | Not Included | IDF ROOM 11.531 |  |  |  | NA | NA | NA | NA
FCU0120 | FCU | Not Included | IDF ROOM 11.531 |  |  |  | NA | NA | NA | NA
FCU0121 | FCU | Not Included | ELECT. CLOSET 11.110 |  |  |  | NA | NA | NA | NA
FCU0122 | FCU | Not Included | MCC/ELEC ROOM 11.106 |  |  |  | 21.9 | NA | NA | NA
FCU0123 | FCU | Included | PRINT COPY ROOM 11.108 |  |  |  | 21 | NA | 21 | NA
FCU0124 | FCU | Not Included | AV ROOM 11.107 |  |  |  | NA | NA | NA | NA
FCU0125 | FCU | Not Included | IDF ROOM 11.512 |  |  |  | 23.02 | NA | NA | NA
FCU0126 | FCU | Not Included | 12.002 MCC CLOSET
FCU0127 | FCU | Not Included | 12.002 MCC CLOSET
FCU0128 | FCU | Not Included | 12.003 MCC CLOSET
FCU0129 | FCU | Not Included | 12.003 MCC CLOSET
FCU0130 | FCU | Not Included | 12.004 MCC CLOSET
FCU0131 | FCU | Not Included | ROOF PLANT / WALKWAY (NEAR CSRR-0008)
FCU0132 | FCU | Not Included | VISITOR CENTER 9.101 |  |  |  | 21.9 | NA | 21.9 | NA
VAV0001 | VAV | Included | STAFF ENTRANCE B.004 | [5 empty] | 24 | 18.96
VAV0002 | VAV | Included | STAFF LOBBY B.103 | [5 empty] | 24 | 18.96
VAV0003 | VAV | Included | STAFF LOBBY B.103 | [5 empty] | 24 | 18.4
VAV0004 | VAV | Included | SPORT SPACE B.110 | [5 empty] | 24.98 | 18.4
VAV0005 | VAV | Not Included | LOBBY B.116 | [5 empty] | 18.96 | 18.4
VAV0006 | VAV | Not Included | LOBBY B.116 | [5 empty] | 18.96 | 18.4
VAV0007 | VAV | Not Included | CONTROL ROOM G.008 | [5 empty] | 22.88 | 18.4
VAV0008 | VAV | Not Included | PR & MARKET MANAGER G.009 | [5 empty] | 25.12 | 18.96
VAV0009 | VAV | Included | PR & MARKET STAFF G.010 | [5 empty] | 25.12 | 18.96
VAV0011 | VAV | Not Included | PR & MARK. MANA. G.011 | [5 empty] | 24.56 | 18.54
VAV0012 | VAV | Included | PR & MARKET STAFF G.012 | [5 empty] | 22.6 | 16.44
VAV0013 | VAV | Not Included | VISITOR OFF. G.014 | [5 empty] | 22.6 | 16.44
VAV0014 | VAV | Included | PR & MARKET STAFF G.015 | [5 empty] | 25.12 | 18.96
VAV0015 | VAV | Included | PR & MAR. STAFF G.018 | [5 empty] | 22.04 | 16.02
VAV0016 | VAV | Included | PR & MAR. STAFF G.019 | [5 empty] | 27.92 | 18.4
VAV0017 | VAV | Included | PR & MAR. STAFF G.020 | [5 empty] | 27.92 | 18.4
VAV0018 | VAV | Included | PR & MAR. STAFF G.021 | [5 empty] | 26.52 | 20.5
VAV0019 | VAV | Included | PR & MARKET SEC. G.022 | [5 empty] | 23.02 | 17
VAV0020 | VAV | Included | PR & MARKET STAFF G.023 | [5 empty] | 26.52 | 20.5
VAV0021 | VAV | Not Included | CORRIDOR G.601 | [5 empty] | 27.92 | 18.4
VAV0022 | VAV | Not Included | CORRIDOR G.601 | [5 empty] | 27.92 | 18.4
VAV0023 | VAV | Included | SHOP G.105 | [5 empty] | 27.92 | 18.4
VAV0024 | VAV | Not Included | LOBBY G.104 | [5 empty] | 27.92 | 18.4
VAV0025 | VAV | Not Included | LOBBY G.104 | [5 empty] | 27.92 | 24.98
VAV0026 | VAV | Not Included | BMS ROOM G.103
VAV0027 | VAV | Not Included | PR & MARKET MANAGER G.004
VAV0028 | VAV | Not Included | PR & MARKET MANAGER G.003
VAV0029 | VAV | Not Included | PR & MARKET MANAGER G.002
VAV0030 | VAV | Not Included | G.CORIDOR
VAV0031 | VAV | Included | PR & MARKET STAFF G.001
VAV0032 | VAV | Included | PR & MARKET STAFF G.038
VAV0033 | VAV | Included | PR & MARKET STAFF G.037
VAV0034 | VAV | Included | PR & MARKET STAFF G.036
VAV0035 | VAV | Included | PR & MARKET STAFF G.035
VAV0036 | VAV | Included | PR & MARKET STAFF G.034
VAV0037 | VAV | Included | PR & MARKET STAFF G.033
VAV0038 | VAV | Included | PR & MARKET STAFF G.032
VAV0039 | VAV | Included | STAFF G.030
VAV0040 | VAV | Included | SENSORY G.029
VAV0041 | VAV | Included | SENSORY G.029
VAV0042 | VAV | Not Included | PR& MARKET DIRECTOR ENSUIT G.028
VAV0043 | VAV | Included | FINANCE CASHIER G.026
VAV0044 | VAV | Not Included | VIP LOUNGE G.025
VAV0045 | VAV | Not Included | E-TOWER LOBBY G.107
VAV0046 | VAV | Not Included | CORRIDOR (SOUTH EAST) G.602
VAV0047 | VAV | Not Included | CORRIDOR (SOUTH EAST) G.603
VAV0048 | VAV | Included | CONFERENCE ROOM G.101
VAV0049 | VAV | Included | CONFERENCE ROOM G.101
VAV0050 | VAV | Included | CONFERENCE ROOM G.101
VAV0051 | VAV | Included | CONFERENCE ROOM G.101
VAV0052 | VAV | Included | SOFT PLAY & CREATIVE LEARNING G.108
VAV0053 | VAV | Included | SOFT PLAY & CREATIVE LEARNING G.108
VAV0054 | VAV | Not Included | FINANCE MANAGER 1.011
VAV0055 | VAV | Not Included | FINANCE MANAGER 1.012
VAV0056 | VAV | Not Included | FINANCE MANAGER 1.013
VAV0057 | VAV | Included | FINANCE STAFF 1.014
VAV0058 | VAV | Included | FINANCE STAFF 1.015
VAV0059 | VAV | Included | FINANCE SECRETARY 1.016
VAV0060 | VAV | Not Included | FINANCE DIRECTOR 1.017
VAV0061 | VAV | Not Included | FINANCE MANAGER 1.018
VAV0062 | VAV | Not Included | FINANCE MANAGER 1.019
VAV0063 | VAV | Not Included | FINANCE MANAGER 1.020
VAV0064 | VAV | Included | FINANCE SEC 1.021
VAV0065 | VAV | Included | FINANCE SEC 1.022
VAV0066 | VAV | Included | FINANCE AUDIT 1.023
VAV0067 | VAV | Included | FINANCE AUDIT 1.024
VAV0068 | VAV | Included | FINANCE STAFF 1.025
VAV0069 | VAV | Included | FINANCE STAFF 1.026
VAV0070 | VAV | Not Included | FINANCE MANAGER 1.027
VAV0071 | VAV | Not Included | FINANCE MANAGER 1.028
VAV0072 | VAV | Not Included | FINANCE MANAGER 1.029
VAV0073 | VAV | Included | FINANCE SECRETARY 1.001
VAV0074 | VAV | Not Included | FINANCE MANAGER 1.002
VAV0075 | VAV | Not Included | FINANCE MANAGER 1.003
VAV0076 | VAV | Not Included | FINANCE MANAGER 1.004
VAV0077 | VAV | Included | FINANCE SECRETARY 1.005
VAV0078 | VAV | Included | FINANCE STAFF 1.006
VAV0079 | VAV | Included | FINANCE STAFF 1.007
VAV0080 | VAV | Not Included | GROUND FLOOR VIP ENTRANCE 1.401
VAV0081 | VAV | Not Included | GROUND FLOOR VIP ENTRANCE 1.401
VAV0082 | VAV | Not Included | GROUND FLOOR VIP ENTRANCE 1.401
VAV0083 | VAV | Included | STAFF LOUNGE 1.101
VAV0084 | VAV | Included | STAFF LOUNGE 1.101
VAV0085 | VAV | Included | STAFF LOUNGE 1.101
VAV0086 | VAV | Included | STAFF LOUNGE 1.101
VAV0087 | VAV | Included | FINANCE MEETING ROOM 1.108
VAV0088 | VAV | Included | CONSULTANT SPACE 1.109
VAV0089 | VAV | Included | CONSULTANT SPACE 1.109
VAV0090 | VAV | Included | CONFERENCE ROOM 1.110
VAV0091 | VAV | Included | PRAYER ROOM 1.105
VAV0092 | VAV | Included | FINANCE CASHIER 1.106
VAV0093 | VAV | Included | FINANCE ROOM 1.116
VAV0094 | VAV | Not Included | FINANCE AUDITOR 1.117
VAV0095 | VAV | Not Included | FINANCE AUDITOR 1.115
VAV0096 | VAV | Included | STAFF LOUNGE 1.101
VAV0097 | VAV | Not Included | CORRIDOR 1.602
VAV0098 | VAV | Not Included | CORRIDOR 1.602
VAV0099 | VAV | Not Included | SOUTH EAST ZONE
VAV0100 | VAV | Included | FINANCE RECORD STORAGE 1.111
VAV0101 | VAV | Included | FOOD HEAT UP 1.702
VAV0102 | VAV | Included | WASHING AREA 1.706
VAV0103 | VAV | Not Included | LOBBY (GROUND FLOOR)
VAV0104 | VAV | Not Included | LOBBY (GROUND FLOOR)
VAV0105 | VAV | Not Included | LOBBY (GROUND FLOOR)
VAV0106 | VAV | Not Included | LOBBY (GROUND FLOOR)
VAV0107 | VAV | Included | STAFF CAFETERIA 1.701
VAV0108 | VAV | Included | STAFF CAFETERIA 1.701
VAV0109 | VAV | Not Included | DIRECTOR ENSUIT 2.018
VAV0110 | VAV | Included | SUPP. SER. ADMIN 2.019
VAV0111 | VAV | Included | SUPP. SER. ADMIN 2.020
VAV0112 | VAV | Included | SUPP. SER. ADMIN 2.021
VAV0113 | VAV | Included | SUPP. SER. SECRETARY 2.022
VAV0114 | VAV | Included | SUPP. SER. ADMIN 2.023
VAV0115 | VAV | Included | SUPP. SER. ADMIN 2.024
VAV0116 | VAV | Included | SUPP. SER. ADMIN 2.025
VAV0117 | VAV | Included | SUPP. SER. SECRETARY 2.026
VAV0118 | VAV | Included | SUPP. SER. ADMIN 2.027
VAV0119 | VAV | Included | SUPP. SER. ADMIN 2.028
VAV0120 | VAV | Included | SUPP. SER. ADMIN 2.029
VAV0121 | VAV | Included | SUPP. SER. SECRETARY 2.030
VAV0122 | VAV | Included | SUPP. SER. ADMIN 2.031
VAV0123 | VAV | Included | SUPP. SER. ADMIN 2.032
VAV0124 | VAV | Included | SUPP. SER. ADMIN 2.033
VAV0125 | VAV | Included | SUPP. SER. SECRETARY 2.034
VAV0126 | VAV | Included | SUPP. SER. ADMIN 2.035
VAV0127 | VAV | Included | SUPP. SER. ADMIN 2.036
VAV0128 | VAV | Included | OFFICE SPACE 2.110A
VAV0129 | VAV | Not Included | 02.CORIDOR
VAV0130 | VAV | Not Included | 02.CORIDOR
VAV0131 | VAV | Included | FEMALE PRAYER ROOM 2.109
VAV0132 | VAV | Included | MEETING ROOM 2.108
VAV0133 | VAV | Included | MEETING ROOM 2.108
VAV0134 | VAV | Not Included | LOUNGE 2.105
VAV0135 | VAV | Included | CONSULTANT SPACE 2.104
VAV0136 | VAV | Included | CONSULTANT SPACE 2.104
VAV0137 | VAV | Included | CONSULTANT SPACE 2.102
VAV0138 | VAV | Included | SUPP. SER. SECRETARY 2.017
VAV0139 | VAV | Included | SUPP. SER. ADMIN 2.016
VAV0140 | VAV | Included | SUPP. SER. ADMIN 2.015
VAV0141 | VAV | Included | SUPP. SER. ADMIN 2.014
VAV0142 | VAV | Included | SUPP. SER. SECRETARY 2.013
VAV0143 | VAV | Included | SUPP. SER. ADMIN 2.012
VAV0144 | VAV | Included | SUPP. SER. ADMIN 2.011
VAV0145 | VAV | Included | SUPP. SER. ADMIN 2.010
VAV0146 | VAV | Included | SUPP. SER. SECRETARY 2.009
VAV0147 | VAV | Not Included | DEBATE EXECUTIVE 2.008
VAV0148 | VAV | Not Included | DEBATE EXECUTIVE 2.007
VAV0149 | VAV | Not Included | DEBATE EXECUTIVE 2.006
VAV0150 | VAV | Not Included | DEBATE EXECUTIVE 2.005
VAV0151 | VAV | Included | DEBATE SECRETARY 2.004
VAV0152 | VAV | Not Included | DEBATE EXECUTIVE 2.003
VAV0153 | VAV | Not Included | DEBATE EXECUTIVE 2.002
VAV0154 | VAV | Included | STORAGE ROOM 2.001
VAV0155 | VAV | Included | OFFICE SPACE 2.101A
VAV0156 | VAV | Not Included | 02.CORIDOR
VAV0157 | VAV | Included | HR IMMIG STAFF 3.017
VAV0158 | VAV | Included | HR IMMIG STAFF 3.018
VAV0159 | VAV | Included | HR IMMIG STAFF 3.019
VAV0160 | VAV | Included | HR IMMIG STAFF 3.020
VAV0161 | VAV | Included | HR IMMIG STAFF 3.021
VAV0162 | VAV | Included | HR IMMIG STAFF 3.022
VAV0163 | VAV | Included | HR IMMIG STAFF 3.023
VAV0164 | VAV | Included | HR IMMIG STAFF 3.024
VAV0165 | VAV | Included | HR IMMIG STAFF 3.025
VAV0166 | VAV | Included | HR IMMIG STAFF 3.026
VAV0167 | VAV | Included | HR IMMIG STAFF 3.027
VAV0168 | VAV | Included | HR IMMIG STAFF 3.028
VAV0169 | VAV | Included | HR IMMIG STAFF 3.029
VAV0170 | VAV | Included | HR IMMIG STAFF 3.030
VAV0171 | VAV | Included | HR IMMIG STAFF 3.031
VAV0172 | VAV | Included | HR IMMIG STAFF 3.032
VAV0173 | VAV | Included | MEETING ROOM 3.033
VAV0174 | VAV | Included | MEETING ROOM 3.033
VAV0175 | VAV | Included | OFFICE SPACE 3.105B
VAV0176 | VAV | Not Included | 03.CORIDOR
VAV0177 | VAV | Not Included | ABLUTION ROOM 3.36
VAV0178 | VAV | Included | FEMALE PRAYER ROOM 3.105A
VAV0179 | VAV | Not Included | 03.CORIDOR
VAV0180 | VAV | Not Included | LOUNGE 3.001
VAV0181 | VAV | Included | CONSULTANT SPACE TRAINEES 3.102
VAV0182 | VAV | Included | CONSULTANT SPACE TRAINEES 3.102
VAV0183 | VAV | Included | CONSULTANT SPACE TRAINEES 3.102
VAV0184 | VAV | Included | HR IMMG SECRETARY 3.104
VAV0185 | VAV | Included | HR IMMIG STAFF 3.012
VAV0186 | VAV | Included | HR IMMIG STAFF 3.013
VAV0187 | VAV | Included | HR IMMIG STAFF 3.014
VAV0188 | VAV | Included | HR IMMIG STAFF 3.015
VAV0189 | VAV | Included | HR IMMIG STAFF 3.016
VAV0190 | VAV | Included | HR IMMIG STAFF 3.003
VAV0191 | VAV | Included | HR IMMIG STAFF 3.004
VAV0192 | VAV | Included | HR IMMIG STAFF 3.005
VAV0193 | VAV | Included | HR IMMIG STAFF 3.006
VAV0194 | VAV | Included | HR IMMIG STAFF 3.007
VAV0195 | VAV | Included | HR IMMIG STAFF 3.008
VAV0196 | VAV | Included | HR IMMIG STAFF 3.009
VAV0197 | VAV | Included | HR IMMIG STAFF 3.010
VAV0198 | VAV | Included | HR IMMIG STAFF 3.011
VAV0199 | VAV | Included | OFFICE SPACE 3.101
VAV0200 | VAV | Included | HR IMMIG STAFF 3.002
VAV0201 | VAV | Not Included | 03.CORIDOR
VAV0202 | VAV | Included | OFFICE SPACE 3.202A
VAV0203 | VAV | Included | OFFICE SPACE 3.202B
VAV0204 | VAV | Included | HR IMMIGRATION 3.205
VAV0205 | VAV | Not Included | HR IMMIG MANAGER 3.206
VAV0206 | VAV | Not Included | HR IMMIG MANAGER 3.207
VAV0207 | VAV | Not Included | HR IMMIG MANAGER 3.208
VAV0208 | VAV | Not Included | HR IMMIG MANAGER 3.209
VAV0209 | VAV | Included | HR IMMIG OFFICER 3.210
VAV0210 | VAV | Included | HR IMMIG OFFICER 3.210
VAV0211 | VAV | Not Included | HR IMMIG MANAGER 3.211
VAV0212 | VAV | Included | HR IMMIG SEC. 3.212
VAV0213 | VAV | Not Included | HR IMMIG DIR. ENSUIT 3.213
VAV0214 | VAV | Not Included | IT DIR. ENSUIT 3.214
VAV0215 | VAV | Not Included | IT DIR. ENSUIT 3.215
VAV0216 | VAV | Included | PROC. CONTR. SECRETARY 3.216
VAV0217 | VAV | Not Included | PROC. & CONTR. DIR. E 3.201
VAV0218 | VAV | Included | PROC. & CONTR. MEETING ROOM 3.301
VAV0219 | VAV | Included | PROC. & CONTR. MEETING ROOM 3.301
VAV0220 | VAV | Included | HR IMMG. MEETING ROOM 3.302
VAV0221 | VAV | Not Included | SOUTH EAST CORRIDOR 3.602
VAV0222 | VAV | Not Included | STR. PL. DIR. ENSUIT 04.004
VAV0223 | VAV | Not Included | STR. PL. DIR. MEETING ROOM 04.005
VAV0224 | VAV | Not Included | STR. PL. DIR. MANAGER 04.006
VAV0225 | VAV | Not Included | STR. PL. DIR. MANAGER 04.007
VAV0226 | VAV | Not Included | STR. PL. DIR. MANAGER 04.008
VAV0227 | VAV | Not Included | STR. PL. DIR. HEAD OF PL. 04.009
VAV0228 | VAV | Not Included | STR. PL. DIR. HEAD OF PL. 04.010
VAV0229 | VAV | Not Included | STR. PL. DIR. HEAD OF PL. 04.011
VAV0230 | VAV | Not Included | STR. PL. DIR. HEAD OF PL. 04.012
VAV0231 | VAV | Not Included | STR. PL. DIR. HEAD OF PL. 04.013
VAV0232 | VAV | Not Included | STR. PL. DIR. MANAGER 04.014
VAV0233 | VAV | Included | OFFICE SPACE 04.015C
VAV0234 | VAV | Included | OFFICE SPACE 04.015A
VAV0235 | VAV | Not Included | S-TOWER CORRIDOR 4.601
VAV0236 | VAV | Not Included | VP EDU STORAGE 04.109
VAV0237 | VAV | Not Included | S-TOWER CORRIDOR 4.601
VAV0238 | VAV | Included | STR. PL. DIR. TECH. STAFF 04.108
VAV0239 | VAV | Included | STR. PL. DIR. TECH. STAFF 04.107
VAV0240 | VAV | Not Included | WAITING LOUNGE 04.104
VAV0241 | VAV | Not Included | WAITING LOUNGE 04.104
VAV0242 | VAV | Not Included | STR. PL. DIR. MANAGER 04.002
VAV0243 | VAV | Included | STR. PL. DIR. EXEC. SECRE. 04.003
VAV0244 | VAV | Included | OFFICE SPACE 04.001B
VAV0245 | VAV | Included | OFFICE SPACE 04.001D
VAV0246 | VAV | Included | OFFICE SPACE 04.001F
VAV0247 | VAV | Included | OFFICE SPACE 04.001G
VAV0248 | VAV | Included | STORAGE SPACE 04.103
VAV0249 | VAV | Included | OFFICE SPACE 04.102
VAV0250 | VAV | Included | OFFICE SPACE 04.101
VAV0251 | VAV | Not Included | S-TOWER CORRIDOR 4.601
VAV0252 | VAV | Included | OFFICE SPACE 04.201
VAV0253 | VAV | Included | OFFICE SPACE 04.204
VAV0254 | VAV | Not Included | VP ADM MANAGER 04.205
VAV0255 | VAV | Not Included | VP ADM MANAGER 04.206
VAV0256 | VAV | Not Included | VP ADM SEC. 04.208
VAV0257 | VAV | Not Included | VP ADM SEC. 04.208
VAV0258 | VAV | Not Included | VP ADM MANAGER 04.209
VAV0259 | VAV | Not Included | VP ADM MANAGER 04.210
VAV0260 | VAV | Not Included | VP ADM MANAGER 04.211
VAV0261 | VAV | Included | VP ADM PERS. ASS. 04.212
VAV0262 | VAV | Not Included | VP ADM ENSUIT 04.213
VAV0263 | VAV | Not Included | VP ADM MEETING ROOM 04.301
VAV0264 | VAV | Not Included | VP ADM MEETING ROOM 04.301
VAV0265 | VAV | Not Included | E-TOWER CORRIDOR 4.603
VAV0266 | VAV | Not Included | E-TOWER CORRIDOR 4.603
VAV0267 | VAV | Not Included | VP EDU DIR ENSUIT 5.012
VAV0268 | VAV | Not Included | VP EDU SECR. 5.013
VAV0269 | VAV | Included | VP EDU ASSIS. 5.014
VAV0270 | VAV | Included | VP EDU ASSIS. 5.015
VAV0271 | VAV | Included | VP EDU ASSIS. 5.016
VAV0272 | VAV | Included | VP EDU ASSIS. 5.017
VAV0273 | VAV | Not Included | VP EDU OFF. 5.018
VAV0274 | VAV | Not Included | VP EDU OFF. 5.019
VAV0275 | VAV | Not Included | VP EDU OFF. 5.020
VAV0276 | VAV | Not Included | VP EDU OFF. 5.021
VAV0277 | VAV | Not Included | VP EDU OFF. 5.022
VAV0278 | VAV | Not Included | VP EDU OFF. 5.023
VAV0279 | VAV | Included | VP EDU SEC. 5.024
VAV0280 | VAV | Not Included | VP EDU DIR ENSUIT 5.025
VAV0281 | VAV | Included | VP EDU ASS. 5.026
VAV0282 | VAV | Not Included | S-TOWER CORRIDOR 5.601
VAV0283 | VAV | Not Included | VP EDU OFF. 5.110
VAV0284 | VAV | Not Included | VP EDU ASS. 5.109
VAV0285 | VAV | Not Included | VP EDU SEC. 5.108
VAV0286 | VAV | Not Included | VP EDU SEC. 5.107
VAV0287 | VAV | Not Included | VP EDU SEC. 5.107
VAV0288 | VAV | Not Included | VP EDU LOUNGE WAITING 5.104
VAV0289 | VAV | Not Included | VP EDU LOUNGE WAITING 5.104
VAV0290 | VAV | Included | VP EDU OFFICERS 5.009
VAV0291 | VAV | Included | VP EDU OFFICERS 5.010
VAV0292 | VAV | Included | VP EDU ASSISTANT 5.011
VAV0293 | VAV | Not Included | VP EDU OFF. DIR ENSUIT 5.002
VAV0294 | VAV | Not Included | VP EDU SECRE. 5.003
VAV0295 | VAV | Included | VP EDU ASSISTANT 5.004
VAV0296 | VAV | Included | VP EDU OFFICERS 5.005
VAV0297 | VAV | Included | VP EDU OFFICERS 5.006
VAV0298 | VAV | Included | VP EDU ASSISTANT 5.007
VAV0299 | VAV | Included | VP EDU ASSISTANT 5.008
VAV0300 | VAV | Included | MEETING ROOM 5.102
VAV0301 | VAV | Included | MEETING ROOM 5.102
VAV0302 | VAV | Included | VP EDU SECRETARY 5.101
VAV0303 | VAV | Included | VP EDU ASSISTANT 5.001
VAV0304 | VAV | Not Included | S-TOWER CORRIDOR 5.601
VAV0305 | VAV | Included | VP EDU MEMB. 5.201
VAV0306 | VAV | Included | VP EDU MEMB. 5.202
VAV0307 | VAV | Included | VP EDU MEMB. 5.203
VAV0308 | VAV | Included | VP EDU MEMB. 5.205
VAV0309 | VAV | Included | VP EDU MEMB. 5.205
VAV0310 | VAV | Included | VP EDU MEMB. 5.206
VAV0311 | VAV | Included | VP EDU MEMB. 5.207
VAV0312 | VAV | Included | VP EDU MEMB. 5.208
VAV0313 | VAV | Included | VP EDU MEMB. 5.209
VAV0314 | VAV | Not Included | VP EDU ENSUIT 5.210
VAV0315 | VAV | Not Included | VP EDU SEC. 5.211
VAV0316 | VAV | Included | VP EDU MEMB. 5.212
VAV0317 | VAV | Not Included | VP EDU DIR. ENSUIT 5.213
VAV0318 | VAV | Not Included | 05.CORIDOR
VAV0319 | VAV | Not Included | 05.CORIDOR
VAV0320 | VAV | Not Included | 05.CORIDOR
VAV0321 | VAV | Not Included | 05.CORIDOR
VAV0322 | VAV | Not Included | VP EDU OFF. 5.027
VAV0323 | VAV | Included | INT. AUDIT 06.012
VAV0324 | VAV | Included | INT. AUDIT SEC. 06.013
VAV0325 | VAV | Included | ACA. AUDIT 06.014
VAV0326 | VAV | Included | ACA. AUDIT 06.015
VAV0327 | VAV | Included | ACA. AUDIT 06.016
VAV0328 | VAV | Included | ACA. AUDIT 06.017
VAV0329 | VAV | Included | ACA. AUDIT 06.018
VAV0330 | VAV | Included | ACA. AUDIT 06.019
VAV0331 | VAV | Included | ACA. AUDIT 06.020
VAV0332 | VAV | Included | ACA. AUDIT SEC. 06.021
VAV0333 | VAV | Included | ACA. AUDIT SEC. 06.022
VAV0334 | VAV | Included | ACA. SEN. AUDIT 06.023
VAV0335 | VAV | Included | ACA. SEN. AUDIT 06.024
VAV0336 | VAV | Included | FACI. MANA. SEC. 06.025
VAV0337 | VAV | Not Included | FACILITY MANAG. DIR. ENSUIT 06.026
VAV0338 | VAV | Not Included | VP CAPITAL CONSUL. 06.027
VAV0339 | VAV | Not Included | VP CAPITAL CONSUL. 06.028
VAV0340 | VAV | Not Included | S-TOWER CORRIDOR 6.601
VAV0341 | VAV | Included | VP CAPITAL WORK ASSIST 06.109
VAV0342 | VAV | Not Included | VP CAPITAL PROJ. COORD 06.108
VAV0343 | VAV | Not Included | S-TOWER CORRIDOR 6.601
VAV0344 | VAV | Not Included | LOUNGE 06.105
VAV0345 | VAV | Not Included | LOUNGE 06.105
VAV0346 | VAV | Included | INT. AUDIT SUPP. AUDIT 06.009
VAV0347 | VAV | Included | INT. AUDIT SEC. 06.010
VAV0348 | VAV | Included | INT. AUDIT 06.011
VAV0349 | VAV | Included | INT. AUDIT ARCHIVE ROOM 06.002
VAV0350 | VAV | Included | INT. AUDIT SUPP. AUDIT 06.003
VAV0351 | VAV | Included | INT. AUDIT SUPP. AUDIT 06.004
VAV0352 | VAV | Included | INT. AUDIT SUPP. AUDIT 06.005
VAV0353 | VAV | Included | INT. AUDIT SUPP. AUDIT 06.006
VAV0354 | VAV | Included | INT. AUDIT SUPP. AUDIT 06.007
VAV0355 | VAV | Included | INT. AUDIT SUPP. AUDIT 06.008
VAV0356 | VAV | Included | OFFICE SPACE 06.103
VAV0357 | VAV | Included | OFFICE SPACE 06.102
VAV0358 | VAV | Included | OFFICE SPACE 06.101
VAV0359 | VAV | Included | AUDIT ARCHIVE 06.001
VAV0360 | VAV | Not Included | S-TOWER CORRIDOR 6.601
VAV0361 | VAV | Not Included | VP CAPITAL PROJ. MANAGER 06.201
VAV0362 | VAV | Not Included | VP CAPITAL PROJ. MANAGER 06.202
VAV0363 | VAV | Not Included | VP CAPITAL PROJ. MANAGER 06.204
VAV0364 | VAV | Not Included | VP CAPITAL CONSU. 06.205
VAV0365 | VAV | Not Included | VP CAPITAL STORAGE 06.206
VAV0366 | VAV | Included | VP CAPITAL SEC. 06.207
VAV0367 | VAV | Not Included | VP CAPITAL ENSUIT 06.209
VAV0368 | VAV | Included | VP CAPITAL SEC. 06.210
VAV0369 | VAV | Included | VP CAPITAL SEC. 06.211
VAV0370 | VAV | Not Included | VP CAPITAL DIR. ENSUIT 06.212
VAV0371 | VAV | Not Included | E-TOWER CORRIDOR 6.603
VAV0372 | VAV | Not Included | E-TOWER CORRIDOR 6.603
VAV0373 | VAV | Included | CA ENSUIT 7.017
VAV0374 | VAV | Included | CA SEC. 7.018
VAV0375 | VAV | Included | BD UNIT SEC. 7.019
VAV0376 | VAV | Not Included | BD UNIT EXECU. 7.020
VAV0377 | VAV | Not Included | BD UNIT EXECU. 7.021
VAV0378 | VAV | Not Included | BD UNIT EXECU. 7.022
VAV0379 | VAV | Not Included | BD UNIT EXECU. 7.023
VAV0380 | VAV | Not Included | BD UNIT EXECU. 7.024
VAV0381 | VAV | Not Included | BD UNIT EXECU. 7.025
VAV0382 | VAV | Not Included | BD UNIT EXECU. 7.026
VAV0383 | VAV | Not Included | BD UNIT EXECU. 7.027
VAV0384 | VAV | Not Included | BD UNIT EXECU. 7.028
VAV0385 | VAV | Included | MEETING ROOM 7.029
VAV0386 | VAV | Included | MEETING ROOM 7.029
VAV0387 | VAV | Included | OFFICE SPACE 7.030
VAV0388 | VAV | Included | OFFICE SPACE 7.031A
VAV0389 | VAV | Not Included | S-TOWER CORRIDOR 7.601
VAV0390 | VAV | Not Included | S-TOWER CORRIDOR 7.601
VAV0391 | VAV | Included | OFFICE SPACE 7.032
VAV0392 | VAV | Included | OFFICE SPACE 7.032
VAV0393 | VAV | Not Included | LOUNGE 7.106
VAV0394 | VAV | Included | CA SECRETARY 7.105
VAV0395 | VAV | Included | CA SECRETARY 7.103
VAV0396 | VAV | Included | CA SECRETARY 7.102
VAV0397 | VAV | Included | DOC. UNIT EMPLOYEE 07.001
VAV0398 | VAV | Included | DOC. UNIT MULTIMEDIA STUDIO 07.002
VAV0399 | VAV | Not Included | S-TOWER CORRIDOR 7.601
VAV0400 | VAV | Included | DOC. UNIT MULTIMEDIA STUDIO 07.002
VAV0401 | VAV | Included | DOC. UNIT EMPLOYEE 7.003
VAV0402 | VAV | Included | DOC. UNIT EMPLOYEE 7.004
VAV0403 | VAV | Included | DOC. UNIT EMPLOYEE 7.005
VAV0404 | VAV | Included | DOC. UNIT EMPLOYEE 7.006
VAV0405 | VAV | Included | CA COORD 7.007
VAV0406 | VAV | Included | CA COORD 7.008
VAV0407 | VAV | Included | CA COORD 7.009
VAV0408 | VAV | Included | CA COORD 7.010
VAV0409 | VAV | Included | CA COORD 7.011
VAV0410 | VAV | Included | CA COORD 7.012
VAV0411 | VAV | Included | CA COORD 7.013
VAV0412 | VAV | Included | CA COORD 7.014
VAV0413 | VAV | Included | CA COORD 7.015
VAV0414 | VAV | Included | CA COORD 7.016
VAV0415 | VAV | Included | CONSULTANT SPACE 7.201
VAV0416 | VAV | Not Included | PRE. EXEC. OFFICE 7.202
VAV0417 | VAV | Not Included | PRE. EXEC. OFFICE 7.204
VAV0418 | VAV | Not Included | PRE. EXEC. OFFICE 7.204
VAV0419 | VAV | Not Included | PRE. EXEC. OFFICE 7.205
VAV0420 | VAV | Not Included | PRE. EXEC. OFFICE 7.205
VAV0421 | VAV | Not Included | PRESIDENT SUPP. SEC. 7.208
VAV0422 | VAV | Not Included | E-TOWER CORRIDOR 7.603
VAV0423 | VAV | Not Included | PRESIDENT EXEC. SEC. 7.209
VAV0424 | VAV | Not Included | PRESIDENT EXEC. SEC. 7.210
VAV0425 | VAV | Not Included | PRESIDENT ENSUIT 7.211
VAV0426 | VAV | Not Included | PRESIDENT MEETING ROOM 7.212
VAV0427 | VAV | Not Included | VICE CHAIRPERSON ENSULT 7.213
VAV0428 | VAV | Not Included | VICE CHAIRPERSON SEC. 7.214
VAV0429 | VAV | Not Included | MEETING ROOM 7.215
VAV0430 | VAV | Included | MEETING ROOM 7.301
VAV0431 | VAV | Included | MEETING ROOM 7.301
VAV0432 | VAV | Included | MEETING ROOM 7.301
VAV0433 | VAV | Not Included | OBSERVATION SPACE 8.001
VAV0434 | VAV | Not Included | OBSERVATION SPACE 8.001
VAV0435 | VAV | Not Included | OBSERVATION SPACE 8.001
VAV0436 | VAV | Not Included | OBSERVATION SPACE 8.001
VAV0437 | VAV | Not Included | OBSERVATION SPACE 8.001
VAV0438 | VAV | Not Included | VISITORS CENTER OFFICE 8.002
VAV0439 | VAV | Not Included | VISITORS CENTER CORRIDOR 8.602
VAV0440 | VAV | Not Included | VISITORS CENTER CORRIDOR 8.602
VAV0441 | VAV | Not Included | VISITORS CENTER CORRIDOR 8.602
VAV0442 | VAV | Not Included | VISITORS CENTER CORRIDOR 8.602
VAV0443 | VAV | Not Included | VISITORS CENTER CORRIDOR 8.602
VAV0444 | VAV | Included | BMO EXEC. ASSIST. 9.011
VAV0445 | VAV | Included | BMO EXEC. ASSIST. 9.012
VAV0446 | VAV | Included | BMO EXEC. ASSIST. 9.013
VAV0447 | VAV | Included | BMO EXEC. ASSIST. 9.014
VAV0448 | VAV | Included | BMO EXEC. ASSIST. 9.015
VAV0449 | VAV | Included | BMO EXEC. ASSIST. 9.016
VAV0450 | VAV | Included | BMO EXEC. ASSIST. 9.017
VAV0451 | VAV | Not Included | BMO EXEC. SEC. 9.018
VAV0452 | VAV | Not Included | BMO EXEC. SEC. 9.019
VAV0453 | VAV | Not Included | BMO EXEC. SEC. 9.020
VAV0454 | VAV | Not Included | BMO OPER. DIR. ENSUIT 9.021
VAV0455 | VAV | Included | BMO EXEC. ASSIST. 9.022
VAV0456 | VAV | Not Included | BMO EXEC. SEC. 9.023
VAV0457 | VAV | Not Included | BMO EXEC. SEC. 9.024
VAV0458 | VAV | Not Included | BMO EXEC. SEC. 9.025
VAV0459 | VAV | Not Included | BMO EXEC. SEC. 9.025
VAV0460 | VAV | Not Included | BMO SUPP. SEC. 9.026
VAV0461 | VAV | Not Included | BMO SUPP. SEC. 9.027
VAV0462 | VAV | Not Included | BMO SUPP. SEC. 9.028
VAV0463 | VAV | Not Included | BMO SUPP. SEC. 9.029
VAV0464 | VAV | Not Included | BMO SUPP. SEC. 9.030
VAV0465 | VAV | Included | BMO PRINT COPY 9.031
VAV0466 | VAV | Included | BMO STORAGE 9.032
VAV0467 | VAV | Included | HR EDU. ADV. ENSUIT 9.033
VAV0468 | VAV | Included | HR EDU. ADV. ENSUIT 9.034
VAV0469 | VAV | Included | HR EDU. ADV. ENSUIT 9.035
VAV0470 | VAV | Not Included | BOD EXECUTIVE 9.036
VAV0471 | VAV | Not Included | BOD SEC. 9.037
VAV0472 | VAV | Not Included | BOD EXECUTIVE 9.038
VAV0473 | VAV | Not Included | HH-WING CORRIDOR 9.601
VAV0474 | VAV | Not Included | HH-WING CORRIDOR 9.601
VAV0475 | VAV | Included | MEETING ROOM 9.039
VAV0476 | VAV | Included | BMO SAFE 9.040
VAV0477 | VAV | Included | BMO ARCHIVE ROOM 9.041
VAV0478 | VAV | Not Included | HH-WING CORRIDOR 9.601
VAV0479 | VAV | Included | LEGAL ARCHIVE 9.001
VAV0480 | VAV | Included | LEGAL CONSULE 9.002
VAV0481 | VAV | Included | LEGAL CONSULE 9.003
VAV0482 | VAV | Included | LEGAL CONSULE 9.004
VAV0483 | VAV | Included | LEGAL CONSULE 9.005
VAV0484 | VAV | Included | LEGAL CONSULE 9.006
VAV0485 | VAV | Included | LEGAL CONSULE 9.007
VAV0486 | VAV | Not Included | LEGAL SUP. SEC. 9.008
VAV0487 | VAV | Not Included | LEGAL SUP. SEC. 9.009
VAV0488 | VAV | Not Included | LEGAL ADV. ENSUIT 9.010
VAV0489 | VAV | Not Included | LOUNGE 9.105
VAV0490 | VAV | Not Included | BMO WAITING AREA 9.104
VAV0491 | VAV | Included | NORTH WEST TOILETS 9.403
VAV0492 | VAV | Not Included | HH-WING CORRIDOR 9.601
VAV0493 | VAV | Not Included | SHEIKA WING DINING AREA 9.110
VAV0494 | VAV | Not Included | SHEIKA WING DINING AREA 9.110
VAV0495 | VAV | Not Included | SOUTH EAST CORRIDOR 9.11
VAV0496 | VAV | Not Included | KITCHEN 9.108
VAV0497 | VAV | Not Included | SHEIKA WING DINING AREA 9.110
VAV0498 | VAV | Included | ARCHIVE 10.005
VAV0499 | VAV | Not Included | EXEC. DIR. ARCH. COORD 10.006
VAV0500 | VAV | Included | EXEC. DIR. PROT. ASSIS. 10.007
VAV0501 | VAV | Included | SCHED OFFICER 10.008
VAV0502 | VAV | Included | CEREM. OFFICER 10.009
VAV0503 | VAV | Included | CEREM. OFFICER 10.010
VAV0504 | VAV | Included | CEREM. OFFICER 10.011
VAV0505 | VAV | Included | TR. & VIS. OFFICER 10.012
VAV0506 | VAV | Included | TR. & VIS. OFFICER 10.013
VAV0507 | VAV | Included | SCHED OFFICER 10.015
VAV0508 | VAV | Included | PLANNING ANALYST 10.016
VAV0509 | VAV | Included | STRAT. PLANNER 10.017
VAV0510 | VAV | Not Included | PLANNING DIR. EXT. COORD 10.018
VAV0511 | VAV | Included | SEN. POLICY ANALYST 10.019
VAV0512 | VAV | Included | SEN. RESEARCH ANALYST 10.020
VAV0513 | VAV | Included | RESEARCH ANALYST 10.021
VAV0514 | VAV | Included | RESEARCH ANALYST 10.022
VAV0515 | VAV | Included | HR OFFICER 10.023
VAV0516 | VAV | Included | HR ASSISTANT 10.024
VAV0517 | VAV | Included | PROCUR. REPRESENT 10.025
VAV0518 | VAV | Included | SERVICE COORD 10.026
VAV0519 | VAV | Included | SERV. SUPERVISOR 10.027
VAV0520 | VAV | Not Included | FINANCE CONTROL 10.028
VAV0521 | VAV | Not Included | SERV. DIR. TR. & GU. SERV. 10.029
VAV0522 | VAV | Not Included | HH-WING CORRIDOR 10.601
VAV0523 | VAV | Not Included | COMM. DIR. DESIG. 10.031
VAV0524 | VAV | Not Included | COMM. DIR. EDITOR 10.032
VAV0525 | VAV | Not Included | COMM. DIR. TRANSLTOR 10.033
VAV0526 | VAV | Not Included | COMM. DIR. COORD 10.034
VAV0527 | VAV | Included | SUPP. OFFICER 10.035
VAV0528 | VAV | Not Included | SH. SERV. DIR. ACCOUNUT. 10.036
VAV0529 | VAV | Not Included | SH. SERV. DIR. SR. ACCOUNT. 10.037
VAV0530 | VAV | Not Included | SHEIKHA WING STORAGE 10.001
VAV0531 | VAV | Not Included | SHEIKHA WING STORAGE 10.001
VAV0532 | VAV | Not Included | SHEIKHA WING STORAGE 10.001
VAV0533 | VAV | Not Included | BOARD ROOM WAITING 10.003
VAV0534 | VAV | Not Included | BOARD ROOM WAITING 10.003
VAV0535 | VAV | Included | ARCHIVE COORD 10.004
VAV0536 | VAV | Not Included | LOUNGE 10.106
VAV0537 | VAV | Not Included | NW LOUNGE 10.106
VAV0538 | VAV | Not Included | BOARD PREP. ROOM 10.109
VAV0539 | VAV | Included | CONSULTANT SPACE 10.101
VAV0540 | VAV | Included | CONSULTANT SPACE 10.101
VAV0541 | VAV | Not Included | AV ROOM 10.112
VAV0542 | VAV | Not Included | HH-WING CORRIDOR 10.601
VAV0543 | VAV | Not Included | HH-WING CORRIDOR 10.601
VAV0544 | VAV | Not Included | HH-WING CORRIDOR 10.601
VAV0545 | VAV | Not Included | HH-WING CORRIDOR 10.601
VAV0546 | VAV | Not Included | HH-WING CORRIDOR 10.601
VAV0547 | VAV | Not Included | SHEIKHA WING MULTIPURPOSE ROOM 10.102
VAV0548 | VAV | Included | OFFICE SPACE 10.002E
VAV0549 | VAV | Included | OFFICE SPACE 10.002D
VAV0550 | VAV | Included | OFFICE SPACE 10.002C
VAV0551 | VAV | Included | OFFICE SPACE 10.002A
VAV0552 | VAV | Not Included | PLANNING DIR. 11.012
VAV0553 | VAV | Not Included | EXEC. DIR. CORR. 11.013
VAV0554 | VAV | Not Included | EXEC. DIR. CORR. MANAGER 11.014
VAV0555 | VAV | Not Included | EXEC. DIR. CORR. 11.015
VAV0556 | VAV | Included | LEGAL ASSIST. 11.016
VAV0557 | VAV | Included | LEGAL ADVISOR 11.017
VAV0558 | VAV
VAV0559 | VAV | Included | LEGAL ADVISOR 11.018
VAV0560 | VAV | Not Included | DEP. EXEC. DIRECTOR 11.019
VAV0561 | VAV | Not Included | EXEC. ASSI. 11.020
VAV0562 | VAV | Not Included | EXEC. DIRECTOR 11.021
VAV0564 | VAV | Not Included | SHEIKHA WING WAITING ROOM 11.022
VAV0565 | VAV | Not Included | SHEIKHA WING WAITING ROOM 11.022
VAV0567 | VAV | Not Included | SECURITY ROOM 11.023
VAV0568 | VAV | Not Included | COMMUNICATION DIR. 11.001
VAV0570 | VAV | Included | MED. REL. OFFICER 11.002
VAV0571 | VAV | Not Included | DIR. SHARED SERVICES 11.003
VAV0573 | VAV | Included | ADM. ASSI. 11.004
VAV0574 | VAV | Not Included | PROTOCOL DIR. 11.005
VAV0575 | VAV | Not Included | GIFT DIR. 11.006
VAV0576 | VAV | Not Included | EXEC. DIR. CONSULTANT 11.008
VAV0577 | VAV | Not Included | SEC. 11.009
VAV0578 | VAV | Not Included | DIR. OF POL. & RES. 11.010
VAV0579 | VAV | Not Included | SECRETARY 11.011
VAV0580 | VAV | Not Included | SHEIKHA WING BUSINESS LOUNGE 11.103
VAV0581 | VAV | Not Included | SHEIKHA WING BUSINESS LOUNGE 11.103
VAV0582 | VAV | Not Included | SHEIKHA WING LOBBY 11.201
VAV0583 | VAV | Not Included | SHEIKHA WING LOBBY 11.201
VAV0584 | VAV | Not Included | SHEIKHA WING SHEIKHA ENSUIT 11.202
VAV0585 | VAV | Not Included | SHEIKHA WING SHEIKHA ENSUIT 11.202
VAV0586 | VAV | Not Included | SHEIKHA WING SHEIKHA ENSUIT 11.202
VAV0587 | VAV | Not Included | SHEIKHA WING SHEIKHA ENSUIT 11.202
VAV0588 | VAV | Not Included | SHEIKHA WING RELAX AREA 11.203
VAV0589 | VAV | Not Included | SHEIKHA WING RELAX AREA 11.203
VAV0590 | VAV | Not Included | SHEIKHA WING MEETING ROOM 11.204
VAV0591 | VAV | Not Included | SHEIKHA WING MEETING ROOM 11.204
VAV0592 | VAV | Not Included | VISITORS CENTER 08
VAV0593 | VAV | Not Included | VISITORS CENTER 08
VAV0594 | VAV | Not Included | VISITORS CENTER 08
VAV0595 | VAV | Included | ROOM B.109
VAV0596 | VAV | Included | OFFICE SPACE 04.015B
VAV0597 | VAV | Included | OFFICE SPACE 04.001A
VAV0598 | VAV | Included | OFFICE SPACE 04.001E
VAV0599 | VAV | Included | OFFICE SPACE 04.001C
VAV0600 | VAV | Included | OFFICE SPACE 04.001H
VAV0601 | VAV | Included | OFFICE SPACE 10.002B
VAV0602 | VAV | Included | EXEC. DIR. CONSULTANT 11.007
VAV0603 | VAV | Not Included | SHEIKHA WING CORRIDOR 11.601
VAV0604 | VAV | Not Included | SHEIKHA WING CORRIDOR 11.601
VAV0605 | VAV | Not Included | HH WING BUSINESS LOUNGE 11.102
VAV0606 | VAV | Not Included | HH WING BUSINESS LOUNGE 11.102
VAV0607 | VAV | Included | PR & MARKET STAFF G.013
VAV0608 | VAV | Not Included | TOILET G.405

## SSC Asset Registry
Controllable Asset Registry
Tag No. | Equipment Type | Inluded/ Not Inlcuded | ROOM NAME AS PER DRAWINGS | ZONES SERVED | Supply Air Temp (°C) | Return Air Temp (°C) | Supply Air Temp SP (°C) | Return Air Temp SP (°C) | Room Temp (°C) | Room Unit SP (°C) | Occ. SP Cooling (°C) | Occ. SP Heating (°C) | Unocc. SP Cooling (°C) | Unocc. SP Heating (°C) | Occupancy Status | Source / Notes | Occupied SP (°C) | Unoccupied SP (°C)
AHUB_0001 | AHU | Not Included | CHILLED WATER B.013 | VAV/B/01 ENTRANCE B1.015 / VAV/1/1->3 SHELL SPACE 1.014/ VAV/2/12 EXECUTIVE CONFERENCE ROOM 2.005…
AHUB_0002 | AHU | Not Included | VENT PLANT B.014 | VAV/1/22 CORRIDOR 1.013 / VAV/1/4->6 SHELL SPACE 1.015/ VAV/1/08->13 PRAYER ROOM 1.019….
AHUB_0003 | AHU | Not Included | VENT PLANT B.014 | VENT PLANT B1.008 / GENERATOR B1.012/ CORRIDOR B1.029..
AHUB_0004 | AHU | Not Included | VENT PLANT B.008 | VAV/2/07 & 8 LOBBY 2.002 / VESTIBUTE 2.010…
AHUB_0005 | AHU |  | CHILLED WATER B.013
FCU0001 | FCU | Not Included | SPRINKLER AND WATER B.016
FCU0002 | FCU | Not Included | MAIN SEC. CONTROL ROOM B.025
FCU0003 | FCU | Not Included | B.M.S B.039
FCU0004 | FCU | Not Included | AV ROOM 1.008
FCU0005 | FCU | Not Included | IDF-1 1.027
FCU0006 | FCU | Not Included | IDF-1 1.027
FCU0007 | FCU | Not Included | IDF-2 1.039
FCU0008 | FCU | Not Included | IDF-2 1.039
FCU0009 | FCU | Included | CORRIDOR 1.028
FCU0010 | FCU | Included | CORRIDOR 1.010
FCU0011 | FCU | Included | PRINTING 03.033
VAV0001 | VAV | Included | ENTRANCE B.015
VAV0002 | VAV | Included | SHARED OFFICE 01.014
VAV0003 | VAV | Included | SHARED OFFICE 01.014
VAV0004 | VAV | Included | SHARED OFFICE 01.014
VAV0005 | VAV | Included | SHARED OFFICE 01.015
VAV0006 | VAV | Included | SHARED OFFICE 01.015
VAV0007 | VAV | Included | SHARED OFFICE 01.015
VAV0008 | VAV | Included | CORRIDOR 01.024
VAV0009 | VAV | Included | PRAYER ROOM 01.019
VAV0010 | VAV | Included | PRAYER ROOM 01.019
VAV0011 | VAV | Included | PRAYER ROOM 01.019
VAV0012 | VAV | Included | PRAYER ROOM 01.019
VAV0013 | VAV | Included | PRAYER ROOM 01.019
VAV0014 | VAV | Included | PRAYER ROOM 01.019
VAV0015 | VAV | Included | ROOM NO 42
VAV0016 | VAV | Included | ROOM NO 43
VAV0017 | VAV | Included | ROOM NO 44
VAV0018 | VAV | Included | SHARED OFFICE 01.029
VAV0019 | VAV | Included | SHARED OFFICE 01.029
VAV0020 | VAV | Included | SHARED OFFICE 01.029
VAV0021 | VAV | Included | CORRIDOR 01.013
VAV0022 | VAV | Included | OPEN SPACE 01.003
VAV0023 | VAV | Included | OPEN SPACE 01.003
VAV0024 | VAV | Included | CORRIDOR 01.001
VAV0025 | VAV | Included | TEAM SPACE 01.002
VAV0026 | VAV | Included | TEAM SPACE 01.002
VAV0027 | VAV | Included | TEAM SPACE 01.002
VAV0028 | VAV | Included | TEAM SPACE 01.002
VAV0029 | VAV | Included | CORRIDOR 01.001
VAV0030 | VAV | Included | PRINT COPY 01.016
VAV0031 | VAV | Included | CORRIDOR 01.001
VAV0032 | VAV | Included | CORRIDOR 01.018
VAV0033 | VAV | Included | CORRIDOR 01.028
VAV0034 | VAV | Included | OPEN SPACE 01.003
VAV0035 | VAV | Included | CORRIDOR 01.010
VAV0036 | VAV | Included | ABLUTION ROOM 01.022
VAV0037 | VAV | Not Included | AV ROOM 1.008
VAV0038 | VAV | Included | ST-4 STAIR 4
VAV0039 | VAV | Included | OPEN SPACE 01.003
VAV0040 | VAV | Included | CONFERENCE ROOM 02.006
VAV0041 | VAV | Not Included | EXECUTIVE CONFERENCE ROOM 02.005
VAV0042 | VAV | Not Included | EXECUTIVE CONFERENCE ROOM 02.005
VAV0043 | VAV | Included | CORRIDOR 02.004
VAV0044 | VAV | Included | FOYER 02.001
VAV0045 | VAV | Included | FOYER 02.001
VAV0046 | VAV | Included | LOBBY 02.002
VAV0047 | VAV | Included | LOBBY 02.002
VAV0048 | VAV | Included | LOBBY 02.002
VAV0049 | VAV | Included | LOBBY 02.002
VAV0050 | VAV | Included | CORRIDOR 02.003
VAV0051 | VAV | Not Included | EXECUTIVE CONFERENCE ROOM 02.005
VAV0052 | VAV | Included | CONFERENCE ROOM 02.006
VAV0053 | VAV | Included | RESEARCHER OFFICE 03.015
VAV0054 | VAV | Included | VISITOR'S CUBICLE 03.014
VAV0055 | VAV | Included | RESEARCHER OFFICE 03.013
VAV0056 | VAV | Included | RESEARCHER OFFICE 03.012
VAV0057 | VAV | Included | VISITOR'S CUBICLE 03.011
VAV0058 | VAV | Included | RESEARCHER OFFICE 03.010
VAV0059 | VAV | Included | RESEARCHER OFFICE 03.009
VAV0060 | VAV | Included | VISITOR'S CUBICLE 03.008
VAV0061 | VAV | Included | OPERATION MANAGERS 03.007
VAV0062 | VAV | Included | ROOM 03.006B
VAV0063 | VAV |  | (NOT FOUND ON DRAWING LEVEL 3)
VAV0064 | VAV | Included | ROOM 03.006A
VAV0065 | VAV | Included | RESEARCHER OFFICE 03.005
VAV0066 | VAV | Included | VISITOR'S CUBICLE 03.004
VAV0067 | VAV | Included | RESEARCHER OFFICE 03.003
VAV0068 | VAV | Not Included | DIRECTOR MEETING ROOM 03.002
VAV0069 | VAV | Not Included | DIRECTOR MEETING ROOM 03.002
VAV0070 | VAV | Not Included | DIRECTOR'S OFFICE 03.001
VAV0071 | VAV | Included | GENERAL OFFICE AREA 03.002
VAV0072 | VAV | Included | GENERAL OFFICE AREA 03.002
VAV0073 | VAV | Included | GENERAL OFFICE AREA 03.002
VAV0074 | VAV | Included | GENERAL OFFICE AREA 03.002
VAV0075 | VAV | Included | GENERAL OFFICE AREA 03.002
VAV0076 | VAV | Included | GENERAL OFFICE AREA 03.002
VAV0077 | VAV | Included | GENERAL OFFICE AREA 03.002
VAV0078 | VAV | Included | ASSOC. DOR. OFFICE 03.031
VAV0079 | VAV | Not Included | ASSOC. DIR. MEETING ROOM 03.030
VAV0080 | VAV | Not Included | ASSOC. DIR. MEETING ROOM 03.030
VAV0081 | VAV | Included | RESEARCHER OFFICE 03.029
VAV0082 | VAV | Included | VISITOR'S CUBICLE 03.028
VAV0083 | VAV | Included | RESEARCHER OFFICE 03.027
VAV0084 | VAV | Included | MEETING ROOM 03.026
VAV0085 | VAV | Included | MEETING ROOM 03.026
VAV0086 | VAV | Included | MEETING ROOM 03.026
VAV0087 | VAV | Included | SECRETARIAL AREA 03.025
VAV0088 | VAV | Included | VISITOR'S CUBICLE 03.024
VAV0089 | VAV | Included | RESEARCHER OFFICE 03.023
VAV0090 | VAV | Included | RESEARCHER OFFICE 03.022
VAV0091 | VAV | Included | VISITOR'S CUBICLE 03.021
VAV0092 | VAV | Included | RESEARCHER OFFICE 03.020
VAV0093 | VAV | Included | IT MANAGERS'S OFFICE 03.019
VAV0094 | VAV | Included | VISITOR'S CUBICLE 03.018
VAV0095 | VAV | Included | RESEARCHER OFFICE 03.017
VAV0096 | VAV | Included | LOUNGE 03.016
VAV0097 | VAV | Included | LOUNGE 03.016
VAV0098 | VAV | Included | IT OFFICE 03.049
VAV0099 | VAV | Included | CORRIDOR 03.042
VAV0100 | VAV | Included | CORRIDOR 03.041
VAV0101 | VAV | Included | CORRIDOR 03.044
VAV0102 | VAV | Included | CORRIDOR 03.034
VAV0103 | VAV | Included | CORRIDOR 03.034
VAV0104 | VAV | Included | CORRIDOR 03.034
VAV0105 | VAV | Included | CORRIDOR 03.034
VAV0106 | VAV | Included | CORRIDOR 03.042
VAV0107 | VAV | Included | GENERAL OFFICE AREA 03.002
VAV0108 | VAV | Included | GENERAL OFFICE AREA 03.002

## QNL Asset Registry
Controllable Asset Registry
Tag No. | Equipment Type | Inluded/ Not Inlcuded | ROOM NAME AS PER DRAWINGS | ZONES SERVED | Supply Air Temp (°C) | Return Air Temp (°C) | Supply Air Temp SP (°C) | Return Air Temp SP (°C) | Eff. Temp SP (°C) | Cooling SP (°C) | Heating SP (°C)
AHUB001 | AHU | Not Included | Basement Level Zone 4 Plant Room 4 B.220 | COMPACT SHELVING B.120 / CORRIDOR 6 B.214 / FM STORAGE B.210…
AHUB002 | AHU | Included | Basement Level Zone 1 Plant Room 1 B.063 | HERITAGE ZONE B.143
AHUB003 | AHU | Included | Basement Level Zone 1 Plant Room 2 B.070 | HERITAGE ZONE B.143
AHUB004 | AHU | Included | Basement Level Zone 2 Plant Room 3 B.110 | HERITAGE ZONE B.143
AHUB005 | AHU | Included | Basement Level Zone 4 Plant Room 4 B.220 | HERITAGE ZONE B.143
AHUB006 | AHU | Included | Basement Level Zone 4 Plant Room 4 B.220 | HERITAGE ZONE B.143
AHUB007 | AHU | Included | Basement Level Zone 4 Plant Room 4 B.220 | HERITAGE ZONE B.143
AHUB008 | AHU | Not Included | Basement Level Zone 4 Plant Room 4 B.220 | HERITAGE ZONE B.143 / PLANTROOM B.140 / VAULT B.141 / HL PLANT B.140…
AHUB009 | AHU | Included | Basement Level Zone 2 Plant Room 3 B.110 | LEVEL 2 BRIDGE RAISED FLOOR
AHUB010 | AHU | Not Included | Basement Level Zone 1 Plant Room 2 B.070 | VAV_2F_S10_001 - GULF MATERIAL L2 / VAV_2F_S10_002 - GULF MATERIAL L2 / VAV_2F_S10_003 - GULF MATERIAL L2 / VAV_2F_S10_004 - GULF MATERIAL L2
AHUB011 | AHU | Not Included | Basement Level Zone 1 Plant Room 1 B.063 | VAV_1F_S11_001 - Group Study Room1 L1.026 / VAV_1F_S11_002 - Group Study Room2 L1.027 / VAV_1F_S11_003 - Group Study Room3 L1.028 / VAV_1F_S11_004 - Information Literacy Instr 1 L1.020
AHUB012 | AHU | Not Included | Basement Level Zone 1 Plant Room 1 B.063 | VAV_2F_S12_001 - OPEN READING AREA L1.001 / VAV_2F_S12_002 - OPEN READING AREA L1.001 / VAV_2F_S12_003 - OPEN READING AREA L1.001 / VAV_2F_S12_004 - OPEN READING AREA L1.001
AHUB013 | AHU | Not Included | Basement Level Zone 1 Plant Room 2 B.070 | VAV_2F_S13_001 - Lib. Director's Room L2.044 / VAV_2F_S13_002 - Lib. Director's Room L2.044 / VAV_2F_S13_003 - Service & Lounge L2.043 / VAV_2F_S13_004 - OPEN OFFICE L2.025
AHUB014 | AHU | Not Included | Basement Level Zone 2 Plant Room 3 B.110 | VAV_2F_S14_001 - PUBLIC SERVICES L1.080 / VAV_2F_S14_002 - PUBLIC SERVICES L1.080 / VAV_2F_S14_003 - PUBLIC SERVICES L1.080 / VAV_2F_S14_004 - PUBLIC SERVICES L1.080
AHUB015 | AHU | Not Included | Basement Level Zone 2 Plant Room 3 B.110 | VAV_1F_S15_001 - Media Studio1 L1.063 / VAV_1F_S15_002 - Media Studio1 L1.063 / VAV_1F_S15_003 - Media Studio2 L1.065 / VAV_1F_S15_004 - Media Studio2 L1.065
FCU_1F_001 | FCU | Not Included | IDF ROOM T1.323 |  | 15.8 |  | 21 |  | 21.32
FCU_1F_002 | FCU | Not Included | ICT Room 02 L1.030 |  | 20 |  | 18 |  | 20.79
FCU_1F_003 | FCU | Not Included | IDF Room 02 L1.099 |  | 17.78 |  | 21 |  | 20.75
FCU_1F_004 | FCU | Included | BRIDGE CEILING VOID L1.BR6 |  | 22.23 | 20.55 | 21 | 19 | 19
FCU_1F_005 | FCU | Included | BRIDGE CEILING VOID L1.BR6 |  | 15.75 | 20.22 | 21 | 20 | 20
FCU_1F_006 | FCU | Included | BRIDGE CEILING VOID L1.BR6 |  | 14.74 | 19.89 | 21 | 19.5 | 19.5
FCU_1F_007 | FCU | Included | BRIDGE CEILING VOID L1.BR6 |  | 23.95 | 20.85 | 21 | 20 | 20
FCU_1F_008 | FCU | Included | BRIDGE CEILING VOID L1.BR6 |  | 21.03 | 19.31 | 21 | 19 | 19
FCU_1F_009 | FCU | Included | BRIDGE CEILING VOID L1.BR5 |  | 16.3 | 20.75 | 21 | 20 | 20
FCU_1F_010 | FCU | Included | BRIDGE CEILING VOID L1.BR5 |  | 16.84 | 20.75 | 23 | 20 | 20
FCU_1F_011 | FCU | Included | BRIDGE CEILING VOID L1.BR5 |  | 15.82 | 20.39 | 21 | 19 | 19
FCU_1F_012 | FCU | Included | BRIDGE CEILING VOID L1.BR5 |  | 16.2 | 19.94 | 21 | 19 | 19
FCU_1F_013 | FCU | Included | BRIDGE CEILING VOID L1.BR6 |  | 20.37 | 20.01 | 18 | 20 | 20
FCU_1F_014 | FCU | Included | BRIDGE CEILING VOID L1.BR4 |  | 19.19 | 18.93 | 18 | ?????? | 20
FCU_1F_015 | FCU | Included | BRIDGE CEILING VOID L1.BR6 |  | 20.19 | 20.36 | 19 | 20 | 20
FCU_1F_016 | FCU | Included | BRIDGE CEILING |  | 20.73 | 20.67 | 21 | 21 | 21
FCU_1F_017 | FCU | Included | VOID L1.BR4 |  | 18.83 | 19.22 | 18 | 21 | 21
FCU_1F_018 | FCU | Included | VOID L1.BR4 |  | 12.81 | 41.47 | 25 | 21 | 21
FCU_1F_019 | FCU | Included | BRIDGE CEILING VOID L1.BR5 |  | 15.76 | 20.62 | 19 | 18 | 18
FCU_1F_020 | FCU | Included | BRIDGE CEILING VOID L1.BR3 |  | 14.06 | 20.68 | 24 | 18 | 18
FCU_1F_021 | FCU | Included | BRIDGE CEILING VOID L1.BR5 |  | 12.7 | 20.55 | 15 | 20 | 20
FCU_1F_022 | FCU | Included | BRIDGE CEILING VOID L1.BR3 |  | 20.13 | 19.98 | 19 | 20 | 20
FCU_1F_023 | FCU | Included | BRIDGE CEILING VOID L1.BR3 |  | 21.19 | 20.72 | 18 | 21 | 21
FCU_1F_024 | FCU | Included | BRIDGE CEILING VOID L1.BR3 |  | 19.91 | 19.61 | 18 | 21 | 21
FCU_1F_025 | FCU | Included | BRIDGE CEILING VOID L1.BR2 |  | 20.99 | 21.15 | 21 | 22 | 22
FCU_1F_026 | FCU | Included | BRIDGE CEILING VOID L1.BR4 |  | 19.61 | 18.78 | 20 | 21 | 21
FCU_1F_027 | FCU | Included | BRIDGE CEILING VOID L1.BR2 |  | 17.86 | 17.75 | 21 | 24 | 24
FCU_1F_028 | FCU | Included | BRIDGE CEILING VOID L1.BR4 |  | 17.98 | 17.7 | 20 | 21 | 21
FCU_1F_029 | FCU | Included | BRIDGE CEILING VOID L1.BR2 |  | 18.11 | 18.71 | 21.5 | 24 | 24
FCU_1F_030 | FCU | Included | BRIDGE CEILING VOID L1.BR2 |  | 19.37 | 19.37 | 20 | 24 | 24
FCU_1F_031 | FCU | Included | BRIDGE CEILING VOID L1.BR1 |  | 18.12 | 18.47 | 30 | 24 | 24
FCU_1F_032 | FCU | Included | BRIDGE CEILING VOID L1.BR1 |  | 19.48 | 18.92 | 18 | 22 | 22
FCU_1F_033 | FCU | Included | BRIDGE CEILING VOID L1.BR1 |  | 16.16 | 17.69 | 25 | 24 | 24
FCU_1F_034 | FCU | Included | BRIDGE CEILING VOID L1.BR1 |  | 19.27 | 18.58 | 21 | 24 | 24
FCU_1F_035 | FCU | Included | BRIDGE CEILING VOID L1.BR2 |  | 18.58 | 18.68 | 21 | 26 | 26
FCU_1F_036 | FCU | Included | BRIDGE CEILING VOID L1.BR2 |  | 21.03 | 20.75 | 18 | 22 | 22
FCU_1F_037 | FCU | Included | BRIDGE CEILING VOID L1.BR3 |  | 20.84 | 20.35 | 23 | 21 | 21
FCU_1F_038 | FCU | Included | BRIDGE CEILING VOID L1.BR3 |  | 15.68 | 20.15 | 24 | 20 | 20
FCU_1F_039 | FCU | Included | BRIDGE CEILING VOID L1.BR4 |  | 14.77 | 19.7 | 21 | 21 | 21
FCU_1F_040 | FCU | Included | BRIDGE CEILING VOID L1.BR4 |  | 20.49 | ?????? | 0 | 24 | 24
FCU_1F_041 | FCU | Included | BRIDGE CEILING |  | 19.36 | 20.25 | 21 | 20 | 20
FCU_1F_042 | FCU | Included | VOID L1.BR5 |  | 20.99 | 20.46 | 21 | 21 | 21
FCU_1F_043 | FCU | Included | BRIDGE CEILING VOID L1.BR6 |  | 20.74 | 20.21 | 21 | 19 | 19
FCU_1F_044 | FCU | Included | BRIDGE CEILING VOID L1.BR6 |  | 18.68 | 20.46 | 21 | 21 | 21
FCU_1F_045 | FCU | Included | BRIDGE CEILING VOID L1.BR6 |  | 18.42 | 18.25 | 20 | 18 | 18
FCU_1F_046 | FCU | Included | BRIDGE CEILING VOID L1.BR6 |  | 14.88 | 18.43 | 19 | 18 | 18
FCU_1F_047 | FCU | Included | BRIDGE CEILING VOID L1.BR1 |  | 17.26 | 17.55 | 20 | 19 | 19
FCU_1F_048 | FCU | Included | BRIDGE CEILING VOID L1.BR1 |  | 16.54 | 16.38 | 14 | 23 | 23
FCU_1F_049 | FCU | Included | BRIDGE CEILING VOID L1.BR2 |  | 16.86 | 16.49 | 25 | 24 | 24
FCU_1F_050 | FCU | Included | BRIDGE CEILING VOID L1.BR2 |  | 41.61 | 17.09 | 21 | 24 | 24
FCU_1F_051 | FCU | Included | BRIDGE CEILING VOID L1.BR4 |  | 19.76 | 19.86 | 21 | 21 | 21
FCU_1F_052 | FCU | Included | BRIDGE CEILING VOID L1.BR4 |  | 19.64 | 19.72 | 22 | 21 | 20
FCU_1F_053 | FCU | Included | BRIDGE CEILING VOID L1.BR5 |  | 15.38 | 20.88 | 21 | 18 | 18
FCU_1F_054 | FCU | Included | BRIDGE CEILING VOID L1.BR5 |  | 21.09 | 20.55 | 21 | 20 | 20
FCU_1F_055 | FCU | Included | VESTIBULE L1 |  | 22.09 | 23.23 | 21 | 23 | 23
FCU_1F_056 | FCU | Included | External Book Drop L1 |  | 13.43 |  | 21 |  | 19.86
FCU_1F_057 | FCU | Not Included | ILL DIRECTOR L1.144 |  | 56.36 |  | 21 |  | 29.97
FCU_1F_058 | FCU | Not Included | ILL DIRECTOR L1.145 |  | 19.6 |  | 21 |  | 24.02
FCU_1F_059 | FCU | Included | Restaurant L1.150 |  | 25.03 | 25.07 | 21 | 21.5 | 21.5
FCU_1F_060 | FCU | Included | Restaurant L1.150 |  | 17.06 | 24.19 | 21 | 23 | 23
FCU_1F_061 | FCU | Included | Restaurant L1.150 |  | 21.23 | 25.23 | 21 | 23 | 23
FCU_1F_062 | FCU | Included | Restaurant L1.150 |  | 23.68 | 23.31 | 21 | 22 | 22
FCU_1F_063 | FCU | Included | Restaurant L1.150 |  | 22.25 | 22.9 | 22 | 21.5 | 21.5
FCU_1F_064 | FCU | Included | Restaurant L1.150 |  | 23.55 | 23.77 | 21 | 21 | 21
FCU_1F_065 | FCU | Not Included | BRIDGE IDF L1.BI |  | 17.67 |  | 21 |  | 18
FCU_2F_001 | FCU | Not Included | IDF ROOM T1.275 |  | 39.9 |  | 21 |  | 20.81
FCU_2F_002 | FCU | Not Included | IDF ROOM T1.276 |  | 38 |  | 21 |  | 20.83
FCU_2F_003 | FCU | Not Included | IDF ROOM T1.171 |  | 15.63 |  | 21 |  | 20.52
FCU_2F_004 | FCU | Not Included | IDF ROOM T1.1714 |  | 23.84 |  | 21 |  | 21.46
FCU_2F_005 | FCU | Not Included | MDF Room L2.009 |  | 67.02 |  | 21 |  | 21.41
FCU_2F_034 | FCU | Included | Auditorium High Levlel in Ceiling Void L2.087 |  | 19.63 | 19.61 | 23 | 22.2 | 22.2
FCU_2F_035 | FCU | Included | Auditorium High Levlel in Ceiling Void L2.087 |  | 19.14 | 16.22 | 22 | 19 | 19
FCU_2F_036 | FCU | Included | Auditorium High Levlel in Ceiling Void L2.087 |  | 24.93 | 19.47 | 23 | 22 | 22
FCU_2F_037 | FCU | Included | Auditorium High Levlel in Ceiling Void L2.087 |  | 19.47 | 19.45 | 23 | 21 | 21
FCU_2F_038 | FCU | Included | Auditorium Booths L2.087 |  | 19.95 | 19.29 | 21 | 22 | 19.9
FCU_2F_039 | FCU | Included | Auditorium Booths L2.087 |  | 19.76 | 17.04 | 21 | 16 | 19.99
FCU_2F_040 | FCU | Included | Auditorium Booths L2.087 |  | 17.08 | 16.7 | 22 | 20 | 18.83
FCU_2F_041 | FCU | Included | Bridge Raised Floor L2.088 |  | 19.66 | 18.97 | 16 | 19 | 19
FCU_2F_042 | FCU | Included | STUDY AREA L2.088 |  | 14.19 | 19.39 | 16 | 19 | 19
FCU_2F_043 | FCU | Included | Bridge L2.088 |  | 12.99 | 19.31 | 16 | 19 | 19
FCU_2F_044 | FCU | Included | Bridge L2.088 |  | 19.58 | 18.96 | 16 | 21 | 21
FCU_2F_045 | FCU | Included | Group Study Room L2.081 |  | 15.16 |  | 20 |  | 18.5
FCU_2F_046 | FCU | Included | Group Study Room L2.076 |  | 14.31 |  | 12 |  | 21
FCU_2F_047 | FCU | Included | Group Study Room L2.076 |  | 15.7 |  | 20 |  | 23
FCU_2F_048 | FCU | Included | INDIVIDUAL STUDY ROOM L2.070 |  | 14.64 |  | 20 |  | 16
FCU_2F_049 | FCU | Included | INDIVIDUAL STUDY ROOM L2.070 |  | 12.73 |  | 18 |  | 21
FCU_2F_050 | FCU | Included | INDIVIDUAL STUDY ROOM L2.070 |  | 11.76 |  | 20 |  | 21
FCU_2F_051 | FCU | Included | INDIVIDUAL STUDY ROOM L2.073 |  | 11.82 |  | 21 |  | 23
FCU_2F_052 | FCU | Included | INDIVIDUAL STUDY ROOM L2.073 |  | 12.83 |  | 18 |  | 21
FCU_2F_053 | FCU | Included | INDIVIDUAL STUDY ROOM L2.073 |  | 16.05 |  | 18 |  | 23
FCU_2F_054 | FCU | Included | Bridge Raised Floor L2.088 |  | 21.74 | 22.29 | 14 | 20 | 20
FCU_2F_055 | FCU | Included | Bridge Raised Floor L2.088 |  | 17.19 | 22.09 | 16 | 16 | 16
FCU_2F_056 | FCU | Included | North East Core T1.021 |  | 25.07 | 26.22 | 18 | 21 | 21
FCU_2F_057 | FCU | Included | North East Core T1.021 |  | 23.78 | 26.22 | 21 | 22 | 22
FCU_2F_058 | FCU | Included | North East Core T1.021 |  | 23.71 | 26.22 | 20 | 20 | 20
FCU_2F_059 | FCU | Included | North East Core T1.021 |  | 24.24 | 26.22 | 18 | 20 | 20
FCU_2F_060 | FCU | Included | North West Core T1.020 |  | 26.25 | 26.64 | 18 | 20 | 20
FCU_2F_061 | FCU | Included | North West Core T1.020 |  | 25.81 | 26.57 | 15 | 15 | 15
FCU_2F_062 | FCU | Included | North West Core T1.020 |  | 22.53 | 26.57 | 16 | 20 | 20
FCU_B_001 | FCU | Not Included | IDF ROOM B.155 |  | 14.75 |  | 21 |  | 22.42
FCU_B_002 | FCU | Not Included | FUMIGATION B.085 |  | 16.15 |  | 21 |  | 20.76
FCU_B_003 | FCU | Not Included | IDF (Corridor) B.062 |  | 15.8 |  | 22 |  | 20.89
FCU_B_004 | FCU | Not Included | IDF FM Storage B.215 |  | 18.97 |  | 21 |  | 20.92
FCU_B_005 | FCU | Not Included | HL Plant Room B.140 |  | 20.27 |  | 21 |  | 17.8
FCU_B_006 | FCU | Not Included | Fire Command ROOM B.071 |  | 26.33 |  | 18 |  | 22.38
FCU_B_007 | FCU | Not Included | Sprinklers Pumps ROOM B.072 |  | 22.23 |  | 26 |  | 21.88
FCU_B_008 | FCU | Not Included | GAS SUPPRESSION ROOM B.087 |  | 19.52 |  | 21 |  | 23.97
FCU_B_009 | FCU | Not Included | PEOPLE MOVER ROOM B.088 |  | 17.51 |  | 21 |  | 22.77
FCU_B_010 | FCU | Not Included | Security Contol Room B.105 |  | 18.49 |  | 28 |  | 23
FCU_B_011 | FCU | Not Included | Plant Room 1 B.063 |  | 21.33 |  | 21 |  | 23.89
FCU_B_012 | FCU | Not Included | Plant Room 1 B.063 |  | 21.73 |  | 21 |  | 22.34
FCU_B_013 | FCU | Not Included | Plant Room 2 B.070 |  | 22.71 |  | 21 |  | 21.74
FCU_B_014 | FCU | Not Included | Plant Room 2 B.070 |  | 23.27 |  | 22 |  | 21.73
FCU_B_015 | FCU | Not Included | Plant Room 3 B.110 |  | 21.78 |  | 21 |  | 23.92
FCU_B_016 | FCU | Not Included | Plant Room 3 B.110 |  | 21.34 |  | 21 |  | 17.67
FCU_B_017 | FCU | Not Included | Plant Room 3 B.110 |  | 19.56 |  | 21 |  | 17.74
FCU_B_018 | FCU | Not Included | Plant Room 4 B.220 |  | 23.91 |  | 25 |  | 19.96
FCU_B_019 | FCU | Not Included | Plant Room 4 B.220 |  | 23.12 |  | 21 |  | 21.83
FCU_B_020 | FCU | Not Included | Plant Room 4 B.220 |  | 21 |  | 21 |  | 21.08
FCU_B_021 | FCU | Not Included | Plant Room 4 B.220 |  | 21.81 |  | 21 |  | 23.92
FCU_B_022 | FCU | Included | FM Storage B.210 |  | 24.93 |  | 20 |  | 22.92
FCU_B_023 | FCU | Included | FM Storage B.210 |  | 23.69 |  | 21 |  | 22.88
FCU_B_024 | FCU | Not Included | PH Plant ROOM B.211 |  | 13.7 |  | 21 |  | 18.94
FCU_B_025 | FCU | Not Included | MISTING PUMP ROOM B.212 |  | 21.08 |  | 21 |  | 22.34
FCU_B_026 | FCU | Not Included | MISTING PUMP ROOM B.212 |  | 21.41 |  | 21 |  | 22.37
FCU_B_027 | FCU | Included | Sorting Shelving Room B.121 |  | 18.5 | 19.24 | 13 | 17 | 17
FCU_B_028 | FCU | Included | Sorting Shelving Room B.121 |  | 20.67 | 19.19 | 23 | 17 | 17
FCU_B_029 | FCU | Included | B.145.05 |  | 21.43 | 20.87 | 21 | 22 | 22
FCU_B_030 | FCU | Not Included | WATER FEATURE ROOM B.226 |  | 21.32 |  | 21 |  | 22.3
FCU_B_031 | FCU | Not Included | IDF ROOM B.215A |  | 20.2 |  | 21 |  | 20.8
FCU_B_032 | FCU | Included | Shell Space-Special Collection B.132 |  | 21.88 |  | 24 |  | 24
FCU_B_033 | FCU | Included | Shell Space-Special Collection B.132 |  | 22.45 |  | 21 |  | 23.4
FCU_B_034 | FCU | Included | Shell Space-Special Collection B.132 |  | 21.52 |  | 25 |  | 24
FCU_B_035 | FCU | Included | Shell Space-Special Collection B.132 |  | 18.31 |  | 21 |  | 23.44
FCU_B_036 | FCU | Included | IT Office B.122 |  | 23.09 |  | 24 |  | 24
FCU_B_037 | FCU | Not Included | DIGITALIZATION SERVER SPACE B.215A |  | 14.25 |  | 21 |  | 18.93
FCU_B_038 | FCU | Not Included | ELEC. B.145 |  | NA |  | 20 |  | ??????
VAV0001 | VAV
VAV_1F_S11_001 | VAV | Included | Group Study Room1 L1.026 |  | 17.31 | 20.1 |  |  | 20 | 20 | 14
VAV_1F_S11_002 | VAV | Included | Group Study Room2 L1.027 |  | 17.4 | 20.03 |  |  | 20 | 20 | 15
VAV_1F_S11_003 | VAV | Included | Group Study Room3 L1.028 |  | 17.23 | 19.2 |  |  | 18 | 18 | 15
VAV_1F_S11_004 | VAV | Included | Information Literacy Instr 1 L1.020 |  | 17.47 |  |  |  | 27.5 | 25 | 12
VAV_1F_S11_005 | VAV | Included | Information Literacy Instr 1 L1.020 |  | 17.64 |  |  |  | 17.5 | 26 | 15
VAV_1F_S11_006 | VAV | Included | Infor. Lteracy Instr.2 L1.021 |  | 17.71 | 20.75 |  |  | 20.5 | 22 | 15
VAV_1F_S11_007 | VAV | Included | Infor. Lteracy Instr.2 L1.021 |  | 17.72 | 20.75 |  |  | 10 | 21 | 18
VAV_1F_S11_008 | VAV | Included | Infor. Lteracy Instr.2 L1.021 |  | 18.03 | 20.75 |  |  | 0 | 22 | 15
VAV_1F_S11_009 | VAV | Included | Infor. Lteracy Instr.2 L1.021 |  | 17.74 | 20.92 |  |  | 0 | 27 | 14
VAV_1F_S11_010 | VAV | Included | Infor. Lteracy Instr.2 L1.021 |  | 18.6 | 20.75 |  |  | 0 | 22 | 15
VAV_1F_S11_011 | VAV | Included | Infor. Lteracy Instr.2 L1.021 |  | 18.25 | 20.75 |  |  | 26 | 19 | 18
VAV_1F_S11_012 | VAV | Included | Infor. Lteracy Instr.2 L1.021 |  | 18.13 | 20.75 |  |  | 12 | 23 | 27
VAV_1F_S11_013 | VAV | Included | Infor. Lteracy Instr.2 L1.021 |  | 18 | 20.75 |  |  | 26 | 18 | 18
VAV_1F_S11_014 | VAV | Included | Computer Classroom L1.022 |  | 18.36 | 21.07 |  |  | 22 | 22 | 20
VAV_1F_S11_015 | VAV | Included | Computer Classroom L1.022 |  | 17.45 | 21.07 |  |  | 27 | 25 | 27
VAV_1F_S11_016 | VAV | Included | Computer Classroom L1.022 |  | 25.98 | 21.07 |  |  | 26 | 25 | 26
VAV_1F_S11_017 | VAV | Included | Computer Classroom L1.022 |  | 17.29 | 21.07 |  |  | 15 | 24.5 | 15
VAV_1F_S11_018 | VAV | Included | Computer Classroom L1.022 |  | 17.43 | 21.07 |  |  | 26 | 25 | 26
VAV_1F_S11_019 | VAV | Included | Computer Classroom L1.022 |  | 17.63 | 21.07 |  |  | 15 | 25 | 15
VAV_1F_S11_020 | VAV | Included | Computer Classroom L1.022 |  | 18.07 | 21.07 |  |  | 20 | 20 | 10
VAV_1F_S11_021 | VAV | Included | Computer Classroom L1.022 |  | 17.43 | 21.15 |  |  | 25 | 24 | 25
VAV_1F_S11_022 | VAV | Included | Group Study Room 4 L1.029 |  | 16.9 | 19.38 |  |  | 19 | 19 | 10
VAV_1F_S11_087 | VAV | Included | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 |  | 19.93 | 20.68 |  |  | 19 | 26 | 19
VAV_1F_S11_088 | VAV | Included | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 |  | 17.95 | 21.52 |  |  | 23 | 22 | 17
VAV_1F_S11_089 | VAV | Included | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 |  | 17.95 | 21.52 |  |  | 22 | 22 | 10
VAV_1F_S11_090 | VAV | Included | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 |  | 17.89 | 21.56 |  |  | 22 | 20 | 18
VAV_1F_S15_001 | VAV | Included | Media Studio1 L1.063 |  | 17.16 | 18.42 |  |  | 18 | 26 | 18
VAV_1F_S15_002 | VAV | Included | Media Studio1 L1.063 |  | 19.96 | 18.33 |  |  | 18 | 25 | 18
VAV_1F_S15_003 | VAV | Included | Media Studio2 L1.065 |  | 34.28 | 19.62 |  |  | 35 | 35 | 18
VAV_1F_S15_004 | VAV | Included | Media Studio2 L1.065 |  | 17.32 | 19.58 |  |  | 25 | 25 | 18
VAV_1F_S15_005 | VAV | Not Included | Head Librarian Office L1.040 |  | 17.72 |  |  |  | 22.5 | 25 | 12
VAV_1F_S15_006 | VAV | Included | Children Library - Pre School Reading & Playing L1.047 |  | 17.26 | 21.36 |  |  | 21 | 21 | 13
VAV_1F_S15_007 | VAV | Included | Children Library - Pre School Reading & Playing L1.047 |  | 17.19 | 21.36 |  |  | 21 | 21 | 14
VAV_1F_S15_008 | VAV | Included | Children Library - Pre School Reading & Playing L1.047 |  | 17.12 | 21.36 |  |  | 21 | 21 | 12
VAV_1F_S15_009 | VAV | Included | CHILDRENS LIBRARY-PRE SCHOOL COLLECTION L1.047 |  | 17.3 | 21.64 |  |  | 21 | 21 | 14
VAV_1F_S15_010 | VAV | Included | CHILDRENS LIBRARY-PRE SCHOOL COLLECTION L1.047 |  | 17.41 | 21.6 |  |  | 21 | 21 | 19
VAV_1F_S15_011 | VAV | Included | CHILDRENS LIBRARY-PRE SCHOOL COLLECTION L1.047 |  | 17.49 | 21.64 |  |  | 21 | 21 | 13
VAV_1F_S15_012 | VAV | Included | Staff Office L1.048 |  | 17.86 | 21.57 |  |  | 23 | 23 | 16
VAV_1F_S15_021 | VAV | Included | Prayer Room (Female) L1.104 |  | 17.25 | 21.42 |  |  | 20 | 20 | 13
VAV_1F_S15_022 | VAV | Included | Prayer Room (Female) L1.104 |  | 17.07 | 21.42 |  |  | 20 | 20 | 15
VAV_1F_S15_023 | VAV | Included | Prayer Room (Male) L1.104 |  | 16.88 | 20 |  |  | 21 | 21 | 12
VAV_1F_S15_024 | VAV | Included | Prayer Room (Male) L1.104 |  | 17 | 20.17 |  |  | 18 | 18 | 17
VAV_1F_S15_025 | VAV | Included | Ablution (Women) L1.106 |  | 17.44 | 21.54 |  |  | 20 | 20 | 14
VAV_1F_S15_038 | VAV | Included | Ablution (Men) L1.105 |  | 17.09 | 21.73 |  |  | 20 | 20 | 13
VAV_1F_S15_039 | VAV | Included | Green Room L1.002A |  | 17.36 | 20.28 |  |  | 25 | 25 | 12
VAV_1F_S15_039S | VAV | Included | Staff Office L1.048 |  | 17.48 | 21.27 |  |  | 16 | 16 | 13
VAV_1F_S15_040 | VAV | Included | Green Room L1.002A |  | 17.42 | 20.19 |  |  | 22 | 22 | 13
VAV_1F_S15_096 | VAV | Included | Multipurpose Room L1.041 |  | 17.54 | 21.75 |  |  | 22 | 22 | 12
VAV_1F_S15_097 | VAV | Included | Multipurpose Room L1.041 |  | 17.6 | 21.75 |  |  | 22 | 22 | 12
VAV_1F_S15_098 | VAV | Included | Multipurpose Room L1.041 |  | 17.49 | 21.58 |  |  | 16 | 16 | 12
VAV_2F_S10_001 | VAV | Included | GULF MATERIAL L2 |  | 20.22 | 21.71 |  |  | 25 | 23 | 25
VAV_2F_S10_002 | VAV | Included | GULF MATERIAL L2 |  | 19.85 | 21.71 |  |  | 22 | 22 | 14
VAV_2F_S10_003 | VAV | Included | GULF MATERIAL L2 |  | 19.77 | 21.71 |  |  | 22 | 22 | 15
VAV_2F_S10_004 | VAV | Included | GULF MATERIAL L2 |  | 20.56 | 21.71 |  |  | 22 | 26 | 22
VAV_2F_S10_005 | VAV | Included | GULF MATERIAL L2 |  | 19.64 | 21.71 |  |  | 14 | 24 | 14
VAV_2F_S10_006 | VAV | Included | GULF MATERIAL L2 |  | 19.67 | 21.87 |  |  | 16 | 16 | 15
VAV_2F_S12_001 | VAV | Included | OPEN READING AREA L1.001 |  | 16.12 | 25.45 |  |  | 21 | 21 | 18
VAV_2F_S12_002 | VAV | Included | OPEN READING AREA L1.001 |  | 16.08 | 25.86 |  |  | 20 | 20 | 15
VAV_2F_S12_003 | VAV | Included | OPEN READING AREA L1.001 |  | 16.59 | 25.45 |  |  | 23 | 23 | 18
VAV_2F_S12_004 | VAV | Included | OPEN READING AREA L1.001 |  | 16.34 | 25.45 |  |  | 21 | 21 | 20
VAV_2F_S12_005 | VAV | Included | OPEN READING AREA L1.001 |  | 16.24 | 25.45 |  |  | 20 | 20 | 18
VAV_2F_S12_006 | VAV | Included | OPEN READING AREA L1.001 |  | 15.98 | 21.82 |  |  | 22 | 22 | 18
VAV_2F_S12_007 | VAV | Included | OPEN READING AREA L1.001 |  | 15.83 | 21.82 |  |  | 21.5 | 21.5 | 18
VAV_2F_S12_008 | VAV | Included | OPEN READING AREA L1.001 |  | 15.9 | 21.82 |  |  | 21 | 21 | 19
VAV_2F_S12_009 | VAV | Included | OPEN READING AREA L1.001 |  | 15.95 | 21.82 |  |  | 21 | 21 | 20
VAV_2F_S12_010 | VAV | Included | BRAILLE READER L1.002 |  | 15.7 | 21.82 |  |  | 21 | 21 | 20
VAV_2F_S12_011 | VAV | Included | BRAILLE READER L1.002 |  | 15.82 | 22.6 |  |  | 22 | 22 | 20
VAV_2F_S12_012 | VAV | Included | TUTORING HEAD L1.003 |  | 16.11 | 21.82 |  |  | 21 | 21 | 20
VAV_2F_S12_013 | VAV | Included | WRITING ROOM 1 L1.004 |  | 15.86 | 21.82 |  |  | 22 | 22 | 20
VAV_2F_S12_014 | VAV | Included | WRITING HEAD L1.005 |  | 15.73 | 21.82 |  |  | 21 | 21 | 20
VAV_2F_S12_015 | VAV | Included | WRITING ROOM 2 L1.005 |  | 15.96 | 21.82 |  |  | 21 | 21 | 20
VAV_2F_S12_016 | VAV | Included | STUDENT CARRELS L1.007 |  | 16.19 | 21.82 |  |  | 40 | 26 | 20
VAV_2F_S12_017 | VAV | Included | STUDENT CARRELS L1.007 |  | 15.87 | 21.82 |  |  | 21 | 21 | 16
VAV_2F_S12_018 | VAV | Included | STUDENT CARRELS L1.007 |  | 15.92 | 21.82 |  |  | 24 | 24 | 20
VAV_2F_S12_019 | VAV | Included | STUDENT CARRELS L1.007 |  | 16.08 | 21.82 |  |  | 24 | 24 | 24
VAV_2F_S12_020 | VAV | Included | STUDENT CARRELS L1.007 |  | 16.19 | 21.82 |  |  | 24 | 24 | 24
VAV_2F_S12_021 | VAV | Included | Breakout Space L2.010 |  | 16.11 | 23.25 |  |  | 21 | 21 | 18
VAV_2F_S12_022 | VAV | Included | Circulation Office L2.011 |  | 15.97 |  |  |  | 17 | 23 | 21
VAV_2F_S12_023 | VAV | Included | Office SpL Collection L2.012 |  | 19.93 |  |  |  | 26 | 23 | 21
VAV_2F_S12_024 | VAV | Included | Office SpL Collection L2.013 |  | 16.19 |  |  |  | 20.5 | 23 | 21
VAV_2F_S12_025 | VAV | Included | CORRIDOR L2 |  | 16.11 |  |  |  | 20 | 23 | 21
VAV_2F_S12_026 | VAV | Included | Group Study Room 5 L2.015 |  | 15.68 | 21.25 |  |  | 21 | 21 | 18
VAV_2F_S12_027 | VAV | Included | Group Study Room 7 L2.017 |  | 15.75 | 21.62 |  |  | 20 | 20 | 17
VAV_2F_S12_028 | VAV | Included | Meeting Room L2.018 |  | 16.52 | 22.69 |  |  | 23 | 23 | 12
VAV_2F_S12_029 | VAV | Included | Group Study Room 6 L2.016 |  | 16.25 | 22.12 |  |  | 19 | 19 | 18
VAV_2F_S12_097 | VAV | Included | Group Study Room 8 L2.018 |  | 16.15 | 22.02 |  |  | 21 | 21 | 17
VAV_2F_S13_001 | VAV | Not Included | Lib. Director's Room L2.044 |  | 17.9 | 26.06 |  |  | 18 | 18 | 13
VAV_2F_S13_002 | VAV | Not Included | Lib. Director's Room L2.044 |  | 17.66 | 26.21 |  |  | 18 | 18 | 14
VAV_2F_S13_003 | VAV | Included | Service & Lounge L2.043 |  | 17.48 | 23.2 |  |  | 24 | 24 | 21
VAV_2F_S13_004 | VAV | Included | OPEN OFFICE L2.025 |  | 17.8 | 22.69 |  |  | 21 | 21 | 12
VAV_2F_S13_005 | VAV | Included | ACADEMIC PERS. LIBRARIA L2.022 |  | 17.28 |  |  |  | 21.5 | 23 | 21
VAV_2F_S13_006 | VAV | Included | ACD PERS LIBRARIAN L2.022 |  | 17.62 |  |  |  | 24 | 23 | 21
VAV_2F_S13_007 | VAV | Included | AD ADMIN & PLANNING L2.023 |  | 17.63 |  |  |  | 26 | 23 | 21
VAV_2F_S13_008 | VAV | Included | Office Coord L2.024 |  | 18.74 |  |  |  | 18.5 | 23 | 21
VAV_2F_S13_009 | VAV | Included | OPEN OFFICE L2.025 |  | 16.94 | 22.69 |  |  | 18 | 18 | 10
VAV_2F_S13_010 | VAV | Included | CORRIDOR L2 |  | 17.72 | 24.89 |  |  | 22 | 22 | 21
VAV_2F_S13_011 | VAV | Included | CORRIDOR L2 |  | 17.18 | 22.69 |  |  | 18 | 18 | 16
VAV_2F_S13_012 | VAV | Included | CORRIDOR L2 |  | 16.89 | 22.77 |  |  | 25 | 25 | 12
VAV_2F_S13_013 | VAV | Included | CORRIDOR L2 |  | 17.42 | 22.69 |  |  | 22 | 22 | 16
VAV_2F_S13_014 | VAV | Included | CORRIDOR L2 |  | 17.19 | 22.69 |  |  | 19 | 19 | 17
VAV_2F_S13_015 | VAV | Included | CORRIDOR L2 |  | 17.25 | 22.69 |  |  | 22 | 22 | 21
VAV_2F_S13_016 | VAV | Not Included | VIP Waiting ROOM L2.048 |  | 18.22 | 25.25 |  |  | 22 | 22 | 15
VAV_2F_S14_001 | VAV | Included | PUBLIC SERVICES L1.080 |  | 16.48 | 22.46 |  |  | 21 | 21 | 19
VAV_2F_S14_002 | VAV | Included | PUBLIC SERVICES L1.080 |  | 16.95 | 22.46 |  |  | 21 | 21 | 16
VAV_2F_S14_003 | VAV | Included | PUBLIC SERVICES L1.080 |  | 18.11 | 21.25 |  |  | 13 | 24 | 23
VAV_2F_S14_004 | VAV | Included | PUBLIC SERVICES L1.080 |  | 18.27 | 21.25 |  |  | 13 | 23 | 21
VAV_2F_S14_005 | VAV | Included | BIBLIOGRAPHER 1 L1.081 |  | 16.43 | 22.46 |  |  | 20 | 20 | 20
VAV_2F_S14_006 | VAV | Included | BIBLIOGRAPHER 2 L1.082 |  | 17.67 | 22.46 |  |  | 20 | 20 | 18
VAV_2F_S14_007 | VAV | Included | SPEC COLL & ARCH L1.083 |  | 16.64 | 22.46 |  |  | 20 | 20 | 18
VAV_2F_S14_008 | VAV | Included | R&L SERVICES L1.084 |  | 16.6 | 22.46 |  |  | 20 | 20 | 18
VAV_2F_S14_009 | VAV | Included | AD. PUBLIC SERVICE L1.085 |  | 16.57 | 22.46 |  |  | 21.5 | 21.5 | 18
VAV_2F_S14_010 | VAV | Included | REF LIBRARIAN L1.086 |  | 16.26 | 22.46 |  |  | 21 | 21 | 20
VAV_2F_S14_011 | VAV | Included | REF LIBRARIAN L1.087 |  | 16.44 | 22.46 |  |  | 23 | 23 | 16
VAV_2F_S14_012 | VAV | Included | REF LIBRARIAN L1.088 |  | 16.49 | 22.83 |  |  | 21 | 21 | 20
VAV_2F_S14_013 | VAV | Included | REF LIBRARIAN L1.089 |  | 16.21 | 22.46 |  |  | 22 | 22 | 20
VAV_2F_S14_014 | VAV | Included | REF LIBRARIAN L1.090 |  | 16.66 | 21.25 |  |  | 22 | 22 | 16
VAV_2F_S14_015 | VAV | Included | REF LIBRARIAN L1.091 |  | 16.29 | 21.25 |  |  | 21 | 21 | 20
VAV_2F_S14_016 | VAV | Included | REF LIBRARIAN L1.092 |  | 17.75 | 21.25 |  |  | 13 | 22.5 | 23
VAV_2F_S14_017 | VAV | Included | REF LIBRARIAN L1.093 |  | 16.14 | 21.67 |  |  | 22 | 22 | 20
VAV_2F_S14_018 | VAV | Included | REF LIBRARIAN L1.094 |  | 17.48 | 21.25 |  |  | 22 | 22 | 16
VAV_2F_S14_019 | VAV | Included | REF LIBRARIAN L1.095 |  | 16.52 | 21.25 |  |  | 21.5 | 21.5 | 16
VAV_2F_S14_020 | VAV | Included | REF LIBRARIAN L1.096 |  | 16.26 | 21.25 |  |  | 21.5 | 21.5 | 16
VAV_2F_S14_021 | VAV | Included | REF LIBRARIAN L1.097 |  | 16.63 | 21.25 |  |  | 22 | 22 | 20
VAV_2F_S15_001 | VAV | Not Included | VIP Room L2.051 |  | 17.69 | 25.24 |  |  | 16 | 16 | 10
VAV_2F_S15_002 | VAV | Not Included | VIP Room L2.051 |  | 17.6 | 25.4 |  |  | 16 | 16 | 13
VAV_2F_S15_003 | VAV | Not Included | VIP Room L2.051 |  | 17.29 | 25.24 |  |  | 19 | 19 | 13
VAV_2F_S15_004 | VAV | Not Included | VIP Room L2.051 |  | 17.26 | 25.24 |  |  | 16 | 16 | 13
VAV_2F_S15_005 | VAV | Not Included | MAJLIS-VIP Meeting L2.046 |  | 17.81 | 20.9 |  |  | 20 | 25 | 20
VAV_B_S10_001 | VAV | Included | DIGITISATION AREA B.200 |  | 19.39 | 21.07 |  |  | 12 | 25 | 22
VAV_B_S10_002 | VAV | Included | DIGITISATION AREA B.200 |  | 25.6 | 21.07 |  |  | 22 | 23 | 22
VAV_B_S10_003 | VAV | Included | DIGITISATION AREA B.200 |  | 21.26 | 21.07 |  |  | 27 | 24 | 27
VAV_B_S10_004 | VAV | Included | DIGITISATION AREA B.200 |  | 19.69 | 21.07 |  |  | 22 | 19.8 | 22
VAV_B_S10_005 | VAV | Included | DIGITISATION AREA B.200 |  | 28.6 | 21.07 |  |  | 26 | 26 | 26
VAV_B_S10_006 | VAV | Included | DIGITISATION AREA B.200 |  | 19.57 | 21.07 |  |  | 30 | 19.8 | 18
VAV_B_S10_007 | VAV | Included | DIGITISATION AREA B.200 |  | 26.43 | 21.07 |  |  | 27 | 25 | 18
VAV_B_S10_008 | VAV | Included | DIGITISATION AREA B.200 |  | 19.53 | 21.03 |  |  | 22 | 19.8 | 22
VAV_B_S10_009 | VAV | Included | TECHNICAL SERVICES B.203 |  | 19.3 | 19.94 |  |  | 21 | 23 | 21
VAV_B_S10_010 | VAV | Included | TECHNICAL SERVICES B.204 |  | 19.69 | 19.97 |  |  | 15 | 21 | 15
VAV_B_S10_011 | VAV | Included | TECHNICAL SERVICES B.204 |  | 19.43 | 20.06 |  |  | 21 | 21 | 16
VAV_B_S10_012 | VAV | Included | CR6 CONVERSATION WORK AREA B.209 |  | 20.8 | 22.54 |  |  | 30 | 22 | 25
VAV_B_S10_013 | VAV | Included | CR6 CONVERSATION WORK AREA B.209 |  | 26.88 | 22.54 |  |  | 23 | 24 | 23
VAV_B_S10_014 | VAV | Included | CR6 CONVERSATION WORK AREA B.209 |  | 24.55 | 22.71 |  |  | 30 | 26 | 24
VAV_B_S10_015 | VAV | Included | INSTRUCTION OUTREACH B.206 |  | 19.45 | 19.19 |  |  | 15 | 21.5 | 15
VAV_B_S10_016 | VAV | Included | MULTIMEDIA PRESENTATION B.205 |  | 19.63 | 20.39 |  |  | 20 | 20 | 18
VAV_B_S10_017 | VAV | Included | MULTIMEDIA PRESENTATION B.205 |  | 19.55 | 20.39 |  |  | 18 | 18 | 15
VAV_B_S10_018 | VAV | Included | MULTIMEDIA PRESENTATION B.205 |  | 19.58 | 20.39 |  |  | 18 | 21 | 18
VAV_B_S10_019 | VAV | Included | CR6 PROF LIBRARIAN B.208 |  | 19.59 | 21 |  |  | 21 | 21 | 15
VAV_B_S10_020 | VAV | Included | Reserchers Reading Area B.207 |  | 24.05 | 20.51 |  |  | 23 | 23 | 23
VAV_B_S10_021 | VAV | Included | Reserchers Reading Area B.207 |  | 19.99 | 20.51 |  |  | 18 | 23 | 18
VAV_B_S10_022 | VAV | Included | Reserchers Reading Area B.207 |  | 19.73 | 20.51 |  |  | 23 | 23 | 19
VAV_B_S10_023 | VAV | Included | Reserchers Reading Area B.207 |  | 19.43 | 20.51 |  |  | 23 | 23 | 18
VAV_B_S10_024 | VAV | Included | DIGITISATION AREA B.200 |  | 19.31 | 21.07 |  |  | 26 | 25 | 26
VAV_B_S11_001 | VAV | Included | Break Out Area B.001A |  | 17.47 | 23.44 |  |  | 22 | 22 | 21
VAV_B_S11_002 | VAV | Included | Break Out Area B.001A |  | 17.45 | 23.44 |  |  | 21 | 21 | 20
VAV_B_S11_003 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.93 | 23.44 |  |  | 22 | 22 | 20
VAV_B_S11_004 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.4 | 23.44 |  |  | 22 | 22 | 20
VAV_B_S11_005 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.75 | 25.78 |  |  | 22 | 22 | 20
VAV_B_S11_006 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.84 | 25.78 |  |  | 21 | 21 | 18
VAV_B_S11_007 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.57 | 25.78 |  |  | 21 | 21 | 20
VAV_B_S11_008 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.69 | 25.78 |  |  | 22 | 22 | 23
VAV_B_S11_009 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.78 | 25.78 |  |  | 21 | 21 | 20
VAV_B_S11_010 | VAV | Included | Tech, Services & Collections Office B.001 |  | 18.01 | 25.78 |  |  | 21 | 21 | 20
VAV_B_S11_011 | VAV | Included | Break Out Area B.001A |  | 17.65 | 23.44 |  |  | 21 | 21 | 20
VAV_B_S11_012 | VAV | Included | Break Out Area B.001A |  | 17.6 | 23.44 |  |  | 27 | 27 | 12
VAV_B_S11_013 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.64 | 23.72 |  |  | 21 | 21 | 20
VAV_B_S11_014 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.6 | 23.76 |  |  | 21 | 21 | 20
VAV_B_S11_015 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.86 | 25.78 |  |  | 20 | 20 | 16
VAV_B_S11_016 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.66 | 25.78 |  |  | 23 | 23 | 20
VAV_B_S11_017 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.45 | 25.78 |  |  | 22 | 22 | 21
VAV_B_S11_018 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.38 | 25.78 |  |  | 21 | 21 | 19
VAV_B_S11_019 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.52 | 25.78 |  |  | 21 | 21 | 20
VAV_B_S11_020 | VAV | Included | Tech, Services & Collections Office B.001 |  | 17.93 | 26.12 |  |  | 22 | 22 | 21
VAV_B_S11_021 | VAV | Included | Reception & Lounge B.009 |  | 17.5 | 21.72 |  |  | 24 | 25 | 24
VAV_B_S11_022 | VAV | Included | Corridor Leading To Reception & Lounge B.009 |  | 18.17 | 21.53 |  |  | 26 | 23 | 22
VAV_B_S11_023 | VAV | Included | Corridor Leading To Reception & Lounge B.009 |  | 18.24 | 21.44 |  |  | 0 | 24 | 10
VAV_B_S11_024 | VAV | Not Included | Kitchen B.002 |  | 17.78 | 22.53 |  |  | 10 | 25 | 10
VAV_B_S11_025 | VAV | Included | Storage B.028 |  | 22.47 | 17.39 |  |  | 17 | 17 | 10
VAV_B_S11_026 | VAV | Not Included | AD TECH SERVICES DIRECTOR B.003 |  | 24.55 |  |  |  | 23 | 23 | 21
VAV_B_S11_027 | VAV | Not Included | AD TECH SERVICES DIRECTOR B.003 |  | 22.99 |  |  |  | 23 | 23 | 21
VAV_B_S11_028 | VAV | Included | Analogue Resources B.004 |  | 17.39 |  |  |  | 21 | 23 | 21
VAV_B_S11_029 | VAV | Included | Digital Resources B.005 |  | 24.64 |  |  |  | 23 | 23 | 21
VAV_B_S11_030 | VAV | Included | Budget & Payment 1 B.006 |  | 17.5 |  |  |  | 22 | 23 | 21
VAV_B_S11_031 | VAV | Included | Budget & Payment 2 B.007 |  | 22.62 |  |  |  | 25 | 23 | 21
VAV_B_S11_032 | VAV | Included | Ad Collection B.024 |  | 17.48 |  |  |  | 0 | 23 | 13
VAV_B_S11_033 | VAV | Included | Ad Collection B.024 |  | 17.26 |  |  |  | 16 | 23 | 12
VAV_B_S11_034 | VAV | Included | Engineering B.020 |  | 23.61 |  |  |  | 24.5 | 23 | 21
VAV_B_S11_035 | VAV | Included | Arabic Sudies B.021 |  | 17.98 |  |  |  | 12 | 23 | 21
VAV_B_S11_036 | VAV | Included | Licensing Expert B.022 |  | 18.21 |  |  |  | 0 | 23 | 12
VAV_B_S11_037 | VAV | Included | Art & Humanities B.023 |  | 19.52 |  |  |  | 0 | 23 | 18
VAV_B_S11_038 | VAV | Included | HARD & HEALTH SCIENCES B.027 |  | 23.61 |  |  |  | 25 | 23 | 21
VAV_B_S11_039 | VAV | Included | Business Computing B.026 |  | 17.37 |  |  |  | 0 | 23 | 12
VAV_B_S11_040 | VAV | Included | Social Sciences B.025 |  | 17.58 |  |  |  | 17 | 24 | 14
VAV_B_S11_041 | VAV | Included | Literature Language B.029 |  | 17.09 |  |  |  | 17 | 23 | 21
VAV_B_S11_042 | VAV | Included | GENERAL B.030 |  | 17.67 |  |  |  | 21.5 | 24 | 15
VAV_B_S11_043 | VAV | Included | Receiving Area B.008 |  | 18.08 | 20.98 |  |  | 21 | 23 | 10
VAV_B_S11_044 | VAV | Included | Receiving Area B.008 |  | 17.5 | 20.98 |  |  | 10 | 24 | 10
VAV_B_S11_045 | VAV | Included | Receiving Area B.008 |  | 17.27 | 20.98 |  |  | 10 | 24 | 10
VAV_B_S11_046 | VAV | Included | Receiving Area B.008 |  | 17.44 | 21.02 |  |  | 14 | 24 | 14
VAV_B_S13_001 | VAV | Included | Meeting Room B.034 |  | 16.61 |  |  |  | 19.5 | 25 | 12
VAV_B_S13_002 | VAV | Included | Meeting Room B.034 |  | 16.64 |  |  |  | 19.5 | 24 | 11
VAV_B_S13_003 | VAV | Included | Processing Room B.103 |  | 17.84 | 23.18 |  |  | 40 | 22 | 20
VAV_B_S13_004 | VAV | Included | Processing Room B.103 |  | 16.77 | 22.46 |  |  | 21 | 21 | 19
VAV_B_S13_005 | VAV
VAV_B_S13_006 | VAV | Not Included | Fumigation Room B.085 |  | 17.11 | 21.36 |  |  | 12 | 33 | 12
VAV_B_S13_007 | VAV | Included | Shipping CLIRK B.101 |  | 22.89 |  |  |  | 25 | 23 | 21
VAV_B_S13_008 | VAV | Not Included | SECURITY CONTROL ROOM B.105 |  | 17.74 | 23.09 |  |  | 18 | 18 | 15
VAV_B_S14_001 | VAV | Included | Office B.040 |  | 16.36 |  |  |  | 18 | 23 | 21
VAV_B_S14_002 | VAV | Included | Office Dig Init B.056 |  | 16.25 |  |  |  | 22 | 23 | 21
VAV_B_S14_003 | VAV | Included | Office AD For LIT B.057 |  | 16.13 |  |  |  | 19.5 | 23 | 21
VAV_B_S14_004 | VAV | Included | Digitization Room B.041 |  | 16.35 | 22.32 |  |  | 21 | 21 | 16
VAV_B_S14_005 | VAV | Included | Digitization Room B.041 |  | 16.69 | 22.32 |  |  | 18 | 25 | 18
VAV_B_S14_006 | VAV | Included | Digitization Room B.041 |  | 16.82 | 22.32 |  |  | 21 | 21 | 18
VAV_B_S14_007 | VAV | Included | Shell Space B.58 |  | 16.58 |  |  |  | 22 | 23 | 21
VAV_B_S14_008 | VAV | Included | Shell Space B.59 |  | 16.5 |  |  |  | 22 | 23 | 21
VAV_B_S14_009 | VAV | Included | Digitization Room B.041 |  | 16.74 | 21.78 |  |  | 23 | 23 | 16
VAV_B_S14_010 | VAV | Included | Digitization Room B.041 |  | 16.63 | 21.78 |  |  | 21 | 21 | 14
VAV_B_S14_011 | VAV | Included | Digitization Room B.041 |  | 16.63 | 22.32 |  |  | 18 | 26 | 18
VAV_B_S14_012 | VAV | Included | Digitization Room B.041 |  | 16.54 | 22.32 |  |  | 22 | 22 | 11
VAV_B_S14_013 | VAV | Included | Shell Space B.58 |  | 16.99 |  |  |  | 14.5 | 25 | 12
VAV_B_S14_014 | VAV | Included | Shell Space B.59 |  | 18.31 |  |  |  | 25.75 | 23.5 | 14
VAV_B_S14_015 | VAV | Included | Digitization Room B.041 |  | 16.66 | 20.71 |  |  | 21 | 21 | 18
VAV_B_S14_016 | VAV | Included | Digitization Room B.041 |  | 27.65 | 21.04 |  |  | 21 | 23 | 21
VAV_B_S14_040 | VAV | Included | BOH Kitchen B.044 |  | 20.3 | 21.43 |  |  | 18 | 18 | 11
VAV_B_S14_041 | VAV | Included | Fine Binding B.044 |  | 22.37 | 22.22 |  |  | 24 | 30 | 24
VAV_B_S14_042 | VAV | Included | Binding & Preservation B.043 |  | 19.72 | 22.22 |  |  | 24 | 22 | 24
VAV_B_S14_043 | VAV | Included | Binding & Preservation B.043 |  | 17.57 | 22.22 |  |  | 30 | 22 | 26
VAV_B_S14_044 | VAV | Included | Binding & Preservation B.043 |  | 17.45 | 21.97 |  |  | 30 | 19 | 15
VAV_B_S14_045 | VAV | Included | Binding & Preservation B.043 |  | 21.03 | 21.43 |  |  | 22 | 22 | 22
VAV_B_S14_046 | VAV | Included | Binding & Preservation B.043 |  | 22.3 | 21.43 |  |  | 26 | 23 | 26
VAV_B_S14_047 | VAV | Included | Fine Binding B.044 |  | 16.82 | 22.22 |  |  | 12 | 24 | 12
VAV_B_S14_048 | VAV | Included | Binding & Preservation B.043 |  | 17.79 | 22.22 |  |  | 15 | 15 | 15
VAV_B_S14_049 | VAV | Included | Binding & Preservation B.043 |  | 17.98 | 22.22 |  |  | 30 | 20 | 16
VAV_B_S14_050 | VAV | Included | Binding & Preservation B.043 |  | 19.83 | 22.04 |  |  | 22 | 22 | 22
VAV_B_S14_051 | VAV | Included | Binding & Preservation B.043 |  | 21.02 | 21.43 |  |  | 24 | 23 | 24
VAV_B_S15_001 | VAV | Included | Prof. Librarian B.153 |  | 17.54 | 19.93 |  |  | 0 | 26 | 26
VAV_B_S15_002 | VAV | Included | Lobby and Security B.145 |  | 37.25 | 19.88 |  |  | 27 | 25 | 14
VAV_B_S15_003 | VAV | Included | Lobby and Security B.145 |  | 17.75 | 20.8 |  |  | 0 | 24 | 22
VAV_B_S15_004 | VAV | Included | Lobby and Security B.145 |  | 18.56 | 20.63 |  |  | 12 | 23 | 20
VAV_B_S15_005 | VAV | Included | Prof. Librarian B.153 |  | 17.34 |  |  |  | 20.93 | 23 | 21
VAV_B_S15_006 | VAV | Included | Prof. Librarian B.153 |  | 17.13 |  |  |  | 21.04 | 22 | 20
VAV_B_S15_007 | VAV | Not Included | HC SECURITY ROOM B.152 |  | 25.72 | 21.17 |  |  | 24 | 24 | 24
VAV_B_S15_008 | VAV | Included | RESEARCH & DOC RECORD MGMT B.151 |  | 17.21 |  |  |  | 24 | 22 | 19
VAV_B_S15_009 | VAV | Not Included | HC DIRECTOR HEAD B.149 |  | 17.32 |  |  |  | 10 | 22 | 21
VAV_B_S15_010 | VAV | Not Included | HC DIRECTOR HEAD B.149 |  | 23.13 |  |  |  | 22.34 | 21 | 20
VAV_B_S15_011 | VAV | Not Included | VIP Majlis B.149 |  | 17.4 | 21.39 |  |  | 20 | 20 | 20
VAV_B_S15_012 | VAV | Not Included | VIP Majlis B.149 |  | 17.43 | 21.39 |  |  | 21 | 21 | 19
VAV_B_S15_013 | VAV | Included | RESEARCH & DOC RECORD MGMT B.151 |  | 17.45 |  |  |  | 11 | 26 | 25
CAV_1F_S11_001 | CAV |  | CORRIDOR L1.023 |  | 20.65 |  |  |  | 21 | 20 | 21
CAV_1F_S11_002 | CAV |  | CORRIDOR L1.023 |  | 17.53 |  |  |  | 17 | 30 | 17
CAV_1F_S11_006 | CAV |  | CHILDRENS LIBRRY CIRCULATION NW GLAZED L1.047 |  | 17.81 |  |  |  | 23.2 | 23.2 | 10
CAV_1F_S11_007 | CAV |  | CORRIDOR L1.023 |  | 15.23 |  |  |  | 15 | 25 | 15
CAV_1F_S11_008 | CAV |  | CHILDRENS LIBRRY CIRCULATION NW GLAZED L1.047 |  | 17.54 |  |  |  | 23.5 | 23.5 | 10
CAV_1F_S11_009 | CAV |  | CHILDRENS LIBRRY CIRCULATION NW GLAZED L1.047 |  | 17.88 |  |  |  | 17 | 23 | 17
CAV_1F_S15_002 | CAV |  | Restaurant L1.150 |  | 24.06 |  |  |  | 21 | 21 | 17
CAV_1F_S15_004 | CAV |  | AERIAL PLATFORM PARKING L1.100 |  | 17.51 |  |  |  | 17 | 22 | 17
CAV_1F_S15_005 | CAV |  | Restaurant L1.150 |  | 17.46 |  |  |  | 21 | 21 | 14
CAV_1F_S15_006 | CAV |  | Restaurant L1.150 |  | 17.32 |  |  |  | 17 | 21 | 17
CAV_1F_S15_010 | CAV |  | Restaurant L1.150 |  | 16.84 |  |  |  | 22 | 22 | 10
CAV_1F_S15_011 | CAV |  | Restaurant L1.150 |  | 17.39 |  |  |  | 20 | 20 | 12
CAV_1F_S15_012 | CAV |  | Restaurant L1.150 |  | 17.45 |  |  |  | 21 | 21 | 17
CAV_1F_S15_013 | CAV |  | Restaurant L1.150 |  | 17.35 |  |  |  | 12 | 25 | 12
CAV_1F_S15_014 | CAV |  | Restaurant L1.150 |  | 17.4 |  |  |  | 21 | 21 | 12
CAV_1F_S15_015 | CAV |  | Restaurant L1.150 |  | ?????? |  |  |  | 21 | 21 | 12
CAV_1F_S15_016 | CAV |  | Restaurant L1.150 |  | 17.34 |  |  |  | 22 | 22 | 12
CAV_1F_S15_017 | CAV |  | Restaurant L1.150 |  | 17.07 |  |  |  | 21 | 21 | 10
CAV_1F_S15_018 | CAV |  | AREAL PLATFORM PARK L1.100 |  | 17.56 |  |  |  | 17 | 22 | 17
CAV_1F_S15_019 | CAV |  | FURNITURE STORE L1.153 |  | 17.65 | 20.18 |  |  | 12 | 24 | 12
CAV_B_S12_001 | CAV |  | CORRIDOR B.061 |  | 16.05 | 48.92 |  |  | 22 | 22 | 15
CAV_B_S12_002 | CAV |  | Plant Room 1 B.063 |  | 17.77 |  |  |  | 13 | 26 | 17
CAV_B_S12_003 | CAV |  | Plant Room 1 B.063 |  | 17.76 |  |  |  | 0 | 26 | 17
CAV_B_S13_001 | CAV |  | Corridor 2 B.064 |  | 17.71 |  |  |  | 17 | 28 | 24
CAV_B_S13_002 | CAV |  | Corridor 2 B.064 |  | 17.52 |  |  |  | 23 | 28 | 26
CAV_B_S13_003 | CAV |  | Corridor 2 B.064 |  | 17.46 | 20.28 |  |  | ?????? | 25 | 22
CAV_B_S13_004 | CAV |  | Corridor 2 B.064 |  | 18.28 |  |  |  | 15 | 26 | 24
CAV_B_S13_005 | CAV |  | Corridor 2 B.064 |  | 18.36 |  |  |  | 11 | 26 | 24
CAV_B_S13_006 | CAV |  | CORRIDOR 4 B.035 |  | 16.42 |  |  |  | 17 | 26 | 17
CAV_B_S13_007 | CAV |  | CORRIDOR 4 B.035 |  | 18.13 |  |  |  | 0 | 26 | 14
CAV_B_S13_008 | CAV |  | CORRIDOR 4 B.035 |  | 16.56 |  |  |  | 25 | 23 | 25
CAV_B_S13_009 | CAV |  | IT STORAGE B.104 |  | 18.14 |  |  |  | 17 | 25 | 17
CAV_B_S13_010 | CAV |  | Plant Room 2 B.070 |  | 19.11 |  |  |  | 15 | 26 | 17
CAV_B_S13_011 | CAV |  | Plant Room 2 B.070 |  | 18.3 |  |  |  | 11 | 26 | 25
CAV_B_S13_012 | CAV |  | Fire Command B.071 |  | 16.81 |  |  |  | 23 | 23 | 13
CAV_B_S13_013 | CAV |  | GAS SUPPRESSION B.087 |  | 18.36 |  |  |  | 15 | 22 | 22
CAV_B_S13_014 | CAV |  | PEOPLE MOVER B.088 |  | 18.17 |  |  |  | 12 | 28 | 15
CAV_B_S13_015 | CAV |  | Server Room B.089 |  | 16.72 |  |  |  | 17 | 24 | 17
CAV_B_S13_020 | CAV |  | UPS BATTERY ROOM B.084 |  | 20.58 |  |  |  | 20 | 23 | 20
CAV_B_S13_021 | CAV |  | Sprinklers Pumps & Zones Valves B.072 |  | 17.11 |  |  |  | 0 | 26 | 12
CAV_B_S13_050 | CAV |  | PLANT ROOM B.104A |  | ?????? |  |  |  | ?????? | ?????? | ??????
CAV_B_S14_001 | CAV |  | CORRIDOR 3 B.051 |  | 18.56 |  |  |  | 22 | 30 | 22
CAV_B_S14_002 | CAV |  | CORRIDOR 3 B.052 |  | 16.41 |  |  |  | 16.17 | 20 | 13
CAV_B_S14_003 | CAV |  | PLANT ROOM 3 B.110 |  | 18.95 |  |  |  | 0 | 23 | 12
CAV_B_S14_004 | CAV |  | PLANT ROOM 3 B.110 |  | 17.89 |  |  |  | 0 | 23 | 12
CAV_B_S14_005 | CAV |  | PLANT ROOM 3 B.110 |  | 18 |  |  |  | 0 | 23 | 13
CAV_B_S14_006 | CAV |  | Referigerate Store Kitchen Lobby B.044 |  | 16.71 |  |  |  | 18 | 18 | 12
CAV_B_S14_007 | CAV |  | Washing Area & Fine Binding B.044 |  | 15.69 |  |  |  | 15 | 23 | 15
CAV_B_S15_001 | CAV |  | Corridor 5 B.063 |  | 17.96 |  |  |  | 12 | 23 | 21
CAV_B_S15_002 | CAV |  | Corridor 5 B.063 |  | 18.71 |  |  |  | 0 | 26 | 13
CAV_B_S15_003 | CAV |  | Corridor 5 B.063 |  | 19.05 |  |  |  | 0 | 24 | 12
Note on D74: Ahmad Sharaf Al Masri: HMI reads 56.3 C on IMG_9601.jpeg - by far the highest reading seen across all QNL drawings, against 19.6 C on FCU-1F-058 directly beneath it. Almost certainly a failed sensor; worth raising with the BMS team.
Note on D117: Ahmad Sharaf Al Masri: IMG_9592.jpeg (Basement Zone-3-P2): FCU-B-001 is drawn outside the plan outline on the left with no leader line to any room. Nearest labels are 'IDF Rooom' and 'VIP Restroom', both of which would make this Not Included (technical / executive). Key Plan name used per the agreed rule - please confirm.
Note on D154: Ahmad Sharaf Al Masri: FCU-B-038 shows '??????' instead of a temperature on the HMI (no sensor reading). Room name taken from its yellow leader line pointing into the Pantry.
Note on D184: Ahmad Sharaf Al Masri: HMI reads 34.1 C on IMG_9599.jpeg - well above the ~17-20 C of the adjacent media studios. Consistent with an unconditioned store, but worth checking.
Note on D330: Ahmad Sharaf Al Masri: CONFLICT: previously recorded as 'Plant Room 1 / Plant Room 2 (IMG_9588.jpeg)', Not Included. Honeywell BMS VAV Summary Type-01 (IMG_9563.jpeg) groups VAV/B/S11/022 (Master) and /023 (Slave) together under 'Basement Zone 1 Corridor Leading To Reception & Lounge B009'. Updated to match the BMS and changed to Included. Verify against the basement drawing before final sign-off.
Note on D366: Ahmad Sharaf Al Masri: HMI label on IMG_9589.jpeg reads 'VAV-B-S11-005'. Positionally it sits between VAV-B-S14-004 and VAV-B-S14-006 in the Digitization Room, and VAV_B_S11_005 (row 1075) is already assigned to Tech, Services & Collections Office from IMG_9587.jpeg. Recorded here as S14_005 - please confirm the correct HMI tag.
Note on D398: Ahmad Sharaf Al Masri: Flagged for the executive-room rule, not for the room name. 'Asst. Head' is a management office - confirm whether it counts as an executive room (Not Included) or a senior staff office (currently Included).
Note on D399: Ahmad Sharaf Al Masri: Flagged for the executive-room rule, not for the room name. 'Asst. Head' is a management office - confirm whether it counts as an executive room (Not Included) or a senior staff office (currently Included).

## RDC Asset Registry
Controllable Asset Registry
Tag No. | Equipment Type | Inluded/ Not Inlcuded | ROOM NAME AS PER DRAWINGS | ZONES SERVED | Return Air Temp (°C) | Occupied SP (°C) | Unoccupied SP (°C) | Outside Air Temp (°C) | Exhaust Air Temp (°C) | Discharge Air Temp (°C)
RDC_NB_2F_AHU8511 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | Common Header |  |  |  | 40.2 |  | 12.9
RDC_NB_2F_AHU8512 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | Common Header |  |  |  | 17.3 |  | 17
RDC_NB_2F_AHU8513 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | Common Header |  |  |  | 40 |  | 13.7
RDC_NB_2F_AHU8514 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | Common Header |  |  |  | 28.5 |  | 13.3
RDC_NB_2F_AHU8515 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | Common Header |  |  |  | 40.6 |  | 13.6
RDC_NB_2F_AHU8516 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | Common Header |  |  |  | 40.1 |  | 13.3
RDC_NB_2F_AHU8517 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | Common Header |  |  |  | 40.1 |  | 14.6
RDC_NB_2F_AHU8518 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | Common Header |  |  |  | 39.6 |  | 13.7
RDC_NB_2F_AHU8519 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | Common Header |  |  |  | 37.5 |  | 13.8
RDC_NB_2F_AHU8520 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | Common Header |  |  |  | 39.4 |  | 14.5
RDC_NB_2F_AHU8521 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | Common Header |  |  |  | 39.4 |  | 13.3
RDC_SB_2F_AHU8011 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | Common Header | NA |  |  | 41.1 | 21.6 | 15.7
RDC_SB_2F_AHU8012 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | Common Header | NA |  |  | 42.7 | 20.8 | 19.5
RDC_SB_2F_AHU8021 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | Common Header | 22 |  |  | NA | NA | 14.8
RDC_SB_2F_AHU8022 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | Common Header | 21.6 |  |  | NA | NA | 15
RDC_SB_2F_AHU8023 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | Common Header | 22.2 |  |  | NA | NA | 15
RDC_SB_2F_AHU8024 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | Common Header | 21 |  |  | NA | NA | 12
RDC_SB_2F_AHU8025 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | Common Header | 21.6 |  |  | NA | NA | 14.8
RDC_SB_2F_AHU8026 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | Common Header | 21.9 |  |  | NA | NA | 15.1
RDC_SB_GF_AHU8031 | AHU | Included | COMPUTER RESEARCH LAB S-1112 | Ceiling Mounted AHU | NA |  |  | 22.9 | NA | 15.8
RDC_SB_GF_AHU8032 | AHU | Included | COMPUTER RESEARCH LAB S-1112 | Ceiling Mounted AHU | NA |  |  | 19.9 | NA | 18.3
RDC_SB_GF_AHU8033 | AHU | Included | COMPUTER RESEARCH LAB S-1112 | Ceiling Mounted AHU | NA |  |  | 19.8 | NA | 18.4
RDC_SB_GF_AHU8034 | AHU | Included | COMPUTER RESEARCH LAB S-1112 | Ceiling Mounted AHU | NA |  |  | 20.4 | NA | 18.6
RDC_SB_GF_AHU8035 | AHU | Included | COMPUTER RESEARCH LAB S-1112 | Ceiling Mounted AHU | NA |  |  | 21.9 | NA | 15.7
RDC_SB_GF_AHU8036 | AHU | Included | COMPUTER RESEARCH LAB S-1112 | Ceiling Mounted AHU | NA |  |  | NA | NA | 16.1
RDC_SB_GF_AHU8037 | AHU | Included | COMPUTER RESEARCH LAB S-1112 | Ceiling Mounted AHU | NA |  |  | NA | NA | 17.1
RDC_SB_GF_AHU8041 | AHU | Not Included | UPS ROOM S-0145 | serving this room | 20 |  |  | 18.9 | 20.9 | NA
RDC_SB_GF_AHU8042 | AHU | Not Included | UPS ROOM S-0145 | serving this room | 18.9 |  |  | 18.9 | 20.9 | NA
RDC_UB_AHU8601 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | Multiple rooms | 38.7 |  |  |  |  | 19
RDC_UB_AHU8602 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | Multiple rooms | 21.7 |  |  |  |  | 15.2
RDC_UB_AHU8603 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | Serving Technical Room (TRANSFORMER) | 22.4 |  |  |  |  | 17.5
RDC_UB_AHU8604 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | Serving Technical Room (TRANSFORMER) | 24.1 |  |  |  |  | 17.1
RDC_UB_AHU8605 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | Multiple rooms | 24.4 |  |  |  |  | 19.8
RDC_UB_AHU8606 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | Multiple rooms | 23.1 |  |  |  |  | 21.2
RDC_UB_AHU8607 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | Serving Technical Room (TRANSFORMER) | 22.8 |  |  |  |  | 19.8
RDC_UB_AHU8608 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | Serving Technical Room (TRANSFORMER) | 24.6 |  |  |  |  | 18.2
RDC_UB_AHU8609 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | Serving Technical Room (TRANSFORMER) | 24.5 |  |  |  |  | 18.1
RDC_NB_GF_VAV4001 | VAV | Included | Store N-0201
RDC_NB_GF_VAV4005_EV4006 | EV | Not Included | Electrical N-0202
RDC_NB_GF_VAV4040 | VAV | Not Included | Air Quality High Bay N-0215A
RDC_NB_GF_VAV4050_VEV4051 | VEV | Not Included | CSP High Bay N-0215B
RDC_NB_GF_VAV4060_VEV4061 | VEV | Not Included | Machine Shop N-0215C
RDC_NB_GF_VAV4070A_VEV4073A | VAV | Included | Open High Bay Lab N-0215D
RDC_NB_GF_VAV4070B_VEV4073B | VAV | Included | Open High Bay Lab N-0215D
RDC_NB_GF_VAV4071A_VEV4074A | VAV | Included | Open High Bay Lab N-0215D
RDC_NB_GF_VAV4071B_VEV4074B | VAV | Included | Open High Bay Lab N-0215D
RDC_NB_GF_VAV4072A_VEV4075A | VAV | Included | Open High Bay Lab N-0215D
RDC_NB_GF_VAV4072B_VEV4075B | VAV | Included | Open High Bay Lab N-0215D
RDC_NB_GF_VAV4080A_VEV4082A | VAV | Included | Desal High Bay Lab N-0215E
RDC_NB_GF_VAV4080B_VEV4082B | VAV | Included | Desal High Bay Lab N-0215E
RDC_NB_GF_VAV4081A_VEV4083A | VAV | Included | Desal High Bay Lab N-0215E
RDC_NB_GF_VAV4081B_VEV4083B | VAV | Included | Desal High Bay Lab N-0215E
RDC_NB_GF_VAV4090_VEV4091 | VEV | Included | Support Lab N-0215F
RDC_NB_GF_VAV4100_EV4101 | EV | Not Included | Emergency Elec. Room N-0225
RDC_NB_GF_VAV4105_EV4106 | EV | Not Included | Normal Electrical Room N-0225
RDC_NB_GF_VAV4110_EV4111 | EV | Included | Conference Room N-0227
RDC_NB_GF_VAV4115_EV4116 | EV | Included | Office N-0228
RDC_NB_GF_VAV4120_EV4121 | EV | Included | Office N-0229
RDC_NB_GF_VAV4125_EV4126 | EV | Included | Office N-0230
RDC_NB_GF_VAV4130_EV4131 | EV | Included | Office N-0231
RDC_NB_GF_VAV4135_EV4136 | EV | Included | Office N-0232
RDC_NB_GF_VAV4140_EV4141 | EV | Included | Conference Room N-0233
RDC_NB_GF_VAV4145_EV4146 | EV | Included | Office N-0234
RDC_NB_GF_VAV4165_EV4166 | EV | Included | Office N-0236
RDC_NB_GF_VAV4180_VEV4181 | VEV | Included | Test Room N-0240A
RDC_NB_GF_VAV4190_VEV4192 | VEV | Included | CSP Lab N-0240B
RDC_NB_GF_VAV4191 | VAV | Included | CSP Lab N-0240B
RDC_NB_GF_VAV4200_VEV4201 | VEV | Included | Test Room 1 N-0240C
RDC_NB_GF_VAV4210 | VAV | Included | Desalination Lab N-0240D
RDC_NB_GF_VAV4211 | VAV | Included | Desalination Lab N-0240D
RDC_NB_GF_VAV4212 | VAV | Included | Desalination Lab N-0240D
RDC_NB_GF_VAV4225 | VAV | Included | Office N-0247
RDC_NB_GF_VAV4230 | VAV | Included | Office N-0248
RDC_NB_GF_VAV4235 | VAV | Included | Office 05 -8WS- N-0250
RDC_NB_GF_VAV4240 | VAV | Included | Office 04 N-0251
RDC_NB_GF_VAV4245 | VAV | Included | Office N-0252
RDC_NB_GF_VAV4250 | VAV | Included | Office N-0253
RDC_NB_GF_VAV4255 | VAV | Included | Office N-0254
RDC_NB_GF_VAV4260 | VAV | Included | Office 05 -8WS- N-0255
RDC_NB_GF_VAV4265 | VAV | Included | Office N-0256
RDC_NB_GF_VAV4270 | VAV | Included | Office N-0257
RDC_NB_GF_VAV4275 | VAV | Included | Office N-0258
RDC_NB_GF_VAV4280 | VAV | Included | Office N-0259
RDC_NB_GF_VAV4285 | VAV | Included | Workstation N-0260
RDC_NB_GF_VAV4290 | VAV | Included | Office 04 N-0261
RDC_NB_GF_VAV4295 | VAV | Included | Office N-0262
RDC_NB_GF_VAV4300 | VAV | Included | Office N-0263
RDC_NB_GF_VAV4305 | VAV | Included | Office N-0264
RDC_NB_GF_VAV4310 | VAV | Included | Workstation N-0265
RDC_NB_GF_VAV4312 | VAV | Included | Breakout N-0265B
RDC_NB_GF_VAV5000_EV5002 | EV | Included | Lobby North N-0101
RDC_NB_GF_VAV5001_EV5003 | EV | Included | Lobby North N-0101
RDC_NB_GF_VAV5010_EV5011 | EV | Included | Conf N-0106
RDC_NB_GF_VAV5015_EV5016 | EV | Included | Conference N-0107
RDC_NB_GF_VAV5025 | VAV | Included | Corridor N-0110
RDC_NB_GF_VAV5030_EV5031 | EV | Included | Confr Room N-0112
RDC_NB_GF_VAV5040_EV5041 | EV | Not Included | Normal Elec. N-0113
RDC_NB_GF_VAV5045_EV5046 | EV | Not Included | Emergency Elec. N-0114
RDC_NB_GF_VAV5050 | VAV | Included | Analytical Core Lab 1 N-0114A
RDC_NB_GF_VAV5051 | VAV | Included | Analytical Core Lab 1 N-0114A
RDC_NB_GF_VAV5054 | VAV | Included | Clean Lab N-0114B
RDC_NB_GF_VAV5060_CEV5061 | CEV | Included | Clean Lab N-0114B
RDC_NB_GF_VAV5070 | VAV | Included | Dirty Lab N-0114C
RDC_NB_GF_VAV5080_VEV5081 | VEV | Included | Bio Analyt N-0114D
RDC_NB_GF_VAV5090 | VAV | Included | Air Quality N-0114F
RDC_NB_GF_VAV5091 | VAV | Included | Air Quality N-0114F
RDC_NB_GF_VAV5100_EV5101 | EV | Included | Office N-0115
RDC_NB_GF_VAV5105 | VAV | Included | Office N-0116
RDC_NB_GF_VAV5110 | VAV | Included | Office N-0117
RDC_NB_GF_VAV5115 | VAV | Included | Office N-0118
RDC_NB_GF_VAV5120 | VAV | Included | Office N-0119
RDC_NB_GF_VAV5125 | VAV | Included | Office N-0120
RDC_NB_GF_VAV5130 | VAV | Included | Office N-0121
RDC_NB_GF_VAV5135 | VAV | Included | Office N-0122
RDC_NB_GF_VAV5140 | VAV | Included | Office N-0123
RDC_NB_GF_VAV5145 | VAV | Included | Office N-0124
RDC_NB_GF_VAV5150 | VAV | Included | Office N-0125
RDC_NB_GF_VAV5152 | VAV | Included | Office N-0126
RDC_NB_GF_VAV5155 | VAV | Included | Office N-0127
RDC_NB_GF_VAV5156 | VAV | Included | Office 04 N-0129
RDC_NB_GF_VAV5165_EV5166 | EV | Included | Corridor N-0134
RDC_NB_GF_VAV5180 | VAV | Included | Analytical Core Lab 2 N-0140A
RDC_NB_GF_VAV5181 | VAV | Included | Analytical Core Lab 2 N-0140A
RDC_NB_GF_VAV5190 | VAV | Not Included | Furnace Room N-0140B
RDC_NB_GF_VAV5200 | VAV | Included | Prep Lab N-0140C
RDC_NB_GF_VAV5210 | VAV | Included | Sputter Room N-0140D
RDC_NB_GF_VAV5220 | VAV | Included | MBE/Evap Room N-0140E
RDC_NB_GF_VAV5230 | VAV | Included | ALD Room N-0140F
RDC_NB_GF_VAV5250_VEV5251 | VEV | Included | Support Room N-0140H
RDC_NB_GF_VAV5260_VEV5261 | VEV | Included | PLD Room N-0140J
RDC_NB_GF_VAV5270A | VAV | Included | Organic Chemistry Lab N-0140K
RDC_NB_GF_VAV5270B | VAV | Included | Org Chem N-0140K
RDC_NB_GF_VAV5295_EV5296 | EV | Included | Conference Room N-0149
RDC_NB_GF_VAV5300 | VAV | Included | Corridor N-0150
RDC_NB_GF_VAV5305 | VAV | Included | Office N-0151
RDC_NB_GF_VAV5310 | VAV | Included | Office N-0152
RDC_NB_GF_VAV5315 | VAV | Included | Open Office N-0153
RDC_NB_GF_VAV5325 | VAV | Included | Office N-0155
RDC_NB_GF_VAV5330 | VAV | Included | Office N-0156
RDC_NB_GF_VAV5335 | VAV | Included | Office N-0157
RDC_NB_GF_VAV5340 | VAV | Included | Office N-0158
RDC_NB_GF_VAV5345 | VAV | Included | Office N-0159
RDC_NB_GF_VAV5355 | VAV | Included | Office N-0161
RDC_NB_GF_VAV5360 | VAV | Included | Office N-0162
RDC_NB_GF_VAV5365 | VAV | Included | Office N-0163
RDC_NB_GF_VAV5370 | VAV | Included | Office N-0164
RDC_NB_GF_VAV5380 | VAV | Included | Office N-0166
RDC_NB_GF_VAV5385 | VAV | Included | Office N-0167A
RDC_NB_GF_VAV5390 | VAV | Included | Office 04 N-0168
RDC_NB_GF_VAV5395 | VAV | Included | Exp. Office N-0169
RDC_NB_GF_VAV5400 | VAV | Included | Reception Area N-0170
RDC_NB_GF_VAV5405 | VAV | Included | Exp. Office N-0172
RDC_NB_GF_VAV5410_EV5411 | EV | Included | Conf Room N-0173
RDC_NB_GF_VAV5415 | VAV | Included | Office 04 N-0174
RDC_NB_GF_VAV6000_EV6001 | EV | Included | Conf Room N-0301
RDC_NB_GF_VAV6010_EV6011 | EV | Included | Conf N-0304
RDC_NB_GF_VAV6025_EV6026 | EV | Not Included | Normal Elec. N-0310
RDC_NB_GF_VAV6130_EV6131 | EV | Included | Store N-0315
RDC_NB_GF_VAV6135 | VAV | Included | Store N-0316
RDC_NB_GF_VAV6140 | VAV | Included | Workstation N-0317
RDC_NB_GF_VAV6145 | VAV | Included | Office N-0318
RDC_NB_GF_VAV6150 | VAV | Included | Office N-0319
RDC_NB_GF_VAV6155 | VAV | Included | Workstation N-0320
RDC_NB_GF_VAV6160 | VAV | Included | Office N-0321
RDC_NB_GF_VAV6170 | VAV | Included | Office N-0323
RDC_NB_GF_VAV6175 | VAV | Included | Workstation N-0324
RDC_NB_GF_VAV6180 | VAV | Included | Office N-0325
RDC_NB_GF_VAV6185_EV6186 | EV | Included | Office N-0326
RDC_NB_GF_VAV6190_EV6191 | EV | Not Included | Normal Elec. N-0328
RDC_NB_GF_VAV6195 | VAV | Included | Store N-0329
RDC_NB_GF_VAV6200_EV6201 | EV | Included | Conf N-0330
RDC_NB_GF_VAV6205_EV6206 | EV | Included | Conf N-0331
RDC_NB_GF_VAV6210 | VAV | Included | N-0332C
RDC_NB_GF_VAV6220_EV6221 | EV | Not Included | Emergency Elec. N-0333
RDC_NB_GF_VAV6240_EV6241 | EV | Not Included | Emergency Electrical N-0350A
RDC_NB_GF_VAV6285_EV6286 | EV | Included | Conf N-0358
RDC_NB_GF_VAV6295_EV6296 | EV | Included | Conference N-0360
RDC_NB_GF_VAV6300 | VAV | Included | Store N-0362B
RDC_NB_GF_VAV6305 | VAV | Included | Office N-0363
RDC_NB_GF_VAV6310 | VAV | Included | Office N-0364
RDC_NB_GF_VAV6315_EV6316 | EV | Included | Conf Room N-0364A
RDC_NB_GF_VAV6320 | VAV | Included | Corridor N-0365
RDC_NB_GF_VAV6325 | VAV | Included | Office N-0366
RDC_NB_GF_VAV6330 | VAV | Included | Office 04 N-0367
RDC_NB_GF_VAV6335 | VAV | Included | Office N-0368
RDC_NB_GF_VAV6340 | VAV | Included | Office N-0369
RDC_NB_GF_VAV6345 | VAV | Included | Office N-0370
RDC_NB_GF_VAV6350 | VAV | Included | Office N-0371
RDC_NB_GF_VAV6355 | VAV | Included | Workstation N-0372
RDC_NB_GF_VAV6360 | VAV | Included | Office N-0374
RDC_NB_GF_VAV6365 | VAV | Included | Office N-0375
RDC_NB_GF_VAV6370 | VAV | Included | Office N-0376
RDC_NB_GF_VAV6375 | VAV | Included | Office N-0377
RDC_NB_GF_VAV6380 | VAV | Included | Workstation N-0378
RDC_NB_GF_VAV6390 | VAV | Included | Office N-0379
RDC_NB_GF_VAV6395 | VAV | Included | Office N-0380
RDC_NB_GF_VAV6400 | VAV | Included | Workstation N-0381
RDC_NB_GF_VAV6405 | VAV | Included | Office N-0382
RDC_NB_GF_VAV6410 | VAV | Included | Office N-0383
RDC_NB_GF_VAV7000 | VAV | Included | Vestibule Staging N-0401
RDC_NB_GF_VAV7020A | VAV | Included | NMR Lab N-0404A
RDC_NB_GF_VAV7020B | VAV | Included | NMR Lab N-0404A
RDC_NB_GF_VAV7021A | VAV | Included | NMR Lab N-0404A
RDC_NB_GF_VAV7021B | VAV | Included | NMR Lab N-0404A
RDC_NB_GF_VAV7030_VEV7031 | VEV | Not Included | CONTROL ROOM N-0404B
RDC_NB_GF_VAV7040 | VAV | Included | Service Equipm. Room N-0404C
RDC_NB_GF_VAV7050_VEV7051 | VEV | Included | EM Prep 1 - MAT N-0404D
RDC_NB_GF_VAV7060_VEV7061 | VEV | Included | EM Prep 2 - BIO N-0404E
RDC_NB_GF_VAV7070A | VAV | Included | Surf Analysis Lab N-0404F
RDC_NB_GF_VAV7070B | VAV | Included | Surf Analysis Lab N-0404F
RDC_NB_GF_VAV7071A | VAV | Included | Surf Analysis Lab N-0404F
RDC_NB_GF_VAV7071B | VAV | Included | Surf Analysis Lab N-0404F
RDC_NB_GF_VAV7080 | VAV | Included | Exp. Office N-0410
RDC_NB_GF_VAV7085 | VAV | Included | Office N-0411
RDC_NB_GF_VAV7090 | VAV | Included | Office N-0412
RDC_NB_GF_VAV7095 | VAV | Included | Office N-0413
RDC_NB_GF_VAV7100 | VAV | Included | Office N-0414
RDC_NB_GF_VAV7105 | VAV | Included | Office N-0415
RDC_NB_GF_VAV7110 | VAV | Included | Office N-0416
RDC_NB_GF_VAV7115 | VAV | Included | Office N-0417
RDC_NB_GF_VAV7120 | VAV | Included | Office N-0418
RDC_NB_GF_VAV7125_EV7126 | EV | Not Included | Normal Elec. Room N-0420
RDC_NB_GF_VAV7130 | VAV | Included | Office N-0421
RDC_NB_GF_VAV7135 | VAV | Included | Office N-0422
RDC_NB_GF_VAV7140_EV7141 | EV | Included | Conference N-0423
RDC_NB_GF_VAV7145 | VAV | Included | Office N-0425
RDC_NB_GF_VAV7155 | VAV | Included | Office N-0427
RDC_NB_GF_VAV7165 | VAV | Included | Office N-0429
RDC_NB_GF_VAV7175 | VAV | Included | Office 05-15-WS N-0431
RDC_NB_GF_VAV7176 | VAV | Included | Office 05-15-WS N-0431
RDC_NB_GF_VAV7180 | VAV | Included | Corridor N-0432
RDC_NB_GF_VAV7185_EV7186 | EV | Not Included | Emer. Elec. Room N-0433
RDC_NB_GF_VAV7195 | VAV | Included | Office 04 N-0436
RDC_NB_GF_VAV7205 | VAV | Included | Office 04 N-0438
RDC_NB_GF_VAV7215_EV7216 | EV | Included | Conference Room N-0440
RDC_NB_GF_VAV7220_CEV7221 | CEV | Included | Service Corridor N-0441
RDC_NB_GF_VAV7230_VEV7231 | VEV | Included | Inter Lab N-0442A
RDC_NB_GF_VAV7240_VEV7241A | VAV | Included | Optical Lab N-0442B
RDC_NB_GF_VAV7250_VEV7251 | VEV | Included | CONF N-0442C
RDC_NB_GF_VAV7260_VEV7261 | VEV | Included | SEM 1 Room N-0442D
RDC_NB_GF_VAV7270_VEV7271 | VEV | Included | SERV 1 N-0442E
RDC_NB_GF_VAV7280_VEV7281 | VEV | Included | Confocal 2 Room N-0442F
RDC_NB_GF_VAV7290_VEV7291 | VEV | Included | SEM 2 N-0442G
RDC_NB_GF_VAV7300 | VAV | Included | Air Lock 1 N-0442H
RDC_NB_GF_VAV7310_VEV7311 | VEV | Included | SEM 3 N-0442J
RDC_NB_GF_VAV7320_VEV7321 | VEV | Included | SEM 4 N-0442K
RDC_NB_GF_VAV7330_VEV7331 | VEV | Included | SEM 5 N-0442L
RDC_NB_GF_VAV7340_VEV7341 | VEV | Included | SERV 2 N-0442M
RDC_NB_GF_VAV7350_VEV7351 | VEV | Included | SEM Lab N-0442N
RDC_NB_GF_VAV7360_VEV7361 | VEV | Included | SEM Lab N-0442p
RDC_NB_GF_VAV7370_VEV7371 | VEV | Included | A/L 2 N-0442R
RDC_NB_GF_VAV7385 | VAV | Included | Office N-0444
RDC_NB_GF_VAV7390 | VAV | Included | Office 04 N-0445
RDC_NB_GF_VAV7395 | VAV | Included | Workstation N-0446
RDC_NB_GF_VAV7400 | VAV | Included | Office N-0447
RDC_NB_GF_VAV7405 | VAV | Included | Office N-0448
RDC_NB_GF_VAV7410 | VAV | Included | Office N-0449
RDC_NB_GF_VAV7415 | VAV | Included | Office N-0450
RDC_NB_GF_VAV7425 | VAV | Included | Office 05-8-WKS N-0452
RDC_NB_GF_VAV7430 | VAV | Included | Office N-0453
RDC_NB_GF_VAV7435 | VAV | Included | Office N-0454
RDC_NB_GF_VAV7440 | VAV | Included | Office N-0455
RDC_NB_GF_VAV7445 | VAV | Included | Office 04 N-0456
RDC_NB_GF_VAV7460 | VAV | Included | Office 05-8-WKS N-0457
RDC_NB_GF_VAV7465 | VAV | Included | Office N-0458
RDC_NB_GF_VAV7470 | VAV | Included | Office N-0459
RDC_NB_GF_VAV7475 | VAV | Included | Office N-0460
RDC_NB_GF_VAV7480 | VAV | Included | Office N-0461
RDC_NB_GF_VAV7485 | VAV | Included | Office 05-8-WKS N-0462
RDC_NB_GF_VAV7490_EV7495 | EV | Included | Confer N-0463
RDC_NB_GF_VAV7496 | VAV | Included | Office 04 N-0464
RDC_NB_GF_VAV7498 | VAV | Included | Office N-0465
RDC_NB_GF_VAV7499 | VAV | Included | Office 04 N-0466
RDC_SB_1F_VAV0506 | VAV | Included | Conf. S-1110
RDC_SB_1F_VAV0507 | VAV | Included | Computer Research Lab-4 S-1112
RDC_SB_1F_VAV0508 | VAV | Included | Conf S-1113
RDC_SB_1F_VAV0509 | VAV | Included | NCIR Office S-1115
RDC_SB_1F_VAV0510 | VAV | Included | Workstation S-1115A
RDC_SB_1F_VAV0511 | VAV | Included | NCIR Office S-1116
RDC_SB_1F_VAV0512 | VAV | Included | NCIR Office S-1117
RDC_SB_1F_VAV0513 | VAV | Included | NCIR Office S-1118
RDC_SB_1F_VAV0514 | VAV | Included | NCIR Office S-1119
RDC_SB_1F_VAV0518 | VAV | Included | Office S-1161
RDC_SB_1F_VAV0519 | VAV | Included | Office S-1162
RDC_SB_1F_VAV0520 | VAV | Included | Office S-1163
RDC_SB_1F_VAV0521 | VAV | Included | Office S-1164
RDC_SB_1F_VAV0522 | VAV | Included | Office S-1165
RDC_SB_1F_VAV0523 | VAV | Included | Office S-1166
RDC_SB_1F_VAV0526 | VAV | Included | Office S-1171
RDC_SB_1F_VAV0527 | VAV | Included | Office S-1172
RDC_SB_1F_VAV0528 | VAV | Included | Office S-1173
RDC_SB_1F_VAV0529 | VAV | Included | Corridor S-1174
RDC_SB_1F_VAV0530 | VAV | Included | Situation Room S-1175
RDC_SB_1F_VAV0531 | VAV | Included | Immersive Viz Lab S-1176
RDC_SB_1F_VAV0532 | VAV | Included | Conference Room S-1177
RDC_SB_1F_VAV0533 | VAV | Included | Telepresence S-1179
RDC_SB_1F_VAV0538 | VAV | Included | Workstation S-1151A
RDC_SB_1F_VAV1501 | VAV | Included | Workstation S-1119A
RDC_SB_1F_VAV1502 | VAV | Included | NCIR Office S-1120
RDC_SB_1F_VAV1503 | VAV | Included | NCIR Office S-1121
RDC_SB_1F_VAV1505 | VAV | Included | SC. Comp Office 2 S-1123
RDC_SB_1F_VAV1506 | VAV | Included | SC. Comp Office 3 S-1124
RDC_SB_1F_VAV1507 | VAV | Included | Workstation S-1124A
RDC_SB_1F_VAV1508 | VAV | Included | Scientific Comp. Office 1 S-1125
RDC_SB_1F_VAV1509 | VAV | Included | Scientific Comp. Office S-1126
RDC_SB_1F_VAV1510 | VAV | Included | ALT Office 2 S-1127
RDC_SB_1F_VAV1511 | VAV | Included | ALT Office 3 S-1128
RDC_SB_1F_VAV1512 | VAV | Included | Workstation S-1128A
RDC_SB_1F_VAV1513 | VAV | Included | ALT Office 1 S-1129
RDC_SB_1F_VAV1514 | VAV | Included | ALT Office S-1130
RDC_SB_1F_VAV1515 | VAV | Included | Distub. Syst Office 1 S-1131
RDC_SB_1F_VAV1516 | VAV | Included | Distub. Syst Office S-1132
RDC_SB_1F_VAV1517 | VAV | Included | Workstation S-1132A
RDC_SB_1F_VAV1518 | VAV | Included | Distub. Syst Office S-1133
RDC_SB_1F_VAV1519 | VAV | Included | Distub. Syst Office S-1134
RDC_SB_1F_VAV1520 | VAV | Included | Data Analytic Office S-1135
RDC_SB_1F_VAV1521 | VAV | Included | Data Analytic Office S-1136
RDC_SB_1F_VAV1522 | VAV | Included | Workstation S-1136A
RDC_SB_1F_VAV1523 | VAV | Included | Data Analytic Office S-1137
RDC_SB_1F_VAV1524 | VAV | Included | Data Analytic Office S-1138
RDC_SB_1F_VAV1525 | VAV | Included | Office S-1139
RDC_SB_1F_VAV1526 | VAV | Included | Office S-1140
RDC_SB_1F_VAV1527 | VAV | Included | Conference Room S-1141
RDC_SB_1F_VAV1528 | VAV | Included | Office S-1142
RDC_SB_1F_VAV1529 | VAV | Included | Office S-1144
RDC_SB_1F_VAV1530 | VAV | Included | Office S-1145
RDC_SB_1F_VAV1531 | VAV | Included | Office S-1146
RDC_SB_1F_VAV1532 | VAV | Included | Workstation S-1146A
RDC_SB_1F_VAV1533 | VAV | Included | Office S-1148
RDC_SB_1F_VAV1534 | VAV | Included | Office S-1149
RDC_SB_1F_VAV1536 | VAV | Included | Office S-1150
RDC_SB_1F_VAV1539 | VAV | Included | Video Conf. Room S-1154
RDC_SB_1F_VAV1540 | VAV | Included | Conf S-1159
RDC_SB_1F_VAV1542 | VAV | Included | Office S-1182
RDC_SB_1F_VAV1543 | VAV | Included | Workstation S-1182A
RDC_SB_1F_VAV1544 | VAV | Included | Office S-1182C
RDC_SB_1F_VAV1545 | VAV | Included | Office S-1182D
RDC_SB_1F_VAV1546 | VAV | Included | Office S-1182E
RDC_SB_1F_VAV1547 | VAV | Included | Office S-1182F
RDC_SB_1F_VAV1548 | VAV | Included | Office S-1183
RDC_SB_1F_VAV1549 | VAV | Included | Workstation S-1183A
RDC_SB_1F_VAV1550 | VAV | Included | Office S-1184
RDC_SB_1F_VAV1551 | VAV | Included | Social Comp Office S-1185
RDC_SB_1F_VAV1552 | VAV | Included | Social Comp Office S-1186
RDC_SB_1F_VAV1553 | VAV | Included | Workstation S-1186A
RDC_SB_1F_VAV1554 | VAV | Included | Social Comp Office S-1187
RDC_SB_1F_VAV1555 | VAV | Included | Social Comp Office S-1188
RDC_SB_1F_VAV1556 | VAV | Included | Cyber Sec Office S-1189
RDC_SB_1F_VAV1557 | VAV | Included | Cyber Sec Office S-1190
RDC_SB_1F_VAV1558 | VAV | Included | Workstation S-1190A
RDC_SB_1F_VAV1559 | VAV | Included | Office S-1191
RDC_SB_1F_VAV1560 | VAV | Included | Cyber Sec Office S-1192
RDC_SB_1F_VAV1561 | VAV | Included | Cyber Sec Office S-1193
RDC_SB_1F_VAV2501 | VAV | Included | Lobby S-1201
RDC_SB_1F_VAV2502 | VAV | Included | Lobby S-1202
RDC_SB_1F_VAV2503 | VAV | Included | Lobby S-1202
RDC_SB_1F_VAV2504 | VAV | Included | Lobby S-1202
RDC_SB_1F_VAV2505 | VAV | Included | Lobby S-1202
RDC_SB_1F_VAV2506 | VAV | Included | Lobby S-1202
RDC_SB_1F_VAV2508 | VAV | Included | Female Prayer S-1207
RDC_SB_1F_VAV2509 | VAV | Included | Open Plan S-1210
RDC_SB_1F_VAV2510 | VAV | Not Included | Exc. Dir. Office S-1211
RDC_SB_1F_VAV2511 | VAV | Included | Office S-1212
RDC_SB_1F_VAV2512 | VAV | Included | Office S-1213
RDC_SB_1F_VAV2513 | VAV | Included | Office S-1214
RDC_SB_1F_VAV2514 | VAV | Included | Office S-1215
RDC_SB_1F_VAV2515 | VAV | Included | Office S-1216
RDC_SB_1F_VAV2516 | VAV | Not Included | Executive Director Office S-1217
RDC_SB_1F_VAV2517 | VAV | Not Included | Executive Director Office S-1218
RDC_SB_1F_VAV2518 | VAV | Included | Office S-1219
RDC_SB_1F_VAV2519 | VAV | Included | Office S-1220
RDC_SB_1F_VAV2520 | VAV | Included | Office S-1221
RDC_SB_1F_VAV2521 | VAV | Included | Office S-1222
RDC_SB_1F_VAV2522 | VAV | Included | Office S-1223
RDC_SB_1F_VAV2523 | VAV | Included | Office S-1224
RDC_SB_1F_VAV2524 | VAV | Included | Office S-1225
RDC_SB_1F_VAV2525 | VAV | Included | Office S-1226
RDC_SB_1F_VAV2526 | VAV | Included | Open Plan S-1227
RDC_SB_1F_VAV2527 | VAV | Not Included | Director Office S-1228
RDC_SB_1F_VAV2528 | VAV | Not Included | Director Office S-1230
RDC_SB_1F_VAV2529 | VAV | Included | Office S-1231
RDC_SB_1F_VAV2530 | VAV | Included | Office S-1232
RDC_SB_1F_VAV2531 | VAV | Not Included | Director Office S-1241
RDC_SB_1F_VAV2532 | VAV | Included | Office S-1242
RDC_SB_1F_VAV2533 | VAV | Included | Cooridor S-1246
RDC_SB_1F_VAV2534 | VAV | Included | Meeting Room S-1247
RDC_SB_1F_VAV2535 | VAV | Included | Store S-1248
RDC_SB_1F_VAV2536 | VAV | Not Included | Normal Elec. S-1251
RDC_SB_1F_VAV2538 | VAV | Included | Office S-1257
RDC_SB_1F_VAV2539 | VAV | Included | Office S-1257B
RDC_SB_1F_VAV2540 | VAV | Not Included | Executive Director S-1260
RDC_SB_1F_VAV2541 | VAV | Included | Assistant S-1261
RDC_SB_1F_VAV2542 | VAV | Included | Open Plan S-1263
RDC_SB_1F_VAV2543 | VAV | Included | Office S-1264
RDC_SB_1F_VAV2544 | VAV | Included | Office S-1265
RDC_SB_1F_VAV2545 | VAV | Included | Office S-1266
RDC_SB_1F_VAV2546 | VAV | Included | Office S-1267
RDC_SB_1F_VAV2547 | VAV | Included | Office S-1268
RDC_SB_1F_VAV2548 | VAV | Included | Office S-1269
RDC_SB_1F_VAV2549 | VAV | Included | Office S-1270
RDC_SB_1F_VAV2550 | VAV | Included | Office S-1271
RDC_SB_1F_VAV2551 | VAV | Included | Meeting Room S-1272
RDC_SB_1F_VAV2552 | VAV | Included | Vestibule S-1273
RDC_SB_1F_VAV2553 | VAV | Included | Male Prayer S-1278
RDC_SB_1F_VAV3504 | VAV | Included | Open Plan S-1229
RDC_SB_1F_VAV3505 | VAV | Included | Open Plan S-1229
RDC_SB_1F_VAV3506 | VAV | Included | Office S-1233
RDC_SB_1F_VAV3507 | VAV | Included | Office S-1234
RDC_SB_1F_VAV3508 | VAV | Included | Office S-1235
RDC_SB_1F_VAV3509 | VAV | Not Included | Policy Director Office S-1237
RDC_SB_1F_VAV3510 | VAV | Not Included | Policy Executive Director Office S-1240
RDC_SB_1F_VAV3511 | VAV | Included | Corridor S-1280
RDC_SB_1F_VAV3512 | VAV | Included | Pantry S-1282
RDC_SB_1F_VAV3513 | VAV | Included | Office S-1283
RDC_SB_1F_VAV3514 | VAV | Included | Office S-1284
RDC_SB_1F_VAV3515 | VAV | Not Included | S-1285 VP R&D
RDC_SB_1F_VAV3516 | VAV | Included | Meeting Room S-1288
RDC_SB_1F_VAV3517 | VAV | Included | Dressing Room S-1290
RDC_SB_1F_VAV3518 | VAV | Included | Waiting Area S-1292
RDC_SB_1F_VAV3519 | VAV | Included | Open Plan S-1293
RDC_SB_1F_VAV3520 | VAV | Included | Office S-1294
RDC_SB_1F_VAV3521 | VAV | Included | Office S-1295
RDC_SB_1F_VAV3522 | VAV | Included | Conference Room S-1296
RDC_SB_1F_VAV3523 | VAV | Included | Office S-1299
RDC_SB_1F_VAV3524 | VAV | Not Included | Normal Elec. S-1238
RDC_SB_GF_VAV0001 | VAV | Included | Vestibule S-0101
RDC_SB_GF_VAV0002 | VAV | Included | Main Lobby S-0102
RDC_SB_GF_VAV0003 | VAV | Included | Entrance Lobby S-0102
RDC_SB_GF_VAV0007 | VAV | Included | Conference S-0109
RDC_SB_GF_VAV0008 | VAV | Included | Computer Research Lab 3 S-0110
RDC_SB_GF_VAV0009 | VAV | Included | Phone Booth S-0111
RDC_SB_GF_VAV0010 | VAV | Included | Phone Booth S-0112
RDC_SB_GF_VAV0011 | VAV | Included | Conference S-0113
RDC_SB_GF_VAV0012 | VAV | Included | Computer Research Lab 2 S-0114
RDC_SB_GF_VAV0013 | VAV | Included | Phone Booth S-0115
RDC_SB_GF_VAV0014 | VAV | Included | Phone Booth S-0116
RDC_SB_GF_VAV0016 | VAV | Included | Conference S-0118
RDC_SB_GF_VAV0017 | VAV | Included | Computer Research Lab 1 S-0119
RDC_SB_GF_VAV0018 | VAV | Included | Restaurant S-0123
RDC_SB_GF_VAV0019 | VAV | Included | Restaurant S-0123
RDC_SB_GF_VAV0025 | VAV | Included | Alt Recording Sound S-0135
RDC_SB_GF_VAV1003_VEV1002 | VEV | Included | NOC Lab S-0140A
RDC_SB_GF_VAV1004 | VAV | Included | Corridor S-0137 / S-0143
RDC_SB_GF_VAV1008 | VAV | Included | Cyber Embedded Sys. S-0146
RDC_SB_GF_VAV2002 | VAV | Included | Conference Room S-0207
RDC_SB_GF_VAV2003 | VAV | Included | Multi Purpose Hall S-0208
RDC_SB_GF_VAV2004 | VAV | Included | Multi Purpose Hall S-0208
RDC_SB_GF_VAV2005 | VAV | Included | Technical Open Plan S-0211
RDC_SB_GF_VAV2006 | VAV | Included | Meeting Room S-0212
RDC_SB_GF_VAV2007 | VAV | Included | Office S-0213
RDC_SB_GF_VAV2008 | VAV | Included | Office S-0214
RDC_SB_GF_VAV2009 | VAV | Included | Office S-0215
RDC_SB_GF_VAV2010 | VAV | Included | Office S-0216
RDC_SB_GF_VAV2011 | VAV | Included | Office S-0217
RDC_SB_GF_VAV2012 | VAV | Not Included | Director Office S-0218
RDC_SB_GF_VAV2013 | VAV | Included | Office S-0219
RDC_SB_GF_VAV2014 | VAV | Included | Office S-0220
RDC_SB_GF_VAV2015 | VAV | Not Included | Director Office S-0221
RDC_SB_GF_VAV2016 | VAV | Not Included | Director Office S-0222
RDC_SB_GF_VAV2017 | VAV | Included | Meeting Room S-0223
RDC_SB_GF_VAV2018 | VAV | Included | Print Hub S-0225
RDC_SB_GF_VAV2019 | VAV | Included | Office S-0227
RDC_SB_GF_VAV2020 | VAV | Included | Informal Meeting S-0231
RDC_SB_GF_VAV2021 | VAV | Included | Open Plan S-0228
RDC_SB_GF_VAV2022 | VAV | Not Included | Director Office S-0229
RDC_SB_GF_VAV2023 | VAV | Included | Office S-0230
RDC_SB_GF_VAV2024 | VAV | Not Included | Executive Director Office S-0232
RDC_SB_GF_VAV2025 | VAV | Not Included | Executive Director Office S-0233
RDC_SB_GF_VAV2026 | VAV | Included | Office S-0234
RDC_SB_GF_VAV2027 | VAV | Included | Office S-0235
RDC_SB_GF_VAV2028 | VAV | Included | Office S-0236
RDC_SB_GF_VAV2029 | VAV | Included | Waiting Area S-0251
RDC_SB_GF_VAV2030 | VAV | Included | Office S-0259
RDC_SB_GF_VAV2031 | VAV | Included | Office S-0260
RDC_SB_GF_VAV2032 | VAV | Included | Open Plan S-0269
RDC_SB_GF_VAV2033 | VAV | Included | Store S-0275
RDC_SB_GF_VAV2034 | VAV | Included | Meeting Room S-0274
RDC_SB_GF_VAV2035 | VAV | Included | Pantry S-0270
RDC_SB_GF_VAV2036 | VAV | Not Included | Emergency Elec. Room S-0278
RDC_SB_GF_VAV2037 | VAV | Included | Men S-0284
RDC_SB_GF_VAV2038 | VAV | Included | Informal Meeting S-0285
RDC_SB_GF_VAV2039 | VAV | Included | Meeting Room S-0286
RDC_SB_GF_VAV2040 | VAV | Included | Open Plan S-0289
RDC_SB_GF_VAV2041 | VAV | Included | Open Plan S-0289
RDC_SB_GF_VAV2042 | VAV | Included | Corridor S-0273
RDC_SB_GF_VAV2043 | VAV | Included | Women S-0281
RDC_SB_GF_VAV2044 | VAV | Included | Lobby S-0294
RDC_SB_GF_VAV2045 | VAV | Included | Lobby S-0294
RDC_SB_GF_VAV2046 | VAV | Included | Lobby S-0294
RDC_SB_GF_VAV2047 | VAV | Included | Lobby S-0294
RDC_SB_GF_VAV3001 | VAV | Not Included | Director Office S-0237
RDC_SB_GF_VAV3002 | VAV | Included | Office S-0238
RDC_SB_GF_VAV3003 | VAV | Included | Office S-0239
RDC_SB_GF_VAV3004 | VAV | Included | Office S-0240
RDC_SB_GF_VAV3005 | VAV | Included | Office S-0241
RDC_SB_GF_VAV3006 | VAV | Included | Office S-0242
RDC_SB_GF_VAV3007 | VAV | Not Included | Director Office S-0243
RDC_SB_GF_VAV3008 | VAV | Included | Open Plan S-0244
RDC_SB_GF_VAV3009 | VAV | Included | Open Plan S-0244
RDC_SB_GF_VAV3010 | VAV | Included | Open Plan S-0244
RDC_SB_GF_VAV3011 | VAV | Included | Meeting Room S-0245
RDC_SB_GF_VAV3012 | VAV | Included | Office S-0246
RDC_SB_GF_VAV3013 | VAV | Included | Office S-0247
RDC_SB_GF_VAV3014 | VAV | Included | Office S-0248
RDC_SB_GF_VAV3015 | VAV | Not Included | Security S-0249
RDC_SB_GF_VAV3016 | VAV | Included | Corridor S-0250
RDC_SB_GF_VAV3017 | VAV | Included | Office S-0251
RDC_SB_GF_VAV3018 | VAV | Included | Corridor S-0251
RDC_SB_GF_VAV3019 | VAV | Included | Corridor S-0251
RDC_SB_GF_VAV3020 | VAV | Included | Office S-0252
RDC_SB_GF_VAV3021 | VAV | Included | Office S-0252
RDC_SB_GF_VAV3022 | VAV | Included | Office S-0253
RDC_SB_GF_VAV3023 | VAV | Included | Office S-0253
RDC_SB_GF_VAV3024 | VAV | Included | Office S-0254
RDC_SB_GF_VAV3025 | VAV | Included | Office S-0255
RDC_SB_GF_VAV3026 | VAV | Included | Office S-0256
RDC_SB_GF_VAV3027 | VAV | Included | Office S-0257
RDC_SB_GF_VAV3028 | VAV | Included | Office S-0258
RDC_SB_GF_VAV3029 | VAV | Included | Open Plan S-0261
RDC_SB_GF_VAV3030 | VAV | Included | Open Plan S-0262
RDC_SB_GF_VAV3031 | VAV | Not Included | Server S-0264
RDC_SB_GF_VAV3032 | VAV | Included | Open Plan S-0265
RDC_SB_GF_VAV3033 | VAV | Not Included | Corridor / Print / Emergency Elec Rm / Normal Elec Rm S-0251 / S-0263 / S-0266 / S-0267
RDC_SB_GF_VAV3034 | VAV | Included | Vestibule S-0293
RDC_SB_GF_VAV3035 | VAV | Included | Lobby S-0294
RDC_SB_GF_VAV3036 | VAV | Included | Lobby S-0294
RDC_SB_GF_VAV3501 | VAV | Included | Lobby S-0294
RDC_SB_GF_VAV3502 | VAV | Included | Lobby S-0294
RDC_SB_GF_VAV3503 | VAV | Included | Vestibule S-0293
RDC_NB_1F_VAV4510 | VAV | Included | Corridor N-1202A
RDC_NB_1F_VAV4515_EV4516 | EV | Not Included | Emergency Electrical Room N-1203
RDC_NB_1F_VAV4520_EV4521 | EV | Not Included | Normal Electrical Room N-1204
RDC_NB_1F_VAV4525_EV4526 | EV | Included | Conference Room N-1205
RDC_NB_1F_VAV4530_EV4531 | EV | Included | Office N-1206
RDC_NB_1F_VAV4535_EV4536 | EV | Included | Office N-1207
RDC_NB_1F_VAV4540_EV4541 | EV | Included | Office N-1208
RDC_NB_1F_VAV4545_EV4546 | EV | Included | Office N-1209
RDC_NB_1F_VAV4550_EV4551 | EV | Included | Office N-1210
RDC_NB_1F_VAV4555_EV4556 | EV | Included | Confer Room N-1211
RDC_NB_1F_VAV4560_EV4561 | EV | Included | Office N-1212
RDC_NB_1F_VAV4565_EV4566 | EV | Included | Conference N-1213
RDC_NB_1F_VAV4570_EV4571 | EV | Included | Office 04 N-1214
RDC_NB_1F_VAV4575_EV4576 | EV | Included | Storage N-1215
RDC_NB_1F_VAV4580 | VAV | Included | Photovoltaic Lab N-1216A
RDC_NB_1F_VAV4600 | VAV | Included | Testing Room N-1216B
RDC_NB_1F_VAV4601 | VAV | Included | Testing Room N-1216B
RDC_NB_1F_VAV4620_VEV4621 | VEV | Included | EL Shop N-1216C
RDC_NB_1F_VAV4630_VEV4631 | VEV | Included | GIS N-1216D
RDC_NB_1F_VAV4650 | VAV | Included | Breakout N-1225
RDC_NB_1F_VAV4660 | VAV | Included | Expansion Workstation N-1227
RDC_NB_1F_VAV4665 | VAV | Included | Office N-1228
RDC_NB_1F_VAV4670 | VAV | Included | Office N-1229
RDC_NB_1F_VAV4675 | VAV | Included | Office N-1230
RDC_NB_1F_VAV4680 | VAV | Included | Office N-1231
RDC_NB_1F_VAV4685 | VAV | Included | Workstation N-1232
RDC_NB_1F_VAV4690 | VAV | Included | Office N-1233
RDC_NB_1F_VAV4695 | VAV | Included | Office N-1234
RDC_NB_1F_VAV4700 | VAV | Included | Office N-1235
RDC_NB_1F_VAV4705 | VAV | Included | Office N-1236
RDC_NB_1F_VAV4710 | VAV | Included | Workstation N-1237
RDC_NB_1F_VAV4715 | VAV | Included | Office N-1238
RDC_NB_1F_VAV4720 | VAV | Included | Office N-1239
RDC_NB_1F_VAV4725 | VAV | Included | Office N-1240
RDC_NB_1F_VAV4730 | VAV | Included | Office N-1241
RDC_NB_1F_VAV4735 | VAV | Included | Workstation N-1242
RDC_NB_1F_VAV4740 | VAV | Included | Exp Office N-1243
RDC_NB_1F_VAV4745 | VAV | Included | Office N-1244
RDC_NB_1F_VAV4900P | VAV | Not Included | Normal Electric N-2102
RDC_NB_1F_VAV4910P | VAV | Not Included | Emergency Electr N-2103
RDC_NB_1F_VAV5500 | VAV | Included | Lobby N-1101
RDC_NB_1F_VAV5501 | VAV | Included | Lobby N-1101
RDC_NB_1F_VAV5510_EV5511 | EV | Included | Conference N-1101A
RDC_NB_1F_VAV5515_EV5516 | EV | Not Included | Emergency Electrical Room N-1102
RDC_NB_1F_VAV5520_EV5521 | EV | Included | Conference N-1106
RDC_NB_1F_VAV5525_EV5526 | EV | Included | Conference N-1107
RDC_NB_1F_VAV5535_EV5536 | EV | Included | Conference N-1112
RDC_NB_1F_VAV5540_EV5541 | EV | Not Included | Normal Electrical Room N-1113
RDC_NB_1F_VAV5550_VEV5551 | VEV | Included | PCR N-1115A
RDC_NB_1F_VAV5560_VEV5561 | VEV | Included | PRE-PCR N-1115B
RDC_NB_1F_VAV5570 | VAV | Included | Met/Prot Lab N-1115C
RDC_NB_1F_VAV5571 | VAV | Included | Met/Prot Lab N-1115C
RDC_NB_1F_VAV5580_VEV5581 | VEV | Included | DNA/RNA N-1115D
RDC_NB_1F_VAV5590 | VAV | Included | Cell Culture N-1115E
RDC_NB_1F_VAV5600_VEV5601 | VEV | Included | Library N-1115H
RDC_NB_1F_VAV5610_VEV5611 | VEV | Included | Robotics N-1115J
RDC_NB_1F_VAV5620_VEV5622 | VEV | Included | Sequence Lab N-1115K
RDC_NB_1F_VAV5621_VEV5623 | VEV | Included | Sequence Lab N-1115K
RDC_NB_1F_VAV5630_VEV5631 | VEV | Included | Genom Med Lab N-1115K1
RDC_NB_1F_VAV5650 | VAV | Included | Office N-1120
RDC_NB_1F_VAV5655_EV5656 | EV | Included | Store N-1120B
RDC_NB_1F_VAV5660 | VAV | Included | Office N-1121
RDC_NB_1F_VAV5665 | VAV | Included | Office N-1122
RDC_NB_1F_VAV5670 | VAV | Included | Office N-1123
RDC_NB_1F_VAV5675 | VAV | Included | Office N-1124
RDC_NB_1F_VAV5680 | VAV | Included | Office N-1125
RDC_NB_1F_VAV5685 | VAV | Included | Corridor N-1126
RDC_NB_1F_VAV5690 | VAV | Included | Office N-1127
RDC_NB_1F_VAV5695 | VAV | Included | Office N-1128
RDC_NB_1F_VAV5700 | VAV | Included | Office N-1129
RDC_NB_1F_VAV5705 | VAV | Included | Office N-1130
RDC_NB_1F_VAV5710 | VAV | Included | Office N-1131
RDC_NB_1F_VAV5715_EV5716 | EV | Included | Conf Rm N-1132
RDC_NB_1F_VAV5730_EV5731 | EV | Included | Store N-1135
RDC_NB_1F_VAV5735_EV5736 | EV | Not Included | Normal Elec. N-1136
RDC_NB_1F_VAV5740_EV5741 | EV | Not Included | Emer. Elec. N-1137
RDC_NB_1F_VAV5745 | VAV | Included | Corridor N-1138
RDC_NB_1F_VAV5760_EV5761 | EV | Included | Conf N-1143
RDC_NB_1F_VAV5770_VEV5771 | VEV | Included | Histology N-1144A
RDC_NB_1F_VAV5780_VEV5781 | VEV | Included | Culture & Gel Rm N-1144B
RDC_NB_1F_VAV5790 | VAV | Included | Shafallah N-1144C
RDC_NB_1F_VAV5792_VEV5793 | VEV | Included | Sample Accession N-1144C1
RDC_NB_1F_VAV5794_VEV5795A | VAV | Included | Storage and Archives N-1144C2
RDC_NB_1F_VAV5800_VEV5801 | VEV | Included | Pre-PCR N-1144D
RDC_NB_1F_VAV5810 | VAV | Included | Nano Lab N-1144E
RDC_NB_1F_VAV5814 | VAV | Included | Nano Lab N-1144E
RDC_NB_1F_VAV5835_EV5836 | EV | Included | P/C/S Pantry N-1146
RDC_NB_1F_VAV5840 | VAV | Included | Corridor N-1150
RDC_NB_1F_VAV5845 | VAV | Included | Reception+N-1151B Storage N-1151
RDC_NB_1F_VAV5850 | VAV | Included | Office 04 N-1151A
RDC_NB_1F_VAV5855 | VAV | Included | Office 04 N-1152
RDC_NB_1F_VAV5860 | VAV | Included | Office N-1154
RDC_NB_1F_VAV5865 | VAV | Included | Office N-1155
RDC_NB_1F_VAV5870 | VAV | Included | Exp Office N-1156
RDC_NB_1F_VAV5875 | VAV | Included | Office N-1157
RDC_NB_1F_VAV5880 | VAV | Included | Office N-1158
RDC_NB_1F_VAV5885 | VAV | Included | Office N-1159
RDC_NB_1F_VAV5890 | VAV | Included | Workstation N-1160
RDC_NB_1F_VAV5895 | VAV | Included | Office N-1161
RDC_NB_1F_VAV5900 | VAV | Included | Office N-1162
RDC_NB_1F_VAV5905 | VAV | Included | Office N-1163
RDC_NB_1F_VAV5910 | VAV | Included | Office N-1164
RDC_NB_1F_VAV5915 | VAV | Included | Office N-1167
RDC_NB_1F_VAV5920 | VAV | Included | Workstation N-1168
RDC_NB_1F_VAV5925 | VAV | Included | Office N-1169
RDC_NB_1F_VAV5930 | VAV | Included | Office N-1170
RDC_NB_1F_VAV5930P | VAV | Not Included | Normal Elec. N-2105
RDC_NB_1F_VAV5935 | VAV | Included | Office N-1166
RDC_NB_1F_VAV5940 | VAV | Included | Workstation N-1165
RDC_NB_1F_VAV5940P | VAV | Not Included | Emer. Elec. N-2106
RDC_NB_1F_VAV6505_EV6506 | EV | Included | Conference N-1302
RDC_NB_1F_VAV6510_EV6511 | EV | Included | Conference N-1303
RDC_NB_1F_VAV6525_EV6526 | EV | Not Included | Normal Electrical Room N-1310
RDC_NB_1F_VAV6530_VEV6531 | VEV | Included | AAV N-1316A
RDC_NB_1F_VAV6540 | VAV | Included | Tissure Culture 1 N-1316B
RDC_NB_1F_VAV6550 | VAV | Included | Gene Therapy Lab N-1316C
RDC_NB_1F_VAV6551 | VAV | Included | Gene Therapy Lab N-1316C
RDC_NB_1F_VAV6560_VEV6561 | VEV | Included | TC2 N-1316D
RDC_NB_1F_VAV6570_VEV6571 | VEV | Included | STORE ROOM N-1316E
RDC_NB_1F_VAV6590_VEV6591 | VEV | Included | LENTIV N-1316G
RDC_NB_1F_VAV6600_VEV6601 | VEV | Included | Analytical Core N-1316H
RDC_NB_1F_VAV6610_VEV6611 | VEV | Included | Microscope Room N-1316H
RDC_NB_1F_VAV6620_VEV6621 | VEV | Included | Mscopy1 N-1316K
RDC_NB_1F_VAV6630A | VAV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_VAV6630B | VAV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_VAV6631A | VAV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_VAV6631B | VAV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_VAV6650 | VAV | Included | Office N-1319
RDC_NB_1F_VAV6655 | VAV | Included | Office N-1320
RDC_NB_1F_VAV6660 | VAV | Included | Workstation N-1321
RDC_NB_1F_VAV6665 | VAV | Included | Office N-1322
RDC_NB_1F_VAV6670 | VAV | Included | Office N-1323
RDC_NB_1F_VAV6675 | VAV | Included | Workstation N-1324
RDC_NB_1F_VAV6680 | VAV | Included | Office N-1325
RDC_NB_1F_VAV6685 | VAV | Included | Office N-1326
RDC_NB_1F_VAV6690 | VAV | Included | Exp. Workstation N-1327
RDC_NB_1F_VAV6695 | VAV | Included | Office N-1328
RDC_NB_1F_VAV6700_EV6701 | EV | Not Included | NORMAL ELEC. N-1329
RDC_NB_1F_VAV6705 | VAV | Included | Office N-1330
RDC_NB_1F_VAV6710 | VAV | Included | Office N-1331
RDC_NB_1F_VAV6715 | VAV | Included | Office N-1332
RDC_NB_1F_VAV6720 | VAV | Included | Corridor N-1335
RDC_NB_1F_VAV6725_EV6726 | EV | Not Included | Emer. Elec. N-1336
RDC_NB_1F_VAV6750 | VAV | Included | Tissue Culture 1 N-1345A
RDC_NB_1F_VAV6760 | VAV | Included | Diabetes Lab N-1345B
RDC_NB_1F_VAV6761 | VAV | Included | Diabetes Lab N-1345B
RDC_NB_1F_VAV6800_VEV6801 | VEV | Included | Tissue Culture 3 N-1345D
RDC_NB_1F_VAV6810_VEV6811 | VEV | Included | Calc Imaging N-1345E
RDC_NB_1F_VAV6820_VEV6821 | VEV | Included | Electro Physics N-1345F
RDC_NB_1F_VAV6830_VEV6831 | VEV | Included | Shared Cold Lab N-1345G
RDC_NB_1F_VAV6840_VEV6841 | VEV | Included | Bacterlgy Lab N-1345H
RDC_NB_1F_VAV6850 | VAV | Included | Bio-Med Chem Lab 2 N-1345J
RDC_NB_1F_VAV6851 | VAV | Included | Bio-Med Chem Lab 2 N-1345J
RDC_NB_1F_VAV6870_EV6871 | EV | Not Included | Emergency Electrical Room N-1353
RDC_NB_1F_VAV6880 | VAV | Included | Reception+N-1355C Storage N-1355
RDC_NB_1F_VAV6885 | VAV | Included | Office 04 N-1355A
RDC_NB_1F_VAV6890_EV6891 | EV | Included | Conference Room N-1355B
RDC_NB_1F_VAV6895 | VAV | Included | Office 04 N-1356
RDC_NB_1F_VAV6900 | VAV | Included | Office N-1357
RDC_NB_1F_VAV6905 | VAV | Included | Open Plan N-1358
RDC_NB_1F_VAV6910 | VAV | Included | Office N-1359
RDC_NB_1F_VAV6915 | VAV | Included | Office N-1360
RDC_NB_1F_VAV6920 | VAV | Included | Office N-1360B
RDC_NB_1F_VAV6925 | VAV | Included | Office N-1361
RDC_NB_1F_VAV6930 | VAV | Included | Office N-1362
RDC_NB_1F_VAV6935 | VAV | Included | Workstation N-1363
RDC_NB_1F_VAV6940 | VAV | Included | Office N-1364
RDC_NB_1F_VAV6945 | VAV | Included | Office N-1365
RDC_NB_1F_VAV6950 | VAV | Included | Office N-1366
RDC_NB_1F_VAV6955 | VAV | Included | Office N-1367
RDC_NB_1F_VAV6960 | VAV | Included | Workstation N-1368
RDC_NB_1F_VAV6965 | VAV | Included | Office N-1369
RDC_NB_1F_VAV6967 | VAV | Included | Office N-1370
RDC_NB_1F_VAV6968 | VAV | Included | Workstation N-1371
RDC_NB_1F_VAV6970_EV6971 | EV | Included | PANTRY N-1372
RDC_NB_1F_VAV6972 | VAV | Included | Office N-1374
RDC_NB_1F_VAV6974 | VAV | Included | Office N-1375
RDC_NB_1F_VAV6976 | VAV | Included | Office N-1376
RDC_NB_1F_VAV6978 | VAV | Included | Office N-1377
RDC_NB_1F_VAV6979P | VAV | Not Included | Normal Elec. N-2107
RDC_NB_1F_VAV6980P | VAV | Not Included | Emer. Elec. N-2108
RDC_NB_1F_VAV7510_VEV7511 | VEV | Included | TC1 N-1404A
RDC_NB_1F_VAV7530_VEV7532 | VEV | Included | Cell Bio N-1404C
RDC_NB_1F_VAV7531_VEV7533 | VEV | Included | Cell Bio N-1404C
RDC_NB_1F_VAV7540_VEV7541 | VEV | Included | Shared Eq Rm N-1404D
RDC_NB_1F_VAV7550_VEV7551 | VEV | Included | TC2 N-1404E
RDC_NB_1F_VAV7560_VEV7561 | VEV | Included | Imaging N-1404F
RDC_NB_1F_VAV7570_VEV7571 | VEV | Included | Cell Bio Lab2 N-1404G
RDC_NB_1F_VAV7580_VEV7581 | VEV | Included | TC3 N-1404H
RDC_NB_1F_VAV7600_VEV7601 | VEV | Included | Cell Bio Lab3 N-1404K
RDC_NB_1F_VAV7620 | VAV | Included | Office N-1415
RDC_NB_1F_VAV7625 | VAV | Included | Office N-1416
RDC_NB_1F_VAV7630 | VAV | Included | Office 05 - 2 WKS- N-1407
RDC_NB_1F_VAV7635 | VAV | Included | Office N-1418
RDC_NB_1F_VAV7640 | VAV | Included | Office N-1419
RDC_NB_1F_VAV7645 | VAV | Included | Exp. Workstation N-1420
RDC_NB_1F_VAV7650 | VAV | Included | Office N-1421
RDC_NB_1F_VAV7655 | VAV | Included | Office N-1422
RDC_NB_1F_VAV7660 | VAV | Included | Office 05 - 2 WKS- N-1401
RDC_NB_1F_VAV7665_EV7666 | EV | Not Included | Normal Elec. N-1425
RDC_NB_1F_VAV7670 | VAV | Included | Office N-1426
RDC_NB_1F_VAV7675 | VAV | Included | Office N-1428
RDC_NB_1F_VAV7680_EV7681 | EV | Included | Conf N-1429
RDC_NB_1F_VAV7685 | VAV | Included | Office N-1433
RDC_NB_1F_VAV7690 | VAV | Included | Office N-1435
RDC_NB_1F_VAV7695 | VAV | Included | Office N-1437
RDC_NB_1F_VAV7700_EV7701 | EV | Not Included | Emer. Elec. N-1438
RDC_NB_1F_VAV7705 | VAV | Included | Office 05 - 24 WKS + N-1441 Room N-1442
RDC_NB_1F_VAV7710 | VAV | Included | Workstation N-1442
RDC_NB_1F_VAV7730_VEV7731 | VEV | Included | Microscope 2 N-1450A
RDC_NB_1F_VAV7740_VEV7741 | VEV | Included | LN2 Stor N-1450B
RDC_NB_1F_VAV7750_VEV7751 | VEV | Included | Flow Cyto N-1450C
RDC_NB_1F_VAV7770_VEV7771 | VEV | Included | Qurnt N-1450E
RDC_NB_1F_VAV7780_VEV7781 | VEV | Included | iPS-TC N-1450F
RDC_NB_1F_VAV7800_VEV7801 | VEV | Included | IPS TISSUE CULTURE N-1450J
RDC_NB_1F_VAV7810_VEV7811 | VEV | Included | TC1 N-1450L
RDC_NB_1F_VAV7820_VEV7822 | VEV | Included | STEM/PCR Open Lab N-1450M
RDC_NB_1F_VAV7821_VEV7823 | VEV | Included | STEM/PCR Open Lab N-1450M
RDC_NB_1F_VAV7830_VEV7831 | VEV | Included | TC2 N-1450N
RDC_NB_1F_VAV7840_EV7841 | EV | Included | Conf N-1458
RDC_NB_1F_VAV7845_EV7846 | EV | Included | Conf N-1459
RDC_NB_1F_VAV7850 | VAV | Included | Office N-1459A
RDC_NB_1F_VAV7860 | VAV | Included | Exp. Workstation N-1461
RDC_NB_1F_VAV7865 | VAV | Included | Workstation N-1461A
RDC_NB_1F_VAV7870 | VAV | Included | Office N-1462
RDC_NB_1F_VAV7875 | VAV | Included | Office N-1463
RDC_NB_1F_VAV7880 | VAV | Included | Office N-1464
RDC_NB_1F_VAV7885 | VAV | Included | Office N-1465
RDC_NB_1F_VAV7890 | VAV | Included | Workstation N-1466
RDC_NB_1F_VAV7895 | VAV | Included | Office N-1467
RDC_NB_1F_VAV7900 | VAV | Included | Office N-1468
RDC_NB_1F_VAV7905 | VAV | Included | Office N-1469
RDC_NB_1F_VAV7910 | VAV | Included | Office N-1470
RDC_NB_1F_VAV7915 | VAV | Included | Workstation N-1471
RDC_NB_1F_VAV7920 | VAV | Included | Office N-1472
RDC_NB_1F_VAV7925 | VAV | Included | Office N-1473
RDC_NB_1F_VAV7930 | VAV | Included | Office N-1474
RDC_NB_1F_VAV7935 | VAV | Included | Office N-1475
RDC_NB_1F_VAV7940 | VAV | Included | Workstation N-1476
RDC_NB_1F_VAV7945 | VAV | Included | Office N-1477
RDC_NB_1F_VAV7950 | VAV | Included | Office N-1478
RDC_NB_1F_VAV7955 | VAV | Included | Office N-1479
RDC_NB_1F_VAV7960 | VAV | Included | Office N-1480
RDC_NB_1F_VAV7975P | VAV | Not Included | Normal Elec. N-2111
RDC_NB_1F_VAV7980P | VAV | Not Included | Emer. Elec. N-2112
RDC_NB_1F_FCU4910 | FCU | Included | Stair 1 N-1ST01
RDC_NB_1F_FCU4914 | FCU | Not Included | Mech/ FPC N- L1 A2.1
RDC_NB_1F_FCU4915 | FCU | Not Included | MDF N-1201
RDC_NB_1F_FCU4916 | FCU | Included | Stair 1 N-1ST01
RDC_NB_1F_FCU4917 | FCU | Included | Stair N-1ST02
RDC_NB_1F_FCU5983 | FCU | Not Included | IDF N-1140
RDC_NB_1F_FCU5984 | FCU | Included | ROBOTICS N-115J
RDC_NB_1F_FCU5985 | FCU | Included | Corridor N-1142
RDC_NB_1F_FCU5986 | FCU | Included | Corridor N-1142
RDC_NB_1F_FCU5987 | FCU | Included | Stair 3 N-L1 A2.3
RDC_NB_1F_FCU5993 | FCU | Included | Conference Room N-L0 A2.2
RDC_NB_1F_FCU5994 | FCU | Included | Conference Room N-L0 A2.2
RDC_NB_1F_FCU6988 | FCU | Included | Service Corridor N-1337
RDC_NB_1F_FCU6989 | FCU | Included | Service Corridor N-1337
RDC_NB_1F_FCU6990 | FCU | Not Included | Mech/ FPC N-L1 A2.3
RDC_NB_1F_FCU6991 | FCU | Not Included | Mech/ FPC N-L1 A2.3
RDC_NB_1F_FCU6992 | FCU | Included | Stair 4 N-L1 A2.3
RDC_NB_1F_FCU7790 | FCU | Included | Stair 6 N-1ST06
RDC_NB_1F_FCU7984 | FCU | Included | Stair 6 N-1ST06
RDC_NB_1F_FCU7985 | FCU | Not Included | IDF N-1424
RDC_NB_1F_FCU7986 | FCU | Not Included | IDF N-1424
RDC_NB_1F_FCU7987 | FCU | Included | Service Corridor N-1446
RDC_NB_1F_FCU7988 | FCU | Included | Service Corridor N-1446
RDC_NB_1F_FCU7989 | FCU | Included | Stair 5 N-1ST05
RDC_NB_2F_FCU4918 | FCU | Not Included | IDF N-2104
RDC_NB_2F_FCU4919 | FCU | Not Included | IDF N-2104
RDC_NB_2F_FCU5988 | FCU | Not Included | Mechanical (AHU 8512)
RDC_NB_2F_FCU5989 | FCU | Included | Stair 2 N-2ST02
RDC_NB_2F_FCU5990 | FCU | Not Included | Mechanical (AHU 8512/8514)
RDC_NB_2F_FCU6993 | FCU | Not Included | Mechanical (AHU 8516)
RDC_NB_2F_FCU6994 | FCU | Not Included | Normal Elec. N-2105
RDC_NB_2F_FCU6995 | FCU | Not Included | IDF N-2110
RDC_NB_2F_FCU6996 | FCU | Not Included | IDF N-2110
RDC_NB_2F_FCU7991 | FCU | Not Included | Normal Elec. N-2111
RDC_NB_2F_FCU7992 | FCU | Not Included | Emer. Elec. N-2112
RDC_NB_GF_FCU4911 | FCU | Not Included | MDF Room N-0206A
RDC_NB_GF_FCU4912 | FCU | Not Included | MDF Room N-0206A
RDC_NB_GF_FCU4913 | FCU | Included | Store N-0201
RDC_NB_GF_FCU4920 | FCU | Not Included | Emergency Electrical Landing Room N-0205
RDC_NB_GF_FCU5980 | FCU | Included | Serv Core N-0136
RDC_NB_GF_FCU5981 | FCU | Included | Serv Core N-0136
RDC_NB_GF_FCU5982 | FCU | Included | Stair 3 N-OST03
RDC_NB_GF_FCU5991 | FCU | Included | Vestibule N-0103
RDC_NB_GF_FCU5992 | FCU | Included | Vestibule N-0102
RDC_NB_GF_FCU6981 | FCU | Not Included | IDF N-0133
RDC_NB_GF_FCU6982 | FCU | Not Included | Mech/FPC N-0128
RDC_NB_GF_FCU6983 | FCU | Included | Service Corridor N-0344
RDC_NB_GF_FCU6984 | FCU | Included | Service Corridor N-0344
RDC_NB_GF_FCU6985 | FCU | Not Included | IDF N-0311
RDC_NB_GF_FCU6986 | FCU | Not Included | IDF N-0311
RDC_NB_GF_FCU6987 | FCU | Included | Stair 4 N-0ST04
RDC_NB_GF_FCU7981 | FCU | Included | SURF ANALYSIS LAB N-0404F
RDC_NB_GF_FCU7982 | FCU | Included | SURF ANALYSIS LAB N-0404F
RDC_NB_GF_FCU7983 | FCU | Included | Stair 5 N-0ST05
RDC_NB_SB_Walkway_FCU9001 | FCU | Included | Pedestrian Walkway between North & South Buildings
RDC_NB_SB_Walkway_FCU9002 | FCU | Included | Pedestrian Walkway between North & South Buildings
RDC_NB_SB_Walkway_FCU9003 | FCU | Included | Pedestrian Walkway between North & South Buildings
RDC_NB_SB_Walkway_FCU9004 | FCU | Included | Pedestrian Walkway between North & South Buildings
RDC_NB_SB_Walkway_FCU9005 | FCU | Included | Pedestrian Walkway between North & South Buildings
RDC_SB_1F_FCU0501 | FCU | Included | STAIR-04 1ST04 |  |  | 21.9 | NA
RDC_SB_1F_FCU0502 | FCU | Not Included | UPS ROOM S-1107D |  |  | NA | 22
RDC_SB_1F_FCU0503 | FCU | Not Included | UPS ROOM S-1107D |  |  | 20.9 | 22
RDC_SB_1F_FCU1501 | FCU | Not Included | IDF ROOM S-1156 |  |  | 20.9 | 22
RDC_SB_1F_FCU1502 | FCU | Not Included | IDF ROOM S-1156 |  |  | 20.9 | 22
RDC_SB_1F_FCU1503 | FCU | Included | STAIR-01 1ST01 |  |  | 21.9 | NA
RDC_SB_1F_FCU2501 | FCU | Included | STAIR-03 1ST03 |  |  | 21.9 | NA
RDC_SB_1F_FCU2502 | FCU | Not Included | IDF ROOM S-1244 |  |  | 20.9 | 22
RDC_SB_1F_FCU2503 | FCU | Not Included | IDF ROOM S-1244 |  |  | 20.9 | 22
RDC_SB_1F_FCU2504 | FCU | Not Included | UPS ROOM S-1276 |  |  | 20.9 | 22
RDC_SB_1F_FCU2505 | FCU | Not Included | UPS ROOM S-1276 |  |  | 20.9 | 22
RDC_SB_1F_FCU3501 | FCU | Included | STAIR-04 1ST04 |  |  | 21.9 | NA
RDC_SB_2F_FCU0201 | FCU | Not Included | South Penthouse S-2101
RDC_SB_2F_FCU0202 | FCU | Not Included | South Penthouse S-2101
RDC_SB_2F_FCU0203 | FCU | Not Included | South Penthouse S-2101
RDC_SB_2F_FCU0204 | FCU | Not Included | South Penthouse S-2101
RDC_SB_2F_FCU0205 | FCU | Not Included | Normal Elec. S-2103
RDC_SB_2F_FCU0206 | FCU | Not Included | Normal Elec. S-2103
RDC_SB_2F_FCU0207 | FCU | Not Included | Emerg. Elec. S-2104
RDC_SB_2F_FCU0208 | FCU | Not Included | Emerg. Elec. S-2104
RDC_SB_2F_FCU1201 | FCU | Not Included | IDF S-2102
RDC_SB_2F_FCU1202 | FCU | Not Included | IDF S-2102
RDC_SB_2F_FCU2201 | FCU | Not Included | South Penthouse S-2101
RDC_SB_2F_FCU2202 | FCU | Not Included | South Penthouse S-2101
RDC_SB_2F_FCU2203 | FCU | Not Included | South Penthouse S-2101
RDC_SB_2F_FCU2204 | FCU | Not Included | Emerg. Elec. S-2105
RDC_SB_2F_FCU2205 | FCU | Not Included | Emerg. Elec. S-2105
RDC_SB_2F_FCU2206 | FCU | Not Included | Normal Elec. S-2106
RDC_SB_2F_FCU2207 | FCU | Not Included | Normal Elec. S-2106
RDC_SB_2F_FCU2208 | FCU | Not Included | IDF S-2107
RDC_SB_2F_FCU2209 | FCU | Not Included | IDF S-2107
RDC_SB_2F_FCU2210 | FCU | Not Included | South Penthouse S-2101
RDC_SB_GF_FCU0001 | FCU | Included | STAIR-02 S-02T02 |  |  | 21.9 | NA
RDC_SB_GF_FCU1001 | FCU | Not Included | QTEL ROOM S-0132 |  |  | 21.9 | 20.8
RDC_SB_GF_FCU1002 | FCU | Not Included | QTEL ROOM S-0132 |  |  | 20.9 | 20.8
RDC_SB_GF_FCU1003 | FCU | Not Included | IDF ROOM S-0133 |  |  | 20.9 | 22
RDC_SB_GF_FCU1004 | FCU | Not Included | IDF ROOM S-0133 |  |  | 20.9 | 22
RDC_SB_GF_FCU1005 | FCU | Not Included | EC MDF ROOM S-0134 |  |  | 23.4 | NA
RDC_SB_GF_FCU1006 | FCU | Not Included | EC MDF ROOM S-0134 |  |  | 23.4 | NA
RDC_SB_GF_FCU1007 | FCU | Not Included | MECHANICAL ROOM S-0136 |  |  | NA | NA
RDC_SB_GF_FCU1008 | FCU | Included | STAIR-01 S-01T01 |  |  | 21.9 | NA
RDC_SB_GF_FCU2001 | FCU | Included | STAIR-03 S-0ST03 |  |  | 21.9 | NA
RDC_SB_GF_FCU2002 | FCU | Not Included | AV ROOM S-0210 |  |  | NA | NA
RDC_SB_GF_FCU2003 | FCU | Not Included | AV ROOM S-0210 |  |  | NA | NA
RDC_SB_GF_FCU2004 | FCU | Not Included | IDF ROOM S-0271 |  |  | NA | 22
RDC_SB_GF_FCU2005 | FCU | Not Included | IDF ROOM S-0271 |  |  | 20.9 | 22
RDC_SB_GF_FCU3001 | FCU | Included | STAIR-04 S-0ST04 |  |  | 25 | NA
RDC_UB_GF_FCU8001 | FCU | Not Included | GENERAL STORAGE ROOM U-0129 |  |  | 22.5 | 22
RDC_UB_GF_FCU8002 | FCU | Included | SHOP U-0135 |  |  | NA | NA
RDC_UB_GF_FCU8003 | FCU | Included | MAIL ROOM U-0128
RDC_UB_GF_FCU8004 | FCU | Not Included | GENERAL STORAGE U-0108 |  |  | 21.9 | 22
RDC_UB_GF_FCU8005 | FCU | Not Included | RECYCLING ROOM U-0109 |  |  | 21.9 | 22.9
RDC_UB_GF_FCU8006 | FCU | Not Included | CYLINDER STORAGE U-0105 |  |  | NA | 22
RDC_UB_GF_FCU8007 | FCU | Not Included | LN2 DISPENSER U-0104 |  |  | NA | 22
RDC_UB_GF_FCU8008 | FCU | Not Included | FLAMMABLE STORAGE U-0103 |  |  | NA | 22
RDC_UB_GF_FCU8009 | FCU | Not Included | FLAMMABLE WASTE STORAGE U-0102 |  |  | NA | NA
RDC_UB_GF_FCU8010 | FCU | Not Included | BMS ROOM U-0117 |  |  | 21.9 | 22.9
RDC_UB_GF_FCU8011 | FCU | Included | BREAK ROOM U-0118 |  |  | 21.9 | 22.9
RDC_UB_GF_FCU8012 | FCU | Included | OFFICE SPACE U-0119 |  |  | 22.9 | NA
RDC_UB_GF_FCU8013 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  |  | 20.9 | 25
RDC_UB_GF_FCU8014 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  |  | 20.9 | 25
RDC_UB_GF_FCU8502 | FCU | Included | SHIPPING AND RECEIVING L0 |  |  | NA | 22
RDC_UB_GF_FCU8503 | FCU | Included | SHIPPING AND RECEIVING L0 |  |  | 20.9 | 22
RDC_UB_GF_FCU8504 | FCU | Included | SHIPPING AND RECEIVING L0 |  |  | 20.9 | 22
RDC_UB_GF_FCU8505 | FCU | Included | SHIPPING AND RECEIVING L0 |  |  | NA | 22
RDC_UB_GF_FCU8512 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  |  | 21.9 | 25
RDC_UB_GF_FCU8513 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  |  | 21.9 | 25
RDC_UB_GF_FCU8514 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  |  | 21.9 | 25
RDC_UB_GF_FCU8515 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  |  | 21.9 | 25
RDC_UB_MF_FCU8501 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  | NA | 22
RDC_UB_MF_FCU8506 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  | NA | NA
RDC_UB_MF_FCU8507 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  | NA | NA
RDC_UB_MF_FCU8508 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  | NA | 22
RDC_UB_MF_FCU8509 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  | NA | NA
RDC_UB_MF_FCU8510 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  | NA | NA
RDC_UB_MF_FCU8511 | FCU | Not Included | MECHANICAL ROOM U-1101 |  |  | NA | 22
RDC_SB_L0_AT-1001 | AT | Included | Corridor S-0137
RDC_SB_L0_AT-1002 | AT | Included | Computer Lab S-0139
RDC_SB_L0_EV-1001 | EV | Included | Computer Lab S-0139
RDC_SB_L0_AT-1003 | AT | Not Included | NOC S-0140A
RDC_SB_L0_EV-1002 | EV | Not Included | NOC S-0140A
RDC_SB_L0_AT-1004 | AT | Not Included | Dedicated Cyber SOC/NOC Lab S-0141
RDC_SB_L0_AT-1005 | AT | Not Included | Normal & Emergency Elec. Landing S-0142
RDC_SB_L0_AT-1006 | AT | Included | Corridor S-0137
RDC_SB_L0_AT-1007 | AT | Not Included | UPS S-0145
RDC_SB_L0_EV-1003 | EV | Not Included | UPS S-0145
RDC_SB_L0_AT-1008 | AT | Not Included | Cyber/Embedded/Dist System Electrical Lab S-0146
RDC_SB_L0_AT-1009 | AT | Included | Service Dock S-0151
RDC_NB_GF_AT-4005 | AT | Not Included | Electrical N-0202
RDC_NB_GF_AT-4035 | AT | Included | Corridor N-0207A
RDC_NB_GF_AT-4100 | AT | Not Included | Emergency Elec. Room N-0225
RDC_NB_GF_AT-4105 | AT | Not Included | Normal Electrical Room N-0225
RDC_NB_GF_AT-4110 | AT | Included | Conference Room N-0227
RDC_NB_GF_AT-4115 | AT | Included | Office N-0228
RDC_NB_GF_AT-4120 | AT | Included | Office N-0229
RDC_NB_GF_AT-4125 | AT | Included | Office N-0230
RDC_NB_GF_AT-4130 | AT | Included | Office N-0231
RDC_NB_GF_AT-4135 | AT | Included | Office N-0232
RDC_NB_GF_AT-4140 | AT | Included | Conference Room N-0233
RDC_NB_GF_AT-4145 | AT | Included | Office N-0234
RDC_NB_GF_AT-4165 | AT | Included | Office N-0236
RDC_NB_GF_AT-4170 | AT | Included | Storage Room N-0237
RDC_NB_GF_AT-4225 | AT | Included | Office N-0247
RDC_NB_GF_AT-4230 | AT | Included | Office N-0248
RDC_NB_GF_AT-4235 | AT | Included | Workstation N-0250
RDC_NB_GF_AT-4240 | AT | Included | Office N-0251
RDC_NB_GF_AT-4245 | AT | Included | Office N-0252
RDC_NB_GF_AT-4250 | AT | Included | Office N-0253
RDC_NB_GF_AT-4255 | AT | Included | Office N-0254
RDC_NB_GF_AT-4260 | AT | Included | Workstation N-0255
RDC_NB_GF_AT-4265 | AT | Included | Office N-0256
RDC_NB_GF_AT-4270 | AT | Included | Office N-0257
RDC_NB_GF_AT-4275 | AT | Included | Office N-0258
RDC_NB_GF_AT-4280 | AT | Included | Office N-0259
RDC_NB_GF_AT-4285 | AT | Included | Workstation N-0260
RDC_NB_GF_AT-4290 | AT | Included | Office N-0261
RDC_NB_GF_AT-4295 | AT | Included | Office N-0262
RDC_NB_GF_AT-4300 | AT | Included | Office N-0263
RDC_NB_GF_AT-4305 | AT | Included | Office N-0264
RDC_NB_GF_AT-4310 | AT | Included | Workstation N-0265
RDC_NB_GF_CEV-4031 | CEV | Included | Service Corridor N-0207
RDC_NB_GF_EV-4028 | EV | Not Included | MDF ROOM N-0206A
RDC_NB_GF_EV-4236 | EV | Included | Office 05 -8WS- N-0250
RDC_NB_GF_EV-4261 | EV | Included | Office 05 -8WS- N-0255
RDC_NB_GF_EV-4286 | EV | Included | Office 05 -8WS- N-0260
RDC_NB_GF_EV-4311 | EV | Included | WORKSTATION N-0265
RDC_NB_GF_VEV-4041 | VEV | Included | Air Quality High Bay N-0215A
RDC_NB_GF_FEV-4193 | FEV | Included | CSP Lab N-0240B
RDC_NB_GF_FEV-4194 | FEV | Included | CSP Lab N-0240B
RDC_NB_GF_VEV-4213A | VEV | Included | Desal Lab N-0240D
RDC_NB_GF_VEV-4213B | VEV | Included | Desal Lab N-0240D
RDC_NB_GF_FEV-4214 | FEV | Included | Desal Lab N-0240D
RDC_NB_GF_FEV-4215 | FEV | Included | Desal Lab N-0240D
RDC_NB_GF_FEV-4216 | FEV | Included | Desal Lab N-0240D
RDC_SB_L0_AT-0003 | AT | Included | Entrance Lobby S-0102
RDC_SB_L0_AT-0006 | AT | Not Included | Normal Elec. S-0107
RDC_SB_L0_AT-0007 | AT | Included | Conf S-0109
RDC_SB_L0_AT-0008 | AT | Included | Computer Research Lab 3 S-0110
RDC_SB_L0_AT-0009 | AT | Included | Phone Booth S-0111
RDC_SB_L0_AT-0010 | AT | Included | Phone Booth S-0112
RDC_SB_L0_AT-0011 | AT | Included | Conference Room S-0113
RDC_SB_L0_AT-0012 | AT | Included | Computer Research Lab 2 S-0114
RDC_SB_L0_AT-0013 | AT | Included | Phone Booth S-0115
RDC_SB_L0_AT-0014 | AT | Included | Phone Booth S-0116
RDC_SB_L0_AT-0015 | AT | Included | Corridor S-0117
RDC_SB_L0_AT-0016 | AT | Included | Conf S-0118
RDC_SB_L0_AT-0017 | AT | Included | Computer Research Lab 1 S-0119
RDC_SB_L0_AT-0018 | AT | Included | Restaurant S-0123
RDC_SB_L0_AT-0019 | AT | Included | Restaurant S-0123
RDC_SB_L0_AT-0020 | AT | Included | Storage S-0120B
RDC_SB_L0_AT-0021 | AT | Included | Vestibule S-0125
RDC_SB_L0_AT-0022 | AT | Included | Men S-0126
RDC_SB_L0_AT-0023 | AT | Included | Women S-0127
RDC_SB_L0_AT-0024 | AT | Not Included | NORM. ELEC. S-0129
RDC_SB_L0_AT-0025 | AT | Included | Alt Recording/Sound S-0135
RDC_NB_GF_AT-4001 | AT | Included | Store N-0201
RDC_NB_GF_AT-4312 | AT | Included | Breakout N-0265B
RDC_NB_GF_AT-4315 | AT | Included | Vestibule N-0270A
RDC_NB_GF_AT-5025 | AT | Included | Corridor N-0110
RDC_NB_GF_AT-5100 | AT | Included | Office N-0115
RDC_NB_GF_AT-5105 | AT | Included | Office N-0116
RDC_NB_GF_AT-5110 | AT | Included | Office N-0117
RDC_NB_GF_AT-5115 | AT | Included | Office N-0118
RDC_NB_GF_AT-5120 | AT | Included | Office N-0119
RDC_NB_GF_AT-5125 | AT | Included | Office N-0120
RDC_NB_GF_AT-5130 | AT | Included | Office N-0121
RDC_NB_GF_AT-5135 | AT | Included | Office N-0122
RDC_NB_GF_AT-5140 | AT | Included | Office N-0123
RDC_NB_GF_AT-5145 | AT | Included | Office N-0124
RDC_NB_GF_AT-5150 | AT | Included | Office N-0125
RDC_NB_GF_AT-5152 | AT | Included | Office N-0126
RDC_NB_GF_AT-5155 | AT | Included | Office N-0127
RDC_NB_GF_AT-5156 | AT | Included | Office 04 N-0129
RDC_NB_GF_AT-5160 | AT | Included | MENS ROOM N-0130
RDC_NB_GF_AT-5165 | AT | Included | Corridor N-0134
RDC_NB_GF_AT-5280 | AT | Included | Store N-0146
RDC_NB_GF_AT-5290 | AT | Included | Pantry N-0148
RDC_NB_GF_AT-5295 | AT | Included | Conference Room N-0149
RDC_NB_GF_AT-5300 | AT | Included | Corridor N-0150
RDC_NB_GF_AT-5305 | AT | Included | Office N-0151
RDC_NB_GF_AT-5310 | AT | Included | Office N-0152
RDC_NB_GF_AT-5315 | AT | Included | Open Office N-0153
RDC_NB_GF_AT-5320 | AT | Included | Office N-0154
RDC_NB_GF_AT-5325 | AT | Included | Office N-0155
RDC_NB_GF_AT-5330 | AT | Included | Office N-0156
RDC_NB_GF_AT-5335 | AT | Included | Office N-0157
RDC_NB_GF_AT-5340 | AT | Included | Office N-0158
RDC_NB_GF_AT-5345 | AT | Included | Office N-0159
RDC_NB_GF_AT-5350 | AT | Included | Open Office N-0160
RDC_NB_GF_AT-5355 | AT | Included | Office N-0161
RDC_NB_GF_AT-5360 | AT | Included | Office N-0162
RDC_NB_GF_AT-5365 | AT | Included | Office N-0163
RDC_NB_GF_AT-5370 | AT | Included | Office N-0164
RDC_NB_GF_AT-5375 | AT | Included | Open Office N-0165
RDC_NB_GF_AT-5380 | AT | Included | Office N-0166
RDC_NB_GF_AT-5385 | AT | Included | Office N-0167A
RDC_NB_GF_AT-5390 | AT | Included | Office 04 N-0168
RDC_NB_GF_AT-5415 | AT | Included | Office 04 N-0174
RDC_NB_GF_EV-4316 | EV | Included | Vestibule N-0270A
RDC_NB_GF_EV-5026 | EV | Included | Corridor N-0110
RDC_NB_GF_EV-5161 | EV | Included | Womens+N-0130A+N-0132 JC N-0130
RDC_NB_GF_EV-5163 | EV | Not Included | IDF N-0133
RDC_NB_GF_EV-5291 | EV | Included | Pantry N-0148
RDC_NB_GF_VEV-5052A | VEV | Included | Analytical Core Lab 1 N-0114A
RDC_NB_GF_VEV-5052B | VEV | Included | Analytical Core Lab 1 N-0114A
RDC_NB_GF_FEV-5053 | FEV | Included | Analytical Core Lab 1 N-0114A
RDC_NB_GF_VEV-5055 | VEV | Included | Analytical Core Lab 1 N-0114A
RDC_NB_GF_FEV-5062 | FEV | Included | Clean Lab N-0114B
RDC_NB_GF_VEV-5071 | VEV | Included | Dirty Lab N-0114C
RDC_NB_GF_FEV-5072 | FEV | Included | Dirty Lab N-0114C
RDC_NB_GF_FEV-5073 | FEV | Included | Dirty Lab N-0114C
RDC_NB_GF_FEV-5074 | FEV | Included | Dirty Lab N-0114C
RDC_NB_GF_FEV-5082 | FEV | Included | Bio Analyt N-0114D
RDC_NB_GF_FEV-5083 | FEV | Included | Bio Analyt N-0114D
RDC_NB_GF_VEV-5092 | VEV | Included | Air Quality N-0114F
RDC_NB_GF_FEV-5093 | FEV | Included | Air Quality N-0114F
RDC_NB_GF_FEV-5094 | FEV | Included | Air Quality N-0114F
RDC_NB_GF_FEV-5095A | FEV | Included | Air Quality N-0114F
RDC_NB_GF_FEV-5095B | FEV | Included | Air Quality N-0114F
RDC_NB_GF_VEV-5182A | VEV | Included | Analyt Core-2 N-0140A
RDC_NB_GF_VEV-5182B | VEV | Included | Analyt Core-2 N-0140A
RDC_NB_GF_FEV-5183 | FEV | Included | Analytical Core Lab 2 N-0140A
RDC_NB_GF_VEV-5192a | VEV | Not Included | Furnace Room N-0140B
RDC_NB_GF_VEV-5192b | VEV | Not Included | Furnace Room N-0140B
RDC_NB_GF_FEV-5203 | FEV | Included | Prep Lab N-0140C
RDC_NB_GF_VEV-5211 | VEV | Included | Sputter Room N-0140D
RDC_NB_GF_VEV-5221 | VEV | Included | MBE/Evap Room N-0140E
RDC_NB_GF_FEV-5222 | FEV | Included | Evap Room N-0140E
RDC_NB_GF_FEV-5223 | FEV | Included | Evap Room N-0140E
RDC_NB_GF_VEV-5231 | VEV | Included | ALD Room N-0140F
RDC_NB_GF_CEV-5241 | CEV | Included | Air Lock N-0140G
RDC_NB_GF_FEV-5271 | FEV | Included | Org Chem N-0140K
RDC_NB_GF_FEV-5272 | FEV | Included | Org Chem N-0140K
RDC_NB_GF_FEV-5273 | FEV | Included | Org Chem N-0140K
RDC_NB_GF_FEV-5274 | FEV | Included | Org Chem N-0140K
RDC_NB_GF_FEV-5275 | FEV | Included | Org Chem N-0140K
RDC_NB_GF_FEV-5276 | FEV | Included | Org Chem N-0140K
RDC_NB_GF_FEV-5277 | FEV | Included | Org Chem N-0140K
RDC_SB_L0_AT-0001 | AT | Included | Vestibule S-0101
RDC_SB_L0_AT-0002 | AT | Included | Employee Entry Lobby S-0102
RDC_SB_L0_AT-0004 | AT | Included | Corridor S-0104
RDC_SB_L0_AT-0005 | AT | Included | Men S-0105
RDC_SB_L0_A1.2_AT-2001 | AT | Included | High-Density Room S-0206
RDC_SB_L0_A1.3_AT-2001 | AT | Included | WOMEN S-0205
RDC_NB_GF_AT-5005 | AT | Included | Vestibule N-0105
RDC_NB_GF_AT-5010 | AT | Included | Conf N-0106
RDC_NB_GF_AT-5015 | AT | Included | Conference N-0107
RDC_NB_GF_AT-5020 | AT | Included | Mens + Vestibule + N-0109 N-0108
RDC_NB_GF_AT-5030 | AT | Included | Confr Room N-0112
RDC_NB_GF_AT-5040 | AT | Not Included | Normal Elec. N-0113
RDC_NB_GF_AT-5045 | AT | Not Included | Emergency Elec. N-0114
RDC_NB_GF_AT-5395 | AT | Included | Exp. Office N-0169
RDC_NB_GF_AT-5400 | AT | Included | Reception Area N-0170
RDC_NB_GF_AT-5405 | AT | Included | Exp. Office N-0172
RDC_NB_GF_AT-5410 | AT | Included | Conf Room N-0173
RDC_NB_GF_AT-5000 | AT | Included | Lobby North N-0101
RDC_NB_GF_AT-5001 | AT | Included | Lobby North N-0101
RDC_NB_GF_AT-6000 | AT | Included | Conf Room N-0301
RDC_NB_GF_AT-6005 | AT | Included | Vestibule N-0302
RDC_NB_GF_AT-6010 | AT | Included | Conf N-0304
RDC_NB_GF_AT-6015 | AT | Included | Men N-0306
RDC_NB_GF_AT-6020 | AT | Included | Vestibule N-0308
RDC_NB_GF_AT-6025 | AT | Not Included | Normal Elec. N-0310
RDC_NB_GF_AT-6240 | AT | Not Included | Emergency Electrical N-0350A
RDC_NB_GF_AT-6300 | AT | Included | Store N-0362B
RDC_NB_GF_AT-6305 | AT | Included | Office N-0363
RDC_NB_GF_AT-6310 | AT | Included | Office N-0364
RDC_NB_GF_AT-6315 | AT | Included | Conf Room N-0364A
RDC_NB_GF_EV-6316 | EV | Included | Conf Room N-0364A
RDC_NB_GF_EV-5021 | EV | Included | Mens + Vestibule + N-0109 N-0108
RDC_NB_GF_EV-5035 | EV | Included | Confr Room N-0112
RDC_NB_GF_EV-6016 | EV | Included | Men N-0306
RDC_NB_GF_EV-6127 | EV | Not Included | IDF N-0311
RDC_SB_L0_AT-2002 | AT | Included | Conference Room S-0207
RDC_SB_L0_AT-2003 | AT | Included | Multi Purpose Hall S-0208
RDC_SB_L0_AT-2004 | AT | Included | Multi Purpose Hall S-0208
RDC_SB_L0_AT-2006 | AT | Included | Meeting Room S-0212
RDC_SB_L0_AT-2007 | AT | Included | Office S-0213
RDC_SB_L0_AT-2008 | AT | Included | Office S-0214
RDC_SB_L0_AT-2009 | AT | Included | Office S-0215
RDC_SB_L0_AT-2010 | AT | Included | Office S-0216
RDC_SB_L0_AT-2011 | AT | Included | Office S-0217
RDC_SB_L0_AT-2012 | AT | Not Included | Director Office S-0218
RDC_SB_L0_AT-2013 | AT | Included | Office S-0219
RDC_SB_L0_AT-2014 | AT | Included | Office S-0220
RDC_SB_L0_AT-2015 | AT | Not Included | Director Office S-0221
RDC_SB_L0_AT-2016 | AT | Not Included | Director Office S-0222
RDC_SB_L0_AT-2017 | AT | Included | Meeting Room S-0223
RDC_SB_L0_AT-2018 | AT | Included | PANTRY S-0226
RDC_SB_L0_AT-2019 | AT | Included | Office S-0227
RDC_SB_L0_AT-2020 | AT | Included | Informal Meeting S-0231
RDC_SB_L0_AT-2021 | AT | Included | Open Plan S-0228
RDC_SB_L0_AT-2022 | AT | Not Included | Director Office S-0229
RDC_SB_L0_AT-2023 | AT | Included | Office S-0230
RDC_SB_L0_AT-2024 | AT | Not Included | Executive Director Office S-0232
RDC_SB_L0_AT-2025 | AT | Not Included | Executive Director Office S-0233
RDC_SB_L0_AT-2026 | AT | Included | Office S-0234
RDC_SB_L0_AT-2027 | AT | Included | Office S-0235
RDC_SB_L0_AT-2028 | AT | Included | Office S-0236
RDC_SB_L0_AT-2029 | AT | Included | Waiting Area S-0251
RDC_SB_L0_AT-2030 | AT | Included | Office S-0259
RDC_SB_L0_AT-2031 | AT | Included | Office S-0260
RDC_SB_L0_AT-2032 | AT | Included | Open Plan S-0269
RDC_SB_L0_AT-2033 | AT | Included | CORRIDOR S-0273
RDC_SB_L0_AT-2034 | AT | Included | Meeting Room S-0274
RDC_SB_L0_AT-2035 | AT | Not Included | MECH S-0272
RDC_SB_L0_AT-2036 | AT | Not Included | Emergency Elec. Room S-0278
RDC_SB_L0_AT-2037 | AT | Included | Men S-0284
RDC_SB_L0_AT-2038 | AT | Included | Informal Meeting S-0285
RDC_SB_L0_AT-2039 | AT | Included | Meeting Room S-0286
RDC_SB_L0_AT-2040 | AT | Included | Open Plan S-0289
RDC_SB_L0_AT-2041 | AT | Included | Open Plan S-0289
RDC_SB_L0_AT-2042 | AT | Included | Lobby S-0294
RDC_SB_L0_AT-2043 | AT | Included | Lobby S-0294
RDC_SB_L0_AT-2044 | AT | Included | Lobby S-0294
RDC_SB_L0_AT-2045 | AT | Included | Lobby S-0294
RDC_SB_L0_AT-2046 | AT | Included | Lobby S-0294
RDC_SB_L0_AT-2047 | AT | Included | Lobby S-0294
RDC_SB_L0_AT-0115 | AT | Included | Office S-0233A
RDC_SB_L0_AT-0116 | AT | Included | Office S-0232A
RDC_SB_L0_AT-0117 | AT | Included | Open Plan S-0228
RDC_SB_L0_AT-0118 | AT | Included | Open Plan S-0228B
RDC_SB_L0_AT-0120 | AT | Included | Open Plan S-0228A
RDC_SB_L0_AT-0122 | AT | Included | Office S-0211A
RDC_SB_L0_AT-0123 | AT | Included | Office S-0211B
RDC_SB_L0_AT-0124 | AT | Not Included | Technical Open Plan S-0211
RDC_NB_GF_AT-6130 | AT | Included | Store N-0315
RDC_NB_GF_AT-6135 | AT | Included | Store N-0316
RDC_NB_GF_AT-6140 | AT | Included | Workstation N-0317
RDC_NB_GF_AT-6145 | AT | Included | Office N-0318
RDC_NB_GF_AT-6150 | AT | Included | Office N-0319
RDC_NB_GF_AT-6155 | AT | Included | Workstation N-0320
RDC_NB_GF_AT-6160 | AT | Included | Office N-0321
RDC_NB_GF_AT-6170 | AT | Included | Office N-0323
RDC_NB_GF_AT-6175 | AT | Included | Workstation N-0324
RDC_NB_GF_AT-6180 | AT | Included | Office N-0325
RDC_NB_GF_AT-6185 | AT | Included | Office N-0326
RDC_NB_GF_AT-7000 | AT | Included | Vestibule / Staging N-0401
RDC_NB_GF_AT-6195 | AT | Included | Store N-0329
RDC_NB_GF_AT-6190 | AT | Not Included | Normal Elec. N-0328
RDC_NB_GF_AT-6200 | AT | Included | Conf N-0330
RDC_NB_GF_AT-7005 | AT | Included | WOMEN N-0402
RDC_NB_GF_AT-6220 | AT | Not Included | Emergency Elec. N-0333
RDC_NB_GF_AT-6205 | AT | Included | Conference N-0331
RDC_NB_GF_AT-6285 | AT | Included | Conference N-0358
RDC_NB_GF_AT-7380 | AT | Not Included | Pipe Chase N-0443B
RDC_NB_GF_AT-6210 | AT | Included | Corridor N-0332C
RDC_NB_GF_AT-6280 | AT | Included | Pantry N-0356
RDC_NB_GF_AT-6295 | AT | Included | Conference N-0360
RDC_NB_GF_AT-6320 | AT | Included | Corridor N-0365
RDC_NB_GF_AT-6325 | AT | Included | Office N-0366
RDC_NB_GF_AT-6330 | AT | Included | Office 04 N-0367
RDC_NB_GF_AT-6335 | AT | Included | Office N-0368
RDC_NB_GF_AT-6340 | AT | Included | Office N-0369
RDC_NB_GF_AT-6345 | AT | Included | Office N-0370
RDC_NB_GF_AT-6350 | AT | Included | Office N-0371
RDC_NB_GF_AT-6355 | AT | Included | Workstation N-0372
RDC_NB_GF_AT-6360 | AT | Included | Office N-0374
RDC_NB_GF_AT-6365 | AT | Included | Office N-0375
RDC_NB_GF_AT-6370 | AT | Included | Office N-0376
RDC_NB_GF_AT-6375 | AT | Included | Office N-0377
RDC_NB_GF_AT-6380 | AT | Included | Workstation N-0378
RDC_NB_GF_AT-6390 | AT | Included | Office N-0379
RDC_NB_GF_AT-6395 | AT | Included | Office N-0380
RDC_NB_GF_AT-6400 | AT | Included | Workstation N-0381
RDC_NB_GF_AT-6405 | AT | Included | Office N-0382
RDC_NB_GF_AT-6410 | AT | Included | Office N-0383
RDC_NB_GF_AT-7385 | AT | Included | Office N-0444
RDC_NB_GF_AT-7390 | AT | Included | Office 04 N-0445
RDC_NB_GF_EV-6141 | EV | Included | Workstation N-0317
RDC_NB_GF_EV-6156 | EV | Included | Workstation N-0320
RDC_NB_GF_EV-6176 | EV | Included | Workstation N-0324
RDC_NB_GF_EV-6281 | EV | Included | Pantry N-0356
RDC_NB_GF_EV-6356 | EV | Included | Office 05-8-WKS N-0372
RDC_NB_GF_EV-6381 | EV | Included | Office 05-8-WKS N-0378
RDC_NB_GF_EV-6401 | EV | Included | Office 05-8-WKS N-0381
RDC_NB_GF_EV-7006 | EV | Included | WOMEN N-0402
RDC_NB_GF_EV-7381 | EV | Included | Pipe Chase N-0443B
RDC_NB_GF_VEV-6053 | VEV | Included | Open Lab 1 N-0310C
RDC_NB_GF_VEV-6061 | VEV | Included | Lab Support 3 N-0310D
RDC_NB_GF_VEV-6071 | VEV | Included | Lab Support 4 N-0310E
RDC_NB_GF_VEV-6081 | VEV | Included | Lab Support 5 N-0310F
RDC_NB_GF_VEV-6091 | VEV | Included | Lab Support 6 N-0310G
RDC_NB_GF_VAV-6080 | VAV | Included | Lab Support 5 N-0310F
RDC_NB_GF_FCU6997 | FCU | Included | Lab Sup 2 N-0310B
RDC_SB_L0_AT-3001 | AT | Not Included | Director Office S-0237
RDC_SB_L0_AT-3002 | AT | Included | Office S-0238
RDC_SB_L0_AT-3003 | AT | Included | Office S-0239
RDC_SB_L0_AT-3004 | AT | Included | Office S-0240
RDC_SB_L0_AT-3005 | AT | Included | Office S-0241
RDC_SB_L0_AT-3006 | AT | Included | Office S-0242
RDC_SB_L0_AT-3007 | AT | Not Included | Director Office S-0243
RDC_SB_L0_AT-3010 | AT | Included | Open Plan S-0244
RDC_SB_L0_AT-3011 | AT | Included | Meeting Room S-0245
RDC_SB_L0_AT-3012 | AT | Included | Office S-0246
RDC_SB_L0_AT-3013 | AT | Included | Office S-0247
RDC_SB_L0_AT-3014 | AT | Included | Office S-0248
RDC_SB_L0_AT-3015 | AT | Not Included | Security S-0249
RDC_SB_L0_AT-3016 | AT | Included | Corridor S-0250
RDC_SB_L0_AT-3017 | AT | Included | Office S-0251
RDC_SB_L0_AT-3018 | AT | Included | Corridor S-0251B
RDC_SB_L0_AT-3019 | AT | Included | Corridor S-0251B
RDC_SB_L0_AT-3020 | AT | Included | Office S-0252
RDC_SB_L0_AT-3021 | AT | Included | Office S-0252
RDC_SB_L0_AT-3022 | AT | Included | Office S-0253
RDC_SB_L0_AT-3023 | AT | Included | Office S-0253
RDC_SB_L0_AT-3024 | AT | Included | Office S-0254
RDC_SB_L0_AT-3025 | AT | Included | Office S-0255
RDC_SB_L0_AT-3026 | AT | Included | Office S-0256
RDC_SB_L0_AT-3027 | AT | Included | Office S-0257
RDC_SB_L0_AT-3028 | AT | Included | Office S-0258
RDC_SB_L0_AT-3031 | AT | Not Included | IT Server S-0264
RDC_SB_L0_AT-3032 | AT | Included | Open Plan S-0265
RDC_SB_L0_AT-3033 | AT | Not Included | Emergency Elec. S-0266
RDC_SB_L0_AT-3034 | AT | Included | Reception / Vestibule S-0293
RDC_SB_L0_AT-3035 | AT | Included | Lobby S-0294
RDC_SB_L0_AT-3036 | AT | Included | Lobby S-0294
RDC_SB_L0_AT-0101 | AT | Included | Office S-0244A
RDC_SB_L0_AT-0102 | AT | Included | Office S-0244B
RDC_SB_L0_AT-0103 | AT | Included | Office S-0244C
RDC_SB_L0_AT-0104 | AT | Included | Office S-0244D
RDC_SB_L0_AT-0105 | AT | Included | Office S-0244E
RDC_SB_L0_AT-0107 | AT | Included | Office S-0262A
RDC_SB_L0_AT-0108 | AT | Included | Office S-0262B
RDC_SB_L0_AT-0109 | AT | Included | Office S-0262C
RDC_SB_L0_AT-0110 | AT | Included | Office S-0262H
RDC_SB_L0_AT-0111 | AT | Included | Office S-0262E
RDC_SB_L0_AT-0112 | AT | Included | Office S-0262F
RDC_SB_L0_AT-0113 | AT | Included | Office S-0262G
RDC_SB_L0_AT-0114 | AT | Included | Office S-0262D
RDC_NB_GF_AT-7080 | AT | Included | Exp. Office N-0410
RDC_NB_GF_AT-7085 | AT | Included | Office N-0411
RDC_NB_GF_AT-7095 | AT | Included | Office N-0413
RDC_NB_GF_AT-7100 | AT | Included | Office N-0414
RDC_NB_GF_AT-7110 | AT | Included | Office N-0416
RDC_NB_GF_AT-7115 | AT | Included | Office N-0417
RDC_NB_GF_AT-7125 | AT | Not Included | NORMAL ELEC. ROOM N-0420
RDC_NB_GF_AT-7130 | AT | Included | Office N-0421
RDC_NB_GF_AT-7135 | AT | Included | Office N-0422
RDC_NB_GF_AT-7140 | AT | Included | Conference N-0423
RDC_NB_GF_AT-7145 | AT | Included | Office N-0425
RDC_NB_GF_AT-7155 | AT | Included | Office N-0427
RDC_NB_GF_AT-7165 | AT | Included | Office N-0429
RDC_NB_GF_AT-7180 | AT | Included | Corridor N-0432
RDC_NB_GF_AT-7185 | AT | Not Included | Emer. Elec. Room N-0433
RDC_NB_GF_AT-7195 | AT | Included | OFFICE N-0436
RDC_NB_GF_AT-7205 | AT | Included | Office 04 N-0438
RDC_NB_GF_AT-7215 | AT | Included | CONFERENCE ROOM N-0440
RDC_NB_GF_AT-7395 | AT | Included | Workstation N-0446
RDC_NB_GF_AT-7400 | AT | Included | Office N-0447
RDC_NB_GF_AT-7405 | AT | Included | Office N-0448
RDC_NB_GF_AT-7410 | AT | Included | Office N-0449
RDC_NB_GF_AT-7415 | AT | Included | Office N-0450
RDC_NB_GF_AT-7425 | AT | Included | Workstation N-0452
RDC_NB_GF_AT-7430 | AT | Included | Office N-0453
RDC_NB_GF_AT-7435 | AT | Included | Office N-0454
RDC_NB_GF_AT-7440 | AT | Included | Office N-0455
RDC_NB_GF_AT-7445 | AT | Included | Office N-0456
RDC_NB_GF_AT-7460 | AT | Included | Workstation N-0457
RDC_NB_GF_AT-7465 | AT | Included | Office N-0458
RDC_NB_GF_AT-7470 | AT | Included | Office N-0459
RDC_NB_GF_AT-7475 | AT | Included | Office N-0460
RDC_NB_GF_AT-7480 | AT | Included | Office N-0461
RDC_NB_GF_AT-7485 | AT | Included | WORKSTATION N-0462
RDC_NB_GF_AT-7490 | AT | Included | Confer N-0463
RDC_NB_GF_AT-7496 | AT | Included | Office N-0464
RDC_NB_GF_AT-7498 | AT | Included | Office N-0465
RDC_NB_GF_AT-7499 | AT | Included | Office N-0466
RDC_NB_GF_AT-7090-N1 | AT | Included | Office N-0412
RDC_NB_GF_AT-7090-N2 | AT | Included | Office N-0412A
RDC_NB_GF_AT-7105-N1 | AT | Included | Office N-0415
RDC_NB_GF_AT-7105-N2 | AT | Included | Office N-0415A
RDC_NB_GF_AT-7120-N1 | AT | Included | Office N-0418
RDC_NB_GF_AT-7120-N2 | AT | Included | Office N-0418A
RDC_NB_GF_AT-7120-N3 | AT | Included | Office N-0430A
RDC_NB_GF_AT-7120-N4 | AT | Included | Office N-0430B
RDC_NB_GF_AT-7120-N5 | AT | Included | Office N-0430C
RDC_NB_GF_AT-7120-N6 | AT | Included | Office N-0430D
RDC_NB_GF_AT-7120-N7 | AT | Included | Office N-0430E
RDC_NB_GF_AT-7120-N8 | AT | Included | Office N-0430F
RDC_NB_GF_AT-7120-N9 | AT | Included | Corridor N-0418A
RDC_NB_GF_EV-7091 | EV | Included | Office N-0412A
RDC_NB_GF_EV-7106 | EV | Included | Office N-0415A
RDC_NB_GF_EV-7121 | EV | Included | Office 05-4-WS N-0418
RDC_NB_GF_EV-7122 | EV | Not Included | IDF Room N-0419
RDC_NB_GF_EV-7396 | EV | Included | Office 05-8-WKS N-0446
RDC_NB_GF_EV-7426 | EV | Included | Office 05-8-WKS N-0452
RDC_NB_GF_EV-7461 | EV | Included | Office 05-8-WKS N-0457
RDC_NB_GF_EV-7486 | EV | Included | Office 05-8-WKS N-0462
RDC_NB_GF_VEV-7022A | VEV | Included | NMR Lab N-0404A
RDC_NB_GF_VEV-7022B | VEV | Included | NMR Lab N-0404A
RDC_NB_GF_VEV-7023A | VEV | Included | NMR Lab N-0404A
RDC_NB_GF_VEV-7023B | VEV | Included | NMR Lab N-0404A
RDC_NB_GF_VEV-7024A | VEV | Included | NMR Lab N-0404A
RDC_NB_GF_VEV-7024B | VEV | Included | NMR Lab N-0404A
RDC_NB_GF_FEV-7052 | FEV | Included | EM Prep 1 - MAT N-0404D
RDC_NB_GF_FEV-7053 | FEV | Included | EM Prep 1 - MAT N-0404D
RDC_NB_GF_FEV-7062 | FEV | Included | EM Prep 2 - BIO N-0404E
RDC_NB_GF_VEV-7072A | VEV | Included | Surf Analysis Lab N-0404F
RDC_NB_GF_VEV-7072B | VEV | Included | Surf Analysis Lab N-0404F
RDC_NB_GF_VEV-7073 | VEV | Included | Surf Analysis Lab N-0404F
RDC_NB_GF_FEV-7074 | FEV | Included | Surf Analysis Lab N-0404F
RDC_NB_GF_FEV-7075 | FEV | Included | Surf Analysis Lab N-0404F
RDC_NB_GF_FEV-7232 | FEV | Included | Inter Lab N-0442A
RDC_NB_GF_VEV-7241B | VEV | Included | Optical Lab N-0442B
RDC_NB_GF_VEV-7301 | VEV | Included | A/L 1 N-0442H
RDC_NB_GF_FCU7993 | FCU | Included | Stair 5 N-0ST05
RDC_SB_1F_AT-1504 | AT | Included | Corridor S-1122
RDC_SB_1F_AT-1507 | AT | Included | Workstation S-1124A
RDC_SB_1F_AT-1508 | AT | Included | Scientific Comp. Office 1 S-1125
RDC_SB_1F_AT-1509 | AT | Included | Scientific Comp. Office S-1126
RDC_SB_1F_AT-1510 | AT | Included | ALT Office 2 S-1127
RDC_SB_1F_AT-1511 | AT | Included | ALT Office 3 S-1128
RDC_SB_1F_AT-1512 | AT | Included | Workstation S-1128A
RDC_SB_1F_AT-1513 | AT | Included | ALT Office 1 S-1129
RDC_SB_1F_AT-1514 | AT | Included | ALT Office S-1130
RDC_SB_1F_AT-1515 | AT | Included | Distub. Syst Office 1 S-1131
RDC_SB_1F_AT-1516 | AT | Included | Distub. Syst Office S-1132
RDC_SB_1F_AT-1517 | AT | Included | Workstation S-1132A
RDC_SB_1F_AT-1518 | AT | Included | Distub. Syst Office S-1133
RDC_SB_1F_AT-1519 | AT | Included | Distub. Syst Office S-1134
RDC_SB_1F_AT-1520 | AT | Included | Data Analytic Office S-1135
RDC_SB_1F_AT-1521 | AT | Included | Data Analytic Office S-1136
RDC_SB_1F_AT-1522 | AT | Included | Workstation S-1136A
RDC_SB_1F_AT-1523 | AT | Included | Data Analytic Office S-1137
RDC_SB_1F_AT-1524 | AT | Included | Data Analytic Office S-1138
RDC_SB_1F_AT-1525 | AT | Included | Office S-1139
RDC_SB_1F_AT-1526 | AT | Included | Office S-1140
RDC_SB_1F_AT-1527 | AT | Included | Conference Room S-1141
RDC_SB_1F_AT-1528 | AT | Included | Office S-1142
RDC_SB_1F_AT-1529 | AT | Included | Office S-1144
RDC_SB_1F_AT-1530 | AT | Included | Office S-1145
RDC_SB_1F_AT-1531 | AT | Included | Office S-1146
RDC_SB_1F_AT-1532 | AT | Included | Workstation S-1146A
RDC_SB_1F_AT-1533 | AT | Included | Office S-1148
RDC_SB_1F_AT-1534 | AT | Included | Office S-1149
RDC_SB_1F_AT-1535 | AT | Included | Pantry S-1149A
RDC_SB_1F_AT-1536 | AT | Included | Office S-1150
RDC_SB_1F_AT-1537 | AT | Not Included | Normal Elec. S-1147
RDC_SB_1F_AT-1542 | AT | Included | Office S-1182
RDC_SB_1F_AT-1546 | AT | Included | Office S-1182E
RDC_SB_1F_AT-1548 | AT | Included | Office S-1183
RDC_SB_1F_AT-1549 | AT | Included | Workstation S-1183A
RDC_SB_1F_AT-1550 | AT | Included | Office S-1184
RDC_SB_1F_AT-1551 | AT | Included | Social Comp Office S-1185
RDC_SB_1F_AT-1552 | AT | Included | Social Comp Office S-1186
RDC_SB_1F_AT-1553 | AT | Included | Workstation S-1186A
RDC_SB_1F_AT-1554 | AT | Included | Social Comp Office S-1187
RDC_SB_1F_AT-1555 | AT | Included | Social Comp Office S-1188
RDC_SB_1F_AT-1556 | AT | Included | Cyber Sec Office S-1189
RDC_SB_1F_AT-1557 | AT | Included | Cyber Sec Office S-1190
RDC_SB_1F_AT-1558 | AT | Included | Workstation S-1190A
RDC_SB_1F_AT-1559 | AT | Included | Office S-1191
RDC_SB_1F_AT-1560 | AT | Included | Cyber Sec Office S-1192
RDC_SB_1F_AT-1561 | AT | Included | Cyber Sec Office S-1193
RDC_SB_1F_AT-0538 | AT | Included | Workstation S-1151A
RDC_NB_1F_AT-4660 | AT | Included | Expansion Workstation N-1227
RDC_NB_1F_AT-4665 | AT | Included | Office N-1228
RDC_NB_1F_AT-4680 | AT | Included | Office N-1231
RDC_NB_1F_AT-4690 | AT | Included | Office N-1233
RDC_NB_1F_AT-4705 | AT | Included | Office N-1236
RDC_NB_1F_AT-4720 | AT | Included | Office N-1239
RDC_NB_1F_AT-4730 | AT | Included | Office N-1241
RDC_NB_1F_AT-4745 | AT | Included | Office N-1244
RDC_NB_1F_EV-4500 | EV | Not Included | MDF N-1201
RDC_NB_1F_CEV-4502 | CEV | Included | Corridor N-1202
RDC_NB_1F_EV-4661 | EV | Included | Office 05 - 8 WKS- N-1227
RDC_NB_1F_EV-4686 | EV | Included | Office 05 - 8 WKS- N-1232
RDC_NB_1F_EV-4711 | EV | Included | Office 05 - 8 WKS- N-1237
RDC_NB_1F_EV-4736 | EV | Included | Office 05 - 8 WKS- N-1242
RDC_NB_1F_VEV-4602 | VEV | Included | Testing Room N-1216B
RDC_NB_1F_FEV-4603 | FEV | Included | Testing Room N-1216B
RDC_NB_1F_FEV-4604 | FEV | Included | Testing Room N-1216B
RDC_NB_1F_FEV-4605 | FEV | Included | Testing Room N-1216B
RDC_NB_1F_FEV-4606 | FEV | Included | Testing Room N-1216B
RDC_NB_1F_FEV-4622 | FEV | Included | EL Shop N-1216C
RDC_NB_1F_CAV-4581B | CAV | Included | Photovoltaic Lab N-1216A
RDC_NB_1F_VEV-4585A | VEV | Included | Photovoltaic Lab N-1216A
RDC_NB_1F_VEV-4585B | VEV | Included | Photovoltaic Lab N-1216A
RDC_NB_1F_VEV-4586A | VEV | Included | Photovoltaic Lab N-1216A
RDC_NB_1F_VEV-4586B | VEV | Included | Photovoltaic Lab N-1216A
RDC_NB_1F_FEV-4587 | FEV | Included | Photovoltaic Lab N-1216A
RDC_NB_1F_FEV-4588 | FEV | Included | Photovoltaic Lab N-1216A
RDC_NB_1F_FCU2004 | FCU | Included | Corridor N-1202
RDC_SB_1F_AT-0501 | AT | Included | Lobby S-1102
RDC_SB_1F_AT-0502 | AT | Included | Vestibule S-1105
RDC_SB_1F_AT-0503 | AT | Included | Women S-1106B
RDC_SB_1F_AT-0504 | AT | Included | Vestibule S-1107
RDC_SB_1F_AT-0505 | AT | Not Included | EMERGENCY Elec. S-1107B
RDC_SB_1F_AT-0515 | AT | Included | Corridor S-1122
RDC_SB_1F_AT-0516 | AT | Included | Pantry S-1158
RDC_SB_1F_AT-0517 | AT | Not Included | Normal Elec. S-1160
RDC_SB_1F_AT-0524 | AT | Included | Women S-1169
RDC_SB_1F_AT-0525 | AT | Included | Men S-1170
RDC_SB_1F_AT-0534 | AT | Included | CORRIDOR S-1180
RDC_SB_1F_AT-0535 | AT | Included | Cooridor S-1180
RDC_SB_1F_AT-1541 | AT | Included | Cooridor S-1181
RDC_SB_1F_AT-0506 | AT | Included | Conf. S-1110
RDC_SB_1F_AT-0507 | AT | Not Included | Computer Research Lab-4 S-1112
RDC_SB_1F_AT-0508 | AT | Included | Conf S-1113
RDC_SB_1F_AT-0509 | AT | Included | NCIR OFFICE S-1115
RDC_SB_1F_AT-0510 | AT | Included | Workstation S-1115A
RDC_SB_1F_AT-0511 | AT | Included | NCIR Office S-1116
RDC_SB_1F_AT-0512 | AT | Included | NCIR Office S-1117
RDC_SB_1F_AT-0513 | AT | Included | NCIR Office S-1118
RDC_SB_1F_AT-0514 | AT | Included | NCIR Office S-1119
RDC_SB_1F_AT-0518 | AT | Included | Office S-1161
RDC_SB_1F_AT-0519 | AT | Included | Office S-1162
RDC_SB_1F_AT-0520 | AT | Included | Office S-1163
RDC_SB_1F_AT-0521 | AT | Included | Office S-1164
RDC_SB_1F_AT-0522 | AT | Included | Office S-1165
RDC_SB_1F_AT-0523 | AT | Included | Office S-1166
RDC_SB_1F_AT-0526 | AT | Included | Office S-1171
RDC_SB_1F_AT-0527 | AT | Included | Office S-1172
RDC_SB_1F_AT-0528 | AT | Included | Office S-1173
RDC_SB_1F_AT-0529 | AT | Included | Corridor S-1174
RDC_SB_1F_AT-0530 | AT | Included | Situation Room S-1175
RDC_SB_1F_AT-0531 | AT | Included | Immersive Viz Lab S-1176
RDC_SB_1F_AT-0532 | AT | Included | Conference Room S-1177
RDC_SB_1F_AT-0533 | AT | Included | Telepresence S-1179
RDC_SB_1F_AT-1501 | AT | Included | Workstation S-1119A
RDC_SB_1F_AT-1502 | AT | Included | NCIR Office S-1120
RDC_SB_1F_AT-1503 | AT | Included | NCIR Office S-1121
RDC_SB_1F_AT-1505 | AT | Included | SC. Comp Office 2 S-1123
RDC_SB_1F_AT-1506 | AT | Included | SC. Comp Office 3 S-1124
RDC_SB_1F_AT-1539 | AT | Included | Video Conf. Room S-1154
RDC_SB_1F_AT-1540 | AT | Included | Conf S-1159
RDC_SB_1F_AT-1543 | AT | Included | Workstation S-1182A
RDC_SB_1F_AT-1544 | AT | Included | Office S-1182C
RDC_SB_1F_AT-1545 | AT | Included | Office S-1182D
RDC_SB_1F_AT-1547 | AT | Included | Office S-1182F
RDC_NB_1F_AT-5650 | AT | Included | Office N-1120
RDC_NB_1F_AT-5655 | AT | Included | Store N-1120B
RDC_NB_1F_AT-5660 | AT | Included | Office N-1121
RDC_NB_1F_AT-5665 | AT | Included | Office N-1122
RDC_NB_1F_AT-5670 | AT | Included | Office N-1123
RDC_NB_1F_AT-5675 | AT | Included | Office N-1124
RDC_NB_1F_AT-5680 | AT | Included | Office N-1125
RDC_NB_1F_AT-5685 | AT | Included | Corridor N-1126
RDC_NB_1F_AT-5690 | AT | Included | Office N-1127
RDC_NB_1F_AT-5695 | AT | Included | Office N-1128
RDC_NB_1F_AT-5700 | AT | Included | Office N-1129
RDC_NB_1F_AT-5705 | AT | Included | Office N-1130
RDC_NB_1F_AT-5710 | AT | Included | Office N-1131
RDC_NB_1F_AT-5715 | AT | Included | Conf Rm N-1132
RDC_NB_1F_AT-5730 | AT | Included | Store N-1135
RDC_NB_1F_AT-5735 | AT | Not Included | Normal Elec. N-1136
RDC_NB_1F_AT-5740 | AT | Not Included | Emer. Elec. N-1137
RDC_NB_1F_AT-5745 | AT | Included | Corridor N-1138
RDC_NB_1F_AT-5760 | AT | Included | Conf N-1143
RDC_NB_1F_AT-5835 | AT | Included | P/C/S Pantry N-1146
RDC_NB_1F_AT-5840 | AT | Included | Corridor N-1150
RDC_NB_1F_AT-5860 | AT | Included | Office N-1154
RDC_NB_1F_AT-5865 | AT | Included | Office N-1155
RDC_NB_1F_AT-5870 | AT | Included | Exp Office N-1156
RDC_NB_1F_AT-5875 | AT | Included | Office N-1157
RDC_NB_1F_AT-5880 | AT | Included | Office N-1158
RDC_NB_1F_AT-5885 | AT | Included | Office N-1159
RDC_NB_1F_AT-5890 | AT | Included | Workstation N-1160
RDC_NB_1F_AT-5895 | AT | Included | Office N-1161
RDC_NB_1F_AT-5900 | AT | Included | Office N-1162
RDC_NB_1F_AT-5905 | AT | Included | Office N-1163
RDC_NB_1F_AT-5910 | AT | Included | Office N-1164
RDC_NB_1F_AT-5915 | AT | Included | Office N-1167
RDC_NB_1F_AT-5920 | AT | Included | Workstation N-1168
RDC_NB_1F_AT-5925 | AT | Included | Office N-1169
RDC_NB_1F_AT-5930 | AT | Included | Office N-1170
RDC_NB_1F_AT-5935 | AT | Included | Office N-1166
RDC_NB_1F_AT-5940 | AT | Included | Workstation N-1165
RDC_NB_1F_AT-5720 | AT | Included | Men N-1134
RDC_NB_1F_AT-5750 | AT | Included | Store N-1141
RDC_NB_1F_AT-4640 | AT | Included | Women N-1221
RDC_NB_1F_AT-4650 | AT | Included | Breakout N-1225
RDC_NB_1F_EV-5686 | EV | Included | Corridor N-1126
RDC_NB_1F_EV-5721 | EV | Included | Men N-1134
RDC_NB_1F_EV-5747 | EV | Not Included | IDF N-1140
RDC_NB_1F_EV-4641 | EV | Included | Women N-1221
RDC_NB_1F_EV-5891 | EV | Included | Office 05 - 8 WKS- North N-1160
RDC_NB_1F_EV-5921 | EV | Included | Office 05 - 8 WKS- N-1168
RDC_NB_1F_EV-5941 | EV | Included | Office 05 - 8 WKS- N-1165
RDC_NB_1F_FEV-5624 | FEV | Included | Sequence Lab N-1115K
RDC_NB_1F_VEV-5572 | VEV | Included | Met/Prot Lab N-1115C
RDC_NB_1F_VEV-5573A | VEV | Included | Met/Prot Lab N-1115C
RDC_NB_1F_VEV-5573B | VEV | Included | Met/Prot Lab N-1115C
RDC_NB_1F_FEV-5574 | FEV | Included | Met/Prot Lab N-1115C
RDC_NB_1F_FEV-5575 | FEV | Included | Met/Prot Lab N-1115C
RDC_NB_1F_VEV-5591 | VEV | Included | Cell Culture N-1115E
RDC_NB_1F_FEV-5772 | FEV | Included | Histology N-1144A
RDC_NB_1F_VEV-5791 | VEV | Included | Shafallah N-1144C
RDC_NB_1F_VEV-5795B | VEV | Included | Storage and Archives N-1144C2
RDC_NB_1F_FEV-5796 | FEV | Included | Shafallah N-1144C
RDC_NB_1F_VEV-5811A | VEV | Included | Nano Lab N-1144E
RDC_NB_1F_VEV-5811B | VEV | Included | Nano Lab N-1144E
RDC_NB_1F_FEV-5812 | FEV | Included | Nano Lab N-1144E
RDC_NB_1F_FEV-5813 | FEV | Included | Nano Lab N-1144E
RDC_NB_1F_VEV-5821 | VEV | Included | Nano Lab N-1144E
RDC_SB_1F_AT-2501 | AT | Included | Lobby S-1201
RDC_SB_1F_AT-2507 | AT | Included | Female S-1204
RDC_SB_1F_AT-2502 | AT | Included | Lobby S-1202
RDC_SB_1F_AT-2503 | AT | Included | Lobby S-1202
RDC_SB_1F_AT-2504 | AT | Included | Lobby S-1202
RDC_SB_1F_AT-2505 | AT | Included | Lobby S-1202
RDC_SB_1F_AT-2506 | AT | Included | Lobby S-1202
RDC_SB_1F_AT-2508 | AT | Included | Female Prayer S-1207
RDC_SB_1F_AT-2509 | AT | Included | Open Plan S-1210
RDC_SB_1F_AT-2510 | AT | Not Included | Exc. Dir. Office S-1211
RDC_SB_1F_AT-2511 | AT | Included | Office S-1212
RDC_SB_1F_AT-2512 | AT | Included | Office S-1213
RDC_SB_1F_AT-2513 | AT | Included | Office S-1214
RDC_SB_1F_AT-2514 | AT | Included | Office S-1215
RDC_SB_1F_AT-2515 | AT | Included | Office S-1216
RDC_SB_1F_AT-2516 | AT | Not Included | Executive Director Office S-1217
RDC_SB_1F_AT-2517 | AT | Not Included | Executive Director Office S-1218
RDC_SB_1F_AT-2518 | AT | Included | Office S-1219
RDC_SB_1F_AT-2519 | AT | Included | Office S-1220
RDC_SB_1F_AT-2520 | AT | Included | Office S-1221
RDC_SB_1F_AT-2521 | AT | Included | Office S-1222
RDC_SB_1F_AT-2522 | AT | Included | Office S-1223
RDC_SB_1F_AT-2523 | AT | Included | Office S-1224
RDC_SB_1F_AT-2524 | AT | Included | Office S-1225
RDC_SB_1F_AT-2525 | AT | Included | Office S-1226
RDC_SB_1F_AT-2526 | AT | Included | Open Plan S-1227
RDC_SB_1F_AT-2527 | AT | Not Included | Director Office S-1228
RDC_SB_1F_AT-2528 | AT | Not Included | Director Office S-1230
RDC_SB_1F_AT-2529 | AT | Included | Office S-1231
RDC_SB_1F_AT-2530 | AT | Included | Office S-1232
RDC_SB_1F_AT-2531 | AT | Not Included | Director Ofice S-1241
RDC_SB_1F_AT-2532 | AT | Included | Office S-1242
RDC_SB_1F_AT-2533 | AT | Included | Cooridor S-1246
RDC_SB_1F_AT-2534 | AT | Included | Meeting Room S-1247
RDC_SB_1F_AT-2535 | AT | Included | Store S-1248
RDC_SB_1F_AT-2536 | AT | Not Included | Normal Elec. S-1251
RDC_SB_1F_AT-2538 | AT | Included | Office S-1257
RDC_SB_1F_AT-2539 | AT | Included | Office S-1257B
RDC_SB_1F_AT-2540 | AT | Not Included | Executive Director S-1260
RDC_SB_1F_AT-2541 | AT | Included | Assistant S-1261
RDC_SB_1F_AT-2542 | AT | Included | Open Plan S-1263
RDC_SB_1F_AT-2543 | AT | Included | Office S-1264
RDC_SB_1F_AT-2544 | AT | Included | Office S-1265
RDC_SB_1F_AT-2545 | AT | Included | Office S-1266
RDC_SB_1F_AT-2546 | AT | Included | Office S-1267
RDC_SB_1F_AT-2547 | AT | Included | Office S-1268
RDC_SB_1F_AT-2548 | AT | Included | Office S-1269
RDC_SB_1F_AT-2549 | AT | Included | Office S-1270
RDC_SB_1F_AT-2550 | AT | Included | Office S-1271
RDC_SB_1F_AT-2551 | AT | Included | Meeting Room S-1272
RDC_SB_1F_AT-2552 | AT | Included | Vestibule S-1273
RDC_SB_1F_AT-2553 | AT | Included | Male Prayer S-1278
RDC_SB_1F_AT-4260 | AT | Included | Office 05 -8WS- N-0255
RDC_NB_1F_AT-6650 | AT | Included | Office N-1319
RDC_NB_1F_AT-6655 | AT | Included | Office N-1320
RDC_NB_1F_AT-6660 | AT | Included | Workstation N-1321
RDC_NB_1F_AT-6665 | AT | Included | Office N-1322
RDC_NB_1F_AT-6670 | AT | Included | Office N-1323
RDC_NB_1F_AT-6675 | AT | Included | Workstation N-1324
RDC_NB_1F_AT-6680 | AT | Included | Office N-1325
RDC_NB_1F_AT-6685 | AT | Included | Office N-1326
RDC_NB_1F_AT-6690 | AT | Included | Exp. Workstation N-1327
RDC_NB_1F_AT-6695 | AT | Included | Office N-1328
RDC_NB_1F_AT-6700 | AT | Not Included | NORMAL ELEC. N-1329
RDC_NB_1F_AT-6705 | AT | Included | Office N-1330
RDC_NB_1F_AT-6710 | AT | Included | Office N-1331
RDC_NB_1F_AT-6715 | AT | Included | Office N-1332
RDC_NB_1F_AT-6720 | AT | Included | Corridor N-1335
RDC_NB_1F_AT-6725 | AT | Not Included | Emer. Elec. N-1336
RDC_NB_1F_AT-6740 | AT | Included | Men N-1340
RDC_NB_1F_AT-7500 | AT | Included | Women N-1403
RDC_NB_1F_AT-6900 | AT | Included | Office N-1357
RDC_NB_1F_AT-6905 | AT | Included | Open Plan N-1358
RDC_NB_1F_AT-6910 | AT | Included | Office N-1359
RDC_NB_1F_AT-6915 | AT | Included | Office N-1360
RDC_NB_1F_AT-6920 | AT | Included | Office N-1360B
RDC_NB_1F_AT-6925 | AT | Included | Office N-1361
RDC_NB_1F_AT-6930 | AT | Included | Office N-1362
RDC_NB_1F_AT-6935 | AT | Included | Workstation N-1363
RDC_NB_1F_AT-6940 | AT | Included | Office N-1364
RDC_NB_1F_AT-6945 | AT | Included | Office N-1365
RDC_NB_1F_AT-6950 | AT | Included | Office N-1366
RDC_NB_1F_AT-6955 | AT | Included | Office N-1367
RDC_NB_1F_AT-6960 | AT | Included | Workstation N-1368
RDC_NB_1F_AT-6965 | AT | Included | Office N-1369
RDC_NB_1F_AT-6967 | AT | Included | Office N-1370
RDC_NB_1F_AT-6968 | AT | Included | Workstation N-1371
RDC_NB_1F_AT-6970 | AT | Included | PANTRY N-1372
RDC_NB_1F_AT-7865 | AT | Included | Workstation N-1461A
RDC_NB_1F_AT-6372 | AT | Included | Office N-1374
RDC_NB_1F_AT-6374 | AT | Included | Office N-1375
RDC_NB_1F_AT-6376 | AT | Included | Office N-1376
RDC_NB_1F_AT-6378 | AT | Included | Office N-1377
RDC_NB_1F_EV-6661 | EV | Included | Workstation N-1321
RDC_NB_1F_EV-6676 | EV | Included | Workstation N-1324
RDC_NB_1F_EV-6691 | EV | Included | Exp. Workstation N-1327
RDC_NB_1F_EV-6741 | EV | Included | Men N-1340
RDC_NB_1F_EV-7501 | EV | Included | Women N-1403
RDC_NB_1F_EV-6936 | EV | Included | Workstation N-1363
RDC_NB_1F_EV-6961 | EV | Included | Workstation N-1368
RDC_NB_1F_EV-6969 | EV | Included | Workstation N-1371
RDC_NB_1F_VEV-6541 | VEV | Included | TC1 N-1316B
RDC_NB_1F_VEV-6552 | VEV | Included | Gene Therapy Lab N-1316C
RDC_NB_1F_VEV-6553 | VEV | Included | Gene Therapy Lab N-1316C
RDC_NB_1F_FEV-6554 | FEV | Included | Gene Therapy Lab N-1316C
RDC_NB_1F_FEV-6555 | FEV | Included | Gene Therapy Lab N-1316C
RDC_NB_1F_CEV-6581 | CEV | Included | TC3 N-1316F
RDC_NB_1F_FEV-6602 | FEV | Included | Analytical Core N-1316H
RDC_NB_1F_FEV-6632 | FEV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_FEV-6633 | FEV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_FEV-6634 | FEV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_FEV-6635 | FEV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_FEV-6636 | FEV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_FEV-6637 | FEV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_FEV-6638 | FEV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_FEV-6639 | FEV | Included | Bio-Med Chem Lab 1 N-1316L
RDC_NB_1F_FEV-6731 | FEV | Included | SERIVICE CORRRIDOR N-1337
RDC_NB_1F_VEV-6751 | VEV | Included | TC1 N-1345A
RDC_NB_1F_VEV-6762 | VEV | Included | Diabetes Lab / Open Lab N-1345B
RDC_NB_1F_VEV-6763 | VEV | Included | Diabetes Lab / Open Lab N-1345B
RDC_NB_1F_FEV-6764 | FEV | Included | Diabetes Lab / Open Lab N-1345B
RDC_NB_1F_FEV-6765 | FEV | Included | Diabetes Lab / Open Lab N-1345B
RDC_NB_1F_FEV-6766 | FEV | Included | Diabetes Lab / Open Lab N-1345B
RDC_NB_1F_CEV-6791 | CEV | Included | TC2 N-1345C
RDC_NB_1F_FEV-6852 | FEV | Included | Bio-Med Chem Lab 2 N-1345J
RDC_NB_1F_FEV-6853 | FEV | Included | Bio-Med Chem Lab 2 N-1345J
RDC_NB_1F_FEV-6854 | FEV | Included | Bio-Med Chem Lab 2 N-1345J
RDC_NB_1F_FEV-6855 | FEV | Included | Bio-Med Chem Lab 2 N-1345J
RDC_NB_1F_FEV-6856 | FEV | Included | Bio-Med Chem Lab 2 N-1345J
RDC_NB_1F_FEV-6857 | FEV | Included | Bio-Med Chem Lab 2 N-1345J
RDC_NB_1F_FEV-6858 | FEV | Included | Bio-Med Chem Lab 2 N-1345J
RDC_NB_1F_FEV-6859 | FEV | Included | Bio-Med Chem Lab 2 N-1345J
RDC_SB_1F_AT-3501 | AT | Included | Lobby S-0294
RDC_SB_1F_AT-3502 | AT | Included | Lobby S-0294
RDC_SB_1F_AT-3503 | AT | Included | Reception S-0293
RDC_SB_1F_AT-3504 | AT | Included | Open Plan S-1229
RDC_SB_1F_AT-3505 | AT | Included | Open Plan S-1229
RDC_SB_1F_AT-3506 | AT | Included | Office S-1233
RDC_SB_1F_AT-3507 | AT | Included | Office S-1234
RDC_SB_1F_AT-3508 | AT | Included | Office S-1235
RDC_SB_1F_AT-3509 | AT | Not Included | Policy Director Office S-1237
RDC_SB_1F_AT-3510 | AT | Not Included | Policy Executive Director Office S-1240
RDC_SB_1F_AT-3511 | AT | Included | CORRIDOR S-1280
RDC_SB_1F_AT-3512 | AT | Included | Pantry S-1282
RDC_SB_1F_AT-3513 | AT | Included | Office S-1283
RDC_SB_1F_AT-3514 | AT | Included | Office S-1284
RDC_SB_1F_AT-3515 | AT | Included | S-1285 VP R&D
RDC_SB_1F_AT-3516 | AT | Included | Meeting Room S-1288
RDC_SB_1F_AT-3517 | AT | Included | Dressing Room S-1290
RDC_SB_1F_AT-3518 | AT | Included | Waiting Area S-1292
RDC_SB_1F_AT-3520 | AT | Included | Office S-1294
RDC_SB_1F_AT-3521 | AT | Included | Office S-1295
RDC_SB_1F_AT-3522 | AT | Included | Conference Room S-1296
RDC_SB_1F_AT-3523 | AT | Included | Office S-1299
RDC_SB_1F_AT-3524 | AT | Not Included | Normal Elec. S-1238
RDC_SB_1F_AT-0207 | AT | Included | Open Plan S-1293A
RDC_SB_1F_AT-0208 | AT | Included | Open Plan S-1293
RDC_SB_1F_AT-0201A | AT | Not Included | Policy Executive Director Office S-1240
RDC_SB_1F_AT-0201B | AT | Included | Open Plan S-1229
RDC_SB_1F_AT-0206 | AT | Not Included | Policy Executive Director Office S-1240
RDC_NB_1F_AT-7620 | AT | Included | Office N-1415
RDC_NB_1F_AT-7625 | AT | Included | Office N-1416
RDC_NB_1F_AT-7630 | AT | Included | Office 05 - 2 WKS- N-1407
RDC_NB_1F_AT-7635 | AT | Included | Office N-1418
RDC_NB_1F_AT-7640 | AT | Included | Office N-1419
RDC_NB_1F_AT-7645 | AT | Included | Exp. Workstation N-1420
RDC_NB_1F_AT-7650 | AT | Included | Office N-1421
RDC_NB_1F_AT-7655 | AT | Included | Office N-1422
RDC_NB_1F_AT-7660 | AT | Included | Office 05 - 2 WKS- N-1401
RDC_NB_1F_AT-7665 | AT | Not Included | Normal Elec. N-1425
RDC_NB_1F_AT-7670 | AT | Included | Office N-1426
RDC_NB_1F_AT-7675 | AT | Included | Office N-1428
RDC_NB_1F_AT-7680 | AT | Included | Conf N-1429
RDC_NB_1F_AT-7685 | AT | Included | Office N-1433
RDC_NB_1F_AT-7690 | AT | Included | Office N-1435
RDC_NB_1F_AT-7695 | AT | Included | Office N-1437
RDC_NB_1F_AT-7700 | AT | Not Included | Emer. Elec. N-1438
RDC_NB_1F_AT-7705 | AT | Included | Expansion WORKstation N-1442
RDC_NB_1F_AT-7710 | AT | Included | Office 05 - 24 WKS + N-1441 Room N-1442
RDC_NB_1F_AT-7840 | AT | Included | Conf N-1458
RDC_NB_1F_AT-7845 | AT | Included | Conf N-1459
RDC_NB_1F_AT-7850 | AT | Included | Office N-1459A
RDC_NB_1F_AT-7860 | AT | Included | Exp. Workstation N-1461
RDC_NB_1F_AT-7870 | AT | Included | Office N-1462
RDC_NB_1F_AT-7875 | AT | Included | Office N-1463
RDC_NB_1F_AT-7880 | AT | Included | Office N-1464
RDC_NB_1F_AT-7885 | AT | Included | Office N-1465
RDC_NB_1F_AT-7890 | AT | Included | Workstation N-1466
RDC_NB_1F_AT-7895 | AT | Included | Office N-1467
RDC_NB_1F_AT-7900 | AT | Included | Office N-1468
RDC_NB_1F_AT-7905 | AT | Included | Office N-1469
RDC_NB_1F_AT-7910 | AT | Included | Office N-1470
RDC_NB_1F_AT-7915 | AT | Included | Workstation N-1471
RDC_NB_1F_AT-7920 | AT | Included | Office N-1472
RDC_NB_1F_AT-7925 | AT | Included | Office N-1473
RDC_NB_1F_AT-7930 | AT | Included | Office N-1474
RDC_NB_1F_AT-7935 | AT | Included | Office N-1475
RDC_NB_1F_AT-7940 | AT | Included | Workstation N-1476
RDC_NB_1F_AT-7945 | AT | Included | Office N-1477
RDC_NB_1F_AT-7950 | AT | Included | Office N-1478
RDC_NB_1F_AT-7955 | AT | Included | Office N-1479
RDC_NB_1F_AT-7960 | AT | Included | Office N-1480
RDC_NB_1F_EV-7631 | EV | Included | Office 05 - 2 WKS- N-1407
RDC_NB_1F_EV-7646 | EV | Included | Exp. Workstation N-1420
RDC_NB_1F_EV-7661 | EV | Included | Office 05 - 2 WKS- N-1401
RDC_NB_1F_EV-7663 | EV | Not Included | IDF N-1424
RDC_NB_1F_EV-7711 | EV | Included | Workstation N-1442
RDC_NB_1F_EV-7712 | EV | Included | Workstation N-1442
RDC_NB_1F_EV-7861 | EV | Included | Office 05 - 9 WKS N-1461
RDC_NB_1F_EV-7916 | EV | Included | Office 05 - 8 WKS N-1471
RDC_NB_1F_CEV-7521 | CEV | Included | Isotope N-1404B
RDC_NB_1F_FEV-7522 | FEV | Included | Isotope N-1404B
RDC_NB_1F_CEV-7591 | CEV | Included | HY Room N-1404J
RDC_NB_1F_CEV-7581 | CEV | Included | TC3 N-1404H
RDC_NB_1F_FEV-7602 | FEV | Included | CELL BIO LABS N-1404K
RDC_NB_1F_CEV-7611 | CEV | Included | TC1 N-1404L
RDC_NB_1F_CEV-6831 | CEV | Included | SHARED COLD LAB N-1345G
RDC_NB_1F_CEV-7761 | CEV | Included | A/L N-1450D
RDC_NB_1F_CEV-7791 | CEV | Included | A/L N-1450G
RDC_NB_1F_FEV-7824 | FEV | Included | STEM/PCR Open Lab N-1450M
RDC_NB_2F_AT-4900 | AT | Not Included | Normal Electric N-2102
RDC_NB_2F_AT-4910 | AT | Not Included | Emergency Electr N-2103
RDC_NB_2F_EV-4920 | EV | Not Included | IDF N-2104
RDC_NB_2F_AT-5930 | AT | Included | Office 04 N-1170
RDC_NB_2F_AT-5940 | AT | Included | Office 05 - 8 WKS- N-1165
RDC_NB_2F_AT-6979 | AT | Not Included | Normal Elec. N-2107
RDC_NB_2F_AT-6980 | AT | Not Included | Emer. Elec. N-2108
RDC_NB_2F_EV-6981 | EV | Not Included | IDF N-2110
RDC_NB_2F_AT-7975 | AT | Not Included | Normal Elec. N-2111
RDC_NB_2F_AT-7980 | AT | Not Included | Emer. Elec. N-2112
Note on D174: Ahmad Sharaf Al Masri: Corrected from Emergency Elec. N-0333. B2.1 places AT-6205/EV-6206 (20.8 C) at Conference N-0331 and AT-6220/EV-6221 (18.1 C) at Emergency Elec. N-0333 - the two rows were swapped. Temperatures support it: 18.1 C is an electrical room, 20.8 C an occupied conference room.
Note on D176: Ahmad Sharaf Al Masri: Corrected from Conf N-0331 - swapped with row 1463. See note on D1463.
Note on D196: Ahmad Sharaf Al Masri: Corrected from Office N-0376. B2.1 places AT-6380 (22.9 C) at Workstation N-0378 and AT-6370 (23.3 C) at Office N-0376; N-0376 is now held by VAV6370 (row 1483).
Note on D228: Ahmad Sharaf Al Masri: Corrected from Office N-0427, which duplicated row 1518. B2.2 places AT-7145 (22.9 C) at Office N-0425 and AT-7155 (21.1 C) at Office N-0427.
Note on D230: Ahmad Sharaf Al Masri: Corrected from Office N-0428. B2.2 places AT-7165 (20.5 C) at Office N-0429; no room N-0428 appears on the Level 0 drawing.
Note on D234: Ahmad Sharaf Al Masri: Corrected from Office N-0426. B2.2 places AT-7185/EV-7186 at Emer. Elec. Room N-0433 - it reads 15.0 C, consistent with an electrical room, not an office.
Note on D279: Ahmad Sharaf Al Masri: Resolved by elimination, NOT read directly off a drawing. VAV0509 was the only unassigned VAV row in the South Building Level 1 block and NCIR Office S-1115 the only unassigned room in the AT-0510/0511/0512/0513/0514 group (S-1115A, S-1116, S-1117, S-1118, S-1119). B1.1 shows a sensor inside S-1115 labelled AT-0503, but A1.3 - the dedicated close-up of that core - places AT-0503 at Women S-1106B in a clean 0502/0503/0505 -> S-1105/S-1106B/S-1107B sequence. Most likely the B1.1 graphic is mislabelled and that sensor is AT-0509. VERIFY AGAINST THE BMS POINT LIST before relying on this row.
Note on D598: Ahmad Sharaf Al Masri: Corrected from Office N-1126. A2.2 labels N-1126 as CORRIDOR (the label appears twice along the corridor run); AT-5685/EV-5686 sit on that corridor, not in an office.
Note on D619: Ahmad Sharaf Al Masri: Corrected from Office N-1163, which duplicated row 1923. On A2.2 the bottom office band has exactly 17 tags for 17 rooms (AT-5860 to AT-5940), all accounted for; AT-5840 is the extra tag and sits above the band on the Corridor N-1150 run beside EV-5941. N-1163 is held by VAV5905 (row 1923).
Note on D745: Ahmad Sharaf Al Masri: Corrected from Flow Cyto N-1450C, which duplicated row 2034. B2.2 (Level 1) places VEV-7781 at iPS-TC N-1450F and VEV-7751 at Flow Cyto N-1450C.
Note on D782: Ahmad Sharaf Al Masri: Corrected from Corridor N-1138. On A2.2 FCU-5983 and FCU-5984 are adjacent boxes serving the JC N-1139 / IDF N-1140 pair; Corridor N-1138 is further west where AT-5745 sits.
Note on D783: Ahmad Sharaf Al Masri: Corrected from Corridor N-1138. On A2.2 FCU-5983 and FCU-5984 are adjacent boxes serving the JC N-1139 / IDF N-1140 pair; Corridor N-1138 is further west where AT-5745 sits.
Note on D828: Ahmad Sharaf Al Masri: Corrected from Stair 5 N-0STO5. B2.2 (Level 0) places FCU-7981 (20.9 C) at IDF N-0419; Stair 5 N-0ST05 is served by FCU-7993 (26.5 C on the same drawing), appended at row 2631.
Note on D829: Ahmad Sharaf Al Masri: Corrected from Service Corridor N-0344. B2.2 (Level 0) places FCU-7982 (21.2 C) at Mech/FPC N-0434, directly below FCU-7981.
Note on D837: Ahmad Sharaf Al Masri: From B1.1 (South Building Level 1): FCU-0502 (21.3 C) sits beside FPC S-1108 / Service Vestibule S-1105.
Note on D838: Ahmad Sharaf Al Masri: From B1.1 (South Building Level 1): FCU-0503 (20.9 C) sits beside Normal Elec. Room S-1107C / UPS S-1107D.
Note on D880: Ahmad Sharaf Al Masri: BMS screen shows the room name as "IDF-S-0271"; written as "IDF ROOM" for consistency with the other IDF entries.
Note on D882: Ahmad Sharaf Al Masri: BMS screen shows the room name as "STAIR-OST04"; written as "STAIR-04" for consistency with the other stair entries.
Note on D897: Ahmad Sharaf Al Masri: BMS screen shows no room number for FCU-8502/8503/8504/8505 (merged room-name cell).
Note on D1422: Ahmad Sharaf Al Masri: CONFLICT between drawings. A1.3 (close-up of the Level 1 core) places AT-0503 at Women S-1106B, forming a clean sequence with AT-0502 -> Vestibule S-1105 and AT-0505 -> Emergency Elec. S-1107B. B1.1 instead shows a sensor labelled AT-0503 reading 22.5 C inside NCIR Office S-1115. A1.3 was taken as authoritative; the S-1115 sensor is most likely AT-0509 (see note on D1569). Verify against the BMS point list.