## Asset Register
CONTROLLABLE ASSET REGISTRY
Tag No. | Equipment type | Included / not included | Room name as per drawings | Room entity | Note | Room name per VAV / FCU list (where different) | Room per BMS screen | BMS screen (image file) | BMS screen vs drawings | Why | Building
AHU12_0001 | AHU | Not Included | RF.001 ROOF | entity:HQ_RF.001_ROOF | [6 empty] | HQ
AHU12_0002 | AHU | Included | RF.001 ROOF | entity:HQ_RF.001_ROOF | [6 empty] | HQ
AHU12_0003 | AHU | Included | RF.001 ROOF | entity:HQ_RF.001_ROOF | [6 empty] | HQ
AHU12_0004 | AHU | Not Included | RF.001 ROOF | entity:HQ_RF.001_ROOF | [6 empty] | HQ
AHU12_0006 | AHU | Not Included | RF.001 ROOF | entity:HQ_RF.001_ROOF | [6 empty] | HQ
AHU12_0007 | AHU | Not Included | RF.001 ROOF | entity:HQ_RF.001_ROOF | [6 empty] | HQ
AHU12_0008 | AHU | Not Included | RF.001 ROOF | entity:HQ_RF.001_ROOF | [6 empty] | HQ
AHU12_0009 | AHU | Not Included | RF.001 ROOF | entity:HQ_RF.001_ROOF | [6 empty] | HQ
AHU12_0010 | AHU | Not Included | RF.001 ROOF | entity:HQ_RF.001_ROOF | [6 empty] | HQ
AHU2_0001 | AHU | Not Included | 2.302 SPA PLANT ROOM | entity:HQ_2.302_SPA_PLANTROOM | [6 empty] | HQ
AHU5_0001 | AHU | Not Included | 5.301 PLANT ROOM | entity:HQ_5.301_PLANT_ROOM | [6 empty] | HQ
AHU5_0002 | AHU | Not Included | 5.301 PLANT ROOM | entity:HQ_5.301_PLANT_ROOM | [6 empty] | HQ
AHU9_0001 | AHU | Not Included | 9.111 PLANT ROOM | entity:HQ_9.111_PLANT_ROOM | [6 empty] | HQ
AHU9_0002 | AHU | Not Included | 9.111 PLANT ROOM | entity:HQ_9.111_PLANT_ROOM | [6 empty] | HQ
AHU9_0003 | AHU | Not Included | 9.109 AHU ROOM | entity:HQ_9.109_AHU_ROOM | [6 empty] | HQ
AHUB_0001 | AHU | Included | B1.001 AHU 4 | entity:HQ_B1.001_AHU_4 | [6 empty] | HQ
AHUB_0002 | AHU | Included | B1.001 AHU 4 | entity:HQ_B1.001_AHU_4 | [6 empty] | HQ
AHUB_0003 | AHU | Included | B1.006 AHU 1 | entity:HQ_B1.006_AHU_1 | [6 empty] | HQ
AHUB_0004 | AHU | Included | B1.006 AHU 1 | entity:HQ_B1.006_AHU_1 | [6 empty] | HQ
AHUB_0005 | AHU | Included | B1.016 AHU 2 | entity:HQ_B1.016_AHU_2 | [6 empty] | HQ
AHUB_0006 | AHU | Included | B1.016 AHU 2 | entity:HQ_B1.016_AHU_2 | [6 empty] | HQ
AHUB_0007 | AHU | Included | B1.022 AHU 3 | entity:HQ_B1.022_AHU_3 | [6 empty] | HQ
AHUB_0008 | AHU | Included | B1.001 AHU 4 | entity:HQ_B1.001_AHU_4 | [6 empty] | HQ
AHUB_0009 | AHU | Included | B1.019 AHU | entity:HQ_B1.019_AHU | [6 empty] | HQ
AHUB_0010 | AHU | Included | B1.019 AHU | entity:HQ_B1.019_AHU | [6 empty] | HQ
AHUB_0011 | AHU | Included | B1.019 AHU | entity:HQ_B1.019_AHU | [6 empty] | HQ
FCU0001 | FCU | Not Included | B1.512 IDF ROOM | entity:HQ_B1.512_IDF_ROOM |  |  | B.512 IDF ROOM | HQ/Basment Floor/BF-2.jpg |  |  | HQ
FCU0002 | FCU | Not Included | B1.003 CONTROL ROOM | entity:HQ_B1.003_CONTROL_ROOM |  | SECURITY CONTROL RM B.003 | B.003 | HQ/Basment Floor/BF-1.jpg |  |  | HQ
FCU0003 | FCU | Included | B1.107 DOCK MASTER OFFICE | entity:HQ_B1.107_DOCK_MASTER_OFFICE |  | DOCKMASTER B.107 | B.107 DOCK MASTER OFFICE | HQ/Basment Floor/BF-2.jpg |  |  | HQ
FCU0004 | FCU | Not Included | B1.116 SHEIKHA LOBBY | entity:HQ_B1.113_SHEIKHA_LOBBY_SECURITY_ROOM |  | HH SECURITY ROOM B.113 |  |  |  |  | HQ
FCU0005 | FCU | Not Included | B1.003 CONTROL ROOM | entity:HQ_B1.401_MALE_TOILET |  | SECURITY CONTROL RM B.003 | B.401 | HQ/Basment Floor/BF-1.jpg |  |  | HQ
FCU0006 | FCU | Included | B1.122 SUPPORT SPACE FOOD STORAGE | entity:HQ_B1.122_SUPPORT_SPACE_FOOD_STORAGE |  | FOOD STORAGE B.122 | B.122 | HQ/Basment Floor/BF-2.jpg |  |  | HQ
FCU0007 | FCU | Included | B1.123 SUPPORT SPACE FOOD STORAGE | entity:HQ_B1.123_SUPPORT_SPACE_FOOD_STORAGE |  | FOOD STORAGE B.123 | B.123 | HQ/Basment Floor/BF-2.jpg |  |  | HQ
FCU0008 | FCU | Included | B1.015 SUPPORT SPACE LOADING | entity:HQ_B1.014_SUPPORT_SPACE_DRY_WASTE_STORAGE |  | SUPPORT SPACE LOADING B.015 | B.014 | HQ/Basment Floor/BF-2.jpg |  |  | HQ
FCU0009 | FCU | Included | B1.014 SUPPORT SPACE DRY WASTE STORAGE | entity:HQ_B1.014_SUPPORT_SPACE_DRY_WASTE_STORAGE |  | DRY WASTE STORAGE B.014 | B.014 | HQ/Basment Floor/BF-2.jpg |  |  | HQ
FCU0010 | FCU | Included | B1.124 WASTE BIN WASH UP | entity:HQ_B1.015_SUPPORT_SPACE_LOADING |  | WASTE BIN WASH UP B.124 |  | HQ/Basment Floor/BF-2.jpg |  |  | HQ
FCU0011 | FCU | Included | B1.117 CHAUFFER ROOM | entity:HQ_B1.117_CHAUFFEUR_ROOM |  |  | B.117 CHAUFFER ROOM | HQ/Basment Floor/BF-2.jpg |  |  | HQ
FCU0012 | FCU | Not Included | G.531 IDF ROOM | entity:HQ_G.531_IDF_ROOM |  |  | G.531 IDF ROOM | HQ/Ground Floor/GF-1.jpg |  |  | HQ
FCU0013 | FCU | Not Included | G.531 IDF ROOM | entity:HQ_G.531_IDF_ROOM |  |  | G.531 IDF ROOM | HQ/Ground Floor/GF-1.jpg |  |  | HQ
FCU0014 | FCU | Not Included | G.512 IDF ROOM | entity:HQ_G.512_IDF_ROOM |  |  | G.512 IDF ROOM | HQ/Ground Floor/GF-2.jpg |  |  | HQ
FCU0015 | FCU | Not Included | G.031 PR AND MARKET STAFF | entity:HQ_G.031_PR_&_MARKET_STAFF |  | PRINT COPY ROOM G.031 | G.031 COPY PRINT | HQ/Ground Floor/GF-2.jpg |  |  | HQ
FCU0016 | FCU | Included | G.017 COPY PRINT | entity:HQ_G.017_COPY_PRINT |  | PRINT COPY ROOM G.017 | G.017 COPY PRINT | HQ/Ground Floor/GF-1.jpg |  |  | HQ
FCU0017 | FCU | Not Included | G.005 EMERGENCY CONTROL CENTER | entity:HQ_G.005_EMERGENCY_CONTROL_CENTER |  | ESCAPE VESTIBULE 0.544 | G.005 CONTROL CENTER | HQ/Ground Floor/GF-1.jpg |  |  | HQ
FCU0018 | FCU | Not Included | G.511 VESTIBULE | entity:HQ_G.511_VESTIBULE |  | ESCAPE VESTIBULE G.511 | G.511 VESTIBULE | HQ/Ground Floor/GF-2.jpg |  |  | HQ
FCU0019 | FCU | Not Included | 1.531 IDF ROOM | entity:HQ_1.531_IDF_ROOM |  |  | 1.531 IDF ROOM | HQ/1F/FF-1.jpg |  |  | HQ
FCU0020 | FCU | Not Included | 1.531 IDF ROOM | entity:HQ_1.531_IDF_ROOM |  |  | 1.531 IDF ROOM | HQ/1F/FF-1.jpg |  |  | HQ
FCU0021 | FCU | Not Included | 1.512 IDF ROOM | entity:HQ_1.512_IDF_ROOM |  |  | 1.512 IDF ROOM | HQ/1F/FF-2.jpg |  |  | HQ
FCU0022 | FCU | Included | 1.112 PRINT COPY | entity:HQ_1.112_PRINT_COPY |  | PRINT COPY ROOM 1.112 | 1.112 PRINT COPY | HQ/1F/FF-2.jpg |  |  | HQ
FCU0023 | FCU | Not Included | 2.531 IDF ROOM | entity:HQ_2.531_IDF_ROOM |  |  | 2.531 IDF ROOM | HQ/2F/SF-1.jpg |  |  | HQ
FCU0024 | FCU | Not Included | 2.531 IDF ROOM | entity:HQ_2.531_IDF_ROOM |  |  | 2.531 IDF ROOM | HQ/2F/SF-1.jpg |  |  | HQ
FCU0025 | FCU | Not Included | 2.701 TERRACE | entity:HQ_2.701_TERRACE |  | BRIDGE BR-2 2.701 | 2.701 TERRACE | HQ/2F/SF-1.jpg |  |  | HQ
FCU0026 | FCU | Not Included | 2.701 TERRACE | entity:HQ_2.701_TERRACE |  | BRIDGE BR-2 2.701 | 2.701 TERRACE | HQ/2F/SF-1.jpg |  |  | HQ
FCU0027 | FCU | Not Included | 2.701 TERRACE | entity:HQ_2.701_TERRACE |  | BRIDGE BR-2 2.701 | 2.701 TERRACE | HQ/2F/SF-1.jpg |  |  | HQ
FCU0028 | FCU | Included | 2.103 PRINT COPY | entity:HQ_2.103_PRINT_COPY |  | PRINT COPY ROOM 2.103 | 2.103 PRINT COPY | HQ/2F/SF-1.jpg |  |  | HQ
FCU0029 | FCU | Not Included | 2.207 SPA LOUNGE BAR | entity:HQ_2.207_SPA_LOUNGE_BAR |  | LOUNGE 2.207 | 2.207 SPA LOUNGE BAR | HQ/2F/SF-1.jpg |  |  | HQ
FCU0030 | FCU | Not Included | 2.207 SPA LOUNGE BAR | entity:HQ_2.207_SPA_LOUNGE_BAR |  |  | 2.207 SPA LOUNGE BAR | HQ/2F/SF-1.jpg |  |  | HQ
FCU0031 | FCU | Not Included | 2.208 SPA FITNESS STUDIO | entity:HQ_2.208_SPA_FITNESS_DTUDIO |  | FITNESS STUDIO 2.208 | 2.208 SPA FITNESS STUDIO | HQ/2F/SF-2.jpg |  |  | HQ
FCU0032 | FCU | Not Included | 2.208 SPA FITNESS STUDIO | entity:HQ_2.208_SPA_FITNESS_DTUDIO |  |  | 2.208 SPA FITNESS STUDIO | HQ/2F/SF-2.jpg |  |  | HQ
FCU0033 | FCU | Not Included | 2.208 SPA FITNESS STUDIO | entity:HQ_2.208_SPA_FITNESS_DTUDIO |  |  | 2.208 SPA FITNESS STUDIO | HQ/2F/SF-2.jpg |  |  | HQ
FCU0034 | FCU | Not Included | 2.209 SPA OFFICE | entity:HQ_2.209_SPA_OFFICE |  | OFFICE 2.209 | 2.209 SPA OFFICE | HQ/2F/SF-2.jpg |  |  | HQ
FCU0035 | FCU | Not Included | 2.210 SPA STAFF WAITING AREA | entity:HQ_2.21_SPA_STAFF_WAITING_AREA |  | STAFF WAFTING ROOM 2.210 | 2.210 STAFF FEMALE WC | HQ/2F/SF-2.jpg |  |  | HQ
FCU0036 | FCU | Not Included | 2.211 SPA FEMALE BEAUTY SALON | entity:HQ_2.211_SPA_FEMALE_BEAUTY_SALON |  | BEAUTY SALON 2.211 | 2.211 SPA. FM BEAUTY SALON | HQ/2F/SF-2.jpg |  |  | HQ
FCU0037 | FCU | Not Included | 2.211 SPA FEMALE BEAUTY SALON | entity:HQ_2.211_SPA_FEMALE_BEAUTY_SALON |  |  | 2.211 SPA. FM BEAUTY SALON | HQ/2F/SF-2.jpg |  |  | HQ
FCU0038 | FCU | Not Included | 2.212 SPA FM TREATMENT 1 | entity:HQ_2.212_SPA_FM_TREATMENT_1 |  | TREATMENT ROOM 2.212 | 2.212 SPA FM TREATMENT | HQ/2F/SF-2.jpg |  |  | HQ
FCU0039 | FCU | Not Included | 2.213 SPA CHANGING ROOM | entity:HQ_2.213_SPA_CHANGING_ROOM |  | CHANGING ROOM 2.213 | 2.213 SPA CHANGING ROOM | HQ/2F/SF-2.jpg |  |  | HQ
FCU0040 | FCU | Not Included | 2.213 SPA CHANGING ROOM | entity:HQ_2.213_SPA_CHANGING_ROOM |  |  | 2.213 SPA CHANGING ROOM | HQ/2F/SF-2.jpg |  |  | HQ
FCU0041 | FCU | Not Included | 2.214 SPA FM TREATMENT 2 | entity:HQ_2.214_SPA_FM_TREATMENT_2 |  | TREATMENT ROOM 2.214 | 2.214 SPA FM TREATMENT | HQ/2F/SF-2.jpg |  |  | HQ
FCU0042 | FCU | Not Included | 2.215 SPA FM TREATMENT 3 | entity:HQ_2.215_SPA_FM_TREATMENT_3 |  | TREATMENT ROOM 2.215 | 2.215 SPA FM TREATMENT | HQ/2F/SF-2.jpg |  |  | HQ
FCU0043 | FCU | Not Included | 2.216 SPA FM RELAXATION | entity:HQ_2.216_SPA_FM_RELAXATION |  | RELAXATION 2.216 | 2.216 SPA FM RELAXATION | HQ/2F/SF-2.jpg |  |  | HQ
FCU0044 | FCU | Not Included | 2.216 SPA FM RELAXATION | entity:HQ_2.216_SPA_FM_RELAXATION |  |  | 2.216 SPA FM RELAXATION | HQ/2F/SF-2.jpg |  |  | HQ
FCU0045 | FCU | Not Included | 2.201 SPA MALE RELAXATION | entity:HQ_2.201_SPA_MALE_RELAXATION |  | RELAXATION 2.201 | 2.201 SPA MALE RELAXATION | HQ/2F/SF-2.jpg |  |  | HQ
FCU0046 | FCU | Not Included | 2.201 SPA MALE RELAXATION | entity:HQ_2.201_SPA_MALE_RELAXATION |  |  | 2.201 SPA MALE RELAXATION | HQ/2F/SF-1.jpg |  |  | HQ
FCU0047 | FCU | Not Included | 2.201 SPA MALE RELAXATION | entity:HQ_2.201_SPA_MALE_RELAXATION |  |  | 2.201 SPA MALE RELAXATION | HQ/2F/SF-1.jpg |  |  | HQ
FCU0048 | FCU | Not Included | 2.202 SPA MALE TREATMENT 3 | entity:HQ_2.202_SPA_MALE_TREATMENT_3 |  | TREATMENT ROOM 2.202 | 2.202 SPA MALE TREATMENT 3 | HQ/2F/SF-1.jpg |  |  | HQ
FCU0049 | FCU | Not Included | 2.203 SPA MALE TREATMENT 2 | entity:HQ_2.203_SPA_MALE_TREATMENT_2 |  | TREATMENT ROOM 2.203 | 2.203 SPA MALE TREATMENT 2 | HQ/2F/SF-1.jpg |  |  | HQ
FCU0050 | FCU | Not Included | 2.204 SPA MALE TREATMENT 1 | entity:HQ_2.204_SPA_MALE_TREATMENT_1 |  | TREATMENT ROOM 2.204 | 2.204 SPA MALE TREATMENT 1 | HQ/2F/SF-1.jpg |  |  | HQ
FCU0051 | FCU | Not Included | 2.205 SPA MALE CHANGING ROOM | entity:HQ_2.205_SPA_MALE_CHANGING_ROOM |  | CHANGING ROOM 2.205 | 2.205 MALE CHANGING ROOM | HQ/2F/SF-1.jpg |  |  | HQ
FCU0052 | FCU | Not Included | 2.205 SPA MALE CHANGING ROOM | entity:HQ_2.205_SPA_MALE_CHANGING_ROOM |  |  | 2.205 MALE CHANGING ROOM | HQ/2F/SF-1.jpg |  |  | HQ
FCU0053 | FCU | Not Included | 2.206 SPA ENTRANCE | entity:HQ_2.206_SPA_ENTRANCE |  | ENTRANCE 2.206 | 2.206 SPA ENTRANCE | HQ/2F/SF-1.jpg |  |  | HQ
FCU0054 | FCU | Not Included | 2.603 SPA LOBBY | entity:HQ_2.603_SPA_LOBBY |  | LOBBY 2.603 | 2.603 SPA LOBBY | HQ/2F/SF-2.jpg |  |  | HQ
FCU0055 | FCU | Not Included | 2.603 SPA LOBBY | entity:HQ_2.603_SPA_LOBBY |  |  | 2.603 SPA LOBBY | HQ/2F/SF-2.jpg |  |  | HQ
FCU0056 | FCU | Not Included | 2.512 MECHANICAL ROOM | entity:HQ_2.512_MECHANICAL_ROOM |  |  | 2.512 IDF ROOM | HQ/2F/SF-2.jpg |  |  | HQ
FCU0057 | FCU | Not Included | 2.302 SPA PLANT ROOM | entity:HQ_2.302_SPA_PLANTROOM |  | PLANT ROOM SE | 2.302 SPA PLANT ROOM | HQ/2F/SF-2.jpg |  |  | HQ
FCU0058 | FCU | Not Included | 2.311 SPA MALE HEAT EXP | entity:HQ_2.302_SPA_PLANTROOM |  | PLANT ROOM SE | 2.311 SPA MALE HEAT EXP | HQ/2F/SF-2.jpg |  |  | HQ
FCU0059 | FCU | Not Included | 3.531 IDF ROOM | entity:HQ_3.531_IDF_ROOM |  |  | 3.531 IDF ROOM | HQ/3F/3F-1.jpg |  |  | HQ
FCU0060 | FCU | Not Included | 3.531 IDF ROOM | entity:HQ_3.531_IDF_ROOM |  |  | NORTH WEST CORRIDOR | HQ/3F/3F-1.jpg |  |  | HQ
FCU0061 | FCU | Not Included | 3.512 IDF ROOM | entity:HQ_3.512_IDF_ROOM |  |  | 3.512 IDF ROOM | HQ/3F/3F-2.jpg |  |  | HQ
FCU0062 | FCU | Included | 3.203 COPY PRINT | entity:HQ_3.203_COPYPRINT |  | PRINT COPY ROOM 3.203 | 3.203 COPY/PRINT | HQ/3F/3F-1.jpg |  |  | HQ
FCU0063 | FCU | Included | 3.103 PRINT COPY | entity:HQ_3.103_PRINT_COPY |  | PRINT COPY ROOM 3.103 | 3.103 PRINT COPY | HQ/3F/3F-1.jpg |  |  | HQ
FCU0064 | FCU | Not Included | 3.630 CORRIDOR BRIDGE | entity:HQ_3.603_CORRIDOR_BRIDGE |  | BRIDGE BR-3B 3.63 | 3.63 CORRIDOR BRIDGE | HQ/3F/3F-1.jpg |  |  | HQ
FCU0065 | FCU | Not Included | 3.630 CORRIDOR BRIDGE | entity:HQ_3.603_CORRIDOR_BRIDGE |  | BRIDGE BR-3B 3.63 | 3.63 CORRIDOR BRIDGE | HQ/3F/3F-1.jpg |  |  | HQ
FCU0066 | FCU | Not Included | 3.630 CORRIDOR BRIDGE | entity:HQ_3.603_CORRIDOR_BRIDGE |  | BRIDGE BR-3B 3.63 | 3.63 CORRIDOR BRIDGE | HQ/3F/3F-1.jpg |  |  | HQ
FCU0067 | FCU | Included | 5.602 BRIDGE | entity:HQ_5.602_BRIDGE |  | BRIDGE BR-3 |  | HQ/3F/3F-2.jpg |  |  | HQ
FCU0068 | FCU | Included | 5.602 BRIDGE | entity:HQ_5.602_BRIDGE |  | BRIDGE BR-3 |  | HQ/3F/3F-2.jpg |  |  | HQ
FCU0069 | FCU | Included | 5.602 BRIDGE | entity:HQ_5.602_BRIDGE |  | BRIDGE BR-3 |  | HQ/3F/3F-2.jpg |  |  | HQ
FCU0070 | FCU | Included | 5.602 BRIDGE | entity:HQ_5.602_BRIDGE |  | BRIDGE BR-3 |  | HQ/3F/3F-2.jpg |  |  | HQ
FCU0071 | FCU | Not Included | 4.531 IDF ROOM | entity:HQ_4.531_IDF_ROOM |  |  |  | HQ/4F/4F-1.jpg |  |  | HQ
FCU0072 | FCU | Not Included | 4.105 PANTRY | entity:HQ_4.531_IDF_ROOM |  |  | 4.105 PANTRY | HQ/4F/4F-1.jpg |  |  | HQ
FCU0073 | FCU | Not Included | 4.512 IDF ROOM | entity:HQ_4.512_IDF_ROOM |  |  | 4.512 IDF ROOM | HQ/4F/4F-2.jpg |  |  | HQ
FCU0074 | FCU | Included | 4.202 PRINT COPY | entity:HQ_5.202_PRINT_COPY |  | PRINT COPY ROOM 04.202 | 4.202 PRINT COPY | HQ/4F/4F-2.jpg |  |  | HQ
FCU0075 | FCU | Not Included | 4.214 GSM ROOM | entity:HQ_5.214_GSM_ROOM |  | GSM ROOM 04.214 | 4.214 GSM ROOM | HQ/4F/4F-2.jpg |  |  | HQ
FCU0076 | FCU | Not Included | 4.214 GSM ROOM | entity:HQ_5.214_GSM_ROOM |  | GSM ROOM 04.214 | 4.214 GSM ROOM | HQ/4F/4F-2.jpg |  |  | HQ
FCU0077 | FCU | Included | 4.701 VP ADM TERRACE | entity:HQ_4.701_VP_ADM_TERRACE |  | BRIDGE BR-5 04.701 |  | HQ/4F/4F-1.jpg |  |  | HQ
FCU0078 | FCU | Included | 4.701 VP ADM TERRACE | entity:HQ_4.701_VP_ADM_TERRACE |  | BRIDGE BR-5 04.701 |  | HQ/4F/4F-1.jpg |  |  | HQ
FCU0079 | FCU | Included | 4.701 VP ADM TERRACE | entity:HQ_4.701_VP_ADM_TERRACE |  | BRIDGE BR-5 04.701 |  | HQ/4F/4F-1.jpg |  |  | HQ
FCU0080 | FCU | Included | 4.701 VP ADM TERRACE | entity:HQ_4.701_VP_ADM_TERRACE |  | BRIDGE BR-5 04.701 |  | HQ/4F/4F-1.jpg |  |  | HQ
FCU0081 | FCU | Not Included | 4.702 TERRACE | entity:HQ_4.702_TERRACE |  | BRIDGE BR-4 04.702 | 4.702 TERRACE | HQ/4F/4F-1.jpg |  |  | HQ
FCU0082 | FCU | Not Included | 4.703 TERRACE | entity:HQ_4.703_TERRACE |  | BRIDGE BR-4 04.703 | 4.703 TERRACE | HQ/4F/4F-1.jpg |  |  | HQ
FCU0083 | FCU | Not Included | 4.702 TERRACE | entity:HQ_4.702_TERRACE |  | BRIDGE BR-4 04.702 | 4.702 TERRACE | HQ/4F/4F-1.jpg |  |  | HQ
FCU0084 | FCU | Included | 4.110 PRINT COPY | entity:HQ_4.11_PRINT_COPY |  | PRINT COPY ROOM 04.110 | 4.110 PRINT COPY | HQ/4F/4F-2.jpg |  |  | HQ
FCU0085 | FCU | Not Included | 5.531 IDF ROOM | entity:HQ_5.531_IDF_ROOM |  |  | 5.531 IDF ROOM | HQ/5F/5F-1.jpg |  |  | HQ
FCU0086 | FCU | Not Included | 5.531 IDF ROOM | entity:HQ_5.531_IDF_ROOM |  |  | 5.531 IDF ROOM | HQ/5F/5F-1.jpg |  |  | HQ
FCU0087 | FCU | Not Included | 5.512 IDF ROOM | entity:HQ_5.512_IDF_ROOM |  |  | 5.512 IDF ROOM | HQ/5F/5F-2.jpg |  |  | HQ
FCU0088 | FCU | Included | 5.103 PRINT COPY | entity:HQ_5.103_PRINT_COPY |  | PRINT COPY ROOM 5.103 | 5.103 PRINT COPY | HQ/5F/5F-1.jpg |  |  | HQ
FCU0089 | FCU | Not Included | 6.604 BRIDGE CORRIDOR | entity:HQ_6.604_BRIDGE_CORRIDOR |  | BRIDGE BR-6 06.604 | BRIDGE 06.604 | HQ/5F/5F-1.jpg |  |  | HQ
FCU0090 | FCU | Not Included | 6.604 BRIDGE CORRIDOR | entity:HQ_6.604_BRIDGE_CORRIDOR |  | BRIDGE BR-6 06.604 | BRIDGE 06.604 | HQ/5F/5F-1.jpg |  |  | HQ
FCU0091 | FCU | Not Included | 6.604 BRIDGE CORRIDOR | entity:HQ_6.604_BRIDGE_CORRIDOR |  | BRIDGE BR-6 06.604 | BRIDGE 06.604 | HQ/5F/5F-1.jpg |  |  | HQ
FCU0092 | FCU | Not Included | 5.602 BRIDGE | entity:HQ_5.602_BRIDGE |  | BRIDGE BR-7 5.602 | BRIDGE 5.602 | HQ/5F/5F-1.jpg |  |  | HQ
FCU0093 | FCU | Not Included | 5.602 BRIDGE | entity:HQ_5.602_BRIDGE |  | BRIDGE BR-7 5.602 | BRIDGE 5.602 | HQ/5F/5F-1.jpg |  |  | HQ
FCU0094 | FCU | Not Included | 5.602 BRIDGE | entity:HQ_5.602_BRIDGE |  | BRIDGE BR-7 5.602 | BRIDGE 5.602 | HQ/5F/5F-1.jpg |  |  | HQ
FCU0095 | FCU | Not Included | 5.602 BRIDGE | entity:HQ_5.602_BRIDGE |  | BRIDGE BR-7 5.602 | BRIDGE 5.602 | HQ/5F/5F-1.jpg |  |  | HQ
FCU0096 | FCU | Not Included | 6.531 IDF ROOM | entity:HQ_6.531_IDF_ROOM |  |  | 6.531 IDF ROOM | HQ/6F/6F-1.jpg |  |  | HQ
FCU0097 | FCU |  | B1.512 IDF ROOM |  |  | IDF ROOM B.512 | B.512 IDF ROOM | HQ/Basment Floor/BF-2.jpg |  |  | HQ
FCU0098 | FCU | Not Included | 6.512 IDF ROOM | entity:HQ_6.512_IDF_ROOM |  |  | 6.512 IDF ROOM | HQ/6F/6F-2.jpg |  |  | HQ
FCU0099 | FCU | Not Included | 7.602 BRIDGE | entity:HQ_7.602_BRIDGE |  | BRIDGE BR-8 07.602 | BRIDGE 07.602 | HQ/6F/6F-2.jpg |  |  | HQ
FCU0100 | FCU | Not Included | 7.602 BRIDGE | entity:HQ_7.602_BRIDGE |  | BRIDGE BR-8 07.602 | BRIDGE 07.602 | HQ/6F/6F-2.jpg |  |  | HQ
FCU0101 | FCU | Not Included | 7.602 BRIDGE | entity:HQ_7.602_BRIDGE |  | BRIDGE BR-8 07.602 | BRIDGE 07.602 | HQ/6F/6F-2.jpg |  |  | HQ
FCU0102 | FCU | Included | 6.104 PRINT COPY | entity:HQ_6.104_PRINT_COPY |  | PRINT COPY ROOM 06.104 | 6.104 PRINT COPY | HQ/6F/6F-1.jpg |  |  | HQ
FCU0103 | FCU | Included | 6.208 PRINT COPY | entity:HQ_6.208_PRINT_COPY |  | PRINT COPY ROOM 06.208 | 6.208 PRINT COPY | HQ/6F/6F-2.jpg |  |  | HQ
FCU0104 | FCU | Not Included | 7.531 IDF ROOM | entity:HQ_7.531_IDF_ROOM |  |  | 7.531 IDF ROOM | HQ/7F/7F-1.jpg |  |  | HQ
FCU0105 | FCU | Not Included | 7.531 IDF ROOM | entity:HQ_7.531_IDF_ROOM |  |  | 7.531 IDF ROOM | HQ/7F/7F-1.jpg |  |  | HQ
FCU0106 | FCU | Not Included | 7.512 IDF ROOM | entity:HQ_7.512_IDF_ROOM |  |  | 7.512 IDF ROOM | HQ/7F/7F-2.jpg |  |  | HQ
FCU0107 | FCU | Included | 7.101 PRINT COPY | entity:HQ_7.101_PRINT_COPY |  | PRINT COPY ROOM 7.101 | 7.101 PRINT COPY | HQ/7F/7F-1.jpg |  |  | HQ
FCU0108 | FCU | Included | 7.104 PRINT COPY | entity:HQ_7.104_PRINT_COPY |  | PRINT COPY ROOM 7.104 | 7.104 PRINT COPY | HQ/7F/7F-1.jpg |  |  | HQ
FCU0109 | FCU | Not Included | 8.512 IDF ROOM | entity:HQ_8.512_IDF_ROOM |  |  | 8.512 IDF ROOM | HQ/8F/8F.jpg |  |  | HQ
FCU0110 | FCU | Not Included | 9.531 IDF ROOM | entity:HQ_9.531_IDF_ROOM |  |  | 9.532 | HQ/9F/9F-1.jpg |  |  | HQ
FCU0111 | FCU | Not Included | G.512 IDF ROOM | entity:HQ_G.512_IDF_ROOM |  |  | G.512 IDF ROOM | HQ/Ground Floor/GF-2.jpg |  |  | HQ
FCU0112 | FCU | Not Included | 9.512 IDF ROOM | entity:HQ_9.512_IDF_ROOM |  |  | 9.512 IDF ROOM | HQ/9F/9F-2.jpg |  |  | HQ
FCU0113 | FCU | Not Included | 10.531 IDF ROOM | entity:HQ_10.531_IDF_ROOM |  |  | 10.531 IDF ROOM | HQ/10F/10F-1.jpg |  |  | HQ
FCU0114 | FCU | Not Included | 1.114 STAFF LOUNGE STORAGE | entity:HQ_1.114_STAFF_LOUNGE_STORAGE |  | IDF ROOM 01.512 | 1.114 STAFF LOUNGE STORAGE | HQ/1F/FF-2.jpg |  |  | HQ
FCU0115 | FCU | Not Included | 10.512 IDF ROOM | entity:HQ_10.512_IDF_ROOM |  |  | 10.512 IDF ROOM | HQ/10F/10F-2.jpg |  |  | HQ
FCU0116 | FCU | Included | 10.038 PRINT COPY | entity:HQ_10.038_PRINT_COPY |  | PRINT COPY ROOM 10.038 | 10.038 PRINT COPY | HQ/10F/10F-1.jpg |  |  | HQ
FCU0117 | FCU | Included | 10.014 PRINT COPY | entity:HQ_10.014_PRINT_COPY |  | PRINT COPY ROOM 10.014 | 10.014 PRINT COPY | HQ/10F/10F-1.jpg |  |  | HQ
FCU0118 | FCU | Included | 10.111 AV ROOM | entity:HQ_10.111_AV_ROOM |  | AV ROOM 10.111 | 10.112 AV ROOM | HQ/10F/10F-2.jpg |  |  | HQ
FCU0119 | FCU | Not Included | 11.531 IDF ROOM | entity:HQ_11.531_IDF_ROOM |  |  | 11.531 IDF ROOM | HQ/11F/11F-1.jpg |  |  | HQ
FCU0120 | FCU | Not Included | 11.531 IDF ROOM | entity:HQ_11.531_IDF_ROOM |  |  | 11.531 IDF ROOM | HQ/11F/11F-1.jpg |  |  | HQ
FCU0121 | FCU | Included | 11.110 ELECTRIC CLOSET | entity:HQ_11.11_ELECTRICAL_CABINET |  | AV ROOM 11.101 | 11.110 ELECTRIC CLOSET | HQ/11F/11F-1.jpg |  |  | HQ
FCU0122 | FCU | Not Included | 11.108 PRINT COPY ROOM | entity:HQ_11.106_ELECTRICAL_ROOM |  |  | 11.108 PRINT COPY ROOM | HQ/11F/11F-2.jpg |  |  | HQ
FCU0123 | FCU | Included | 11.106 MCC ELEC ROOM | entity:HQ_11.108_PRINT_COPY |  |  | 11.106 MCC/ELEC ROOM | HQ/11F/11F-2.jpg |  |  | HQ
FCU0124 | FCU | Not Included | 11.107 AV IT | entity:HQ_11.107_AV_IT |  |  | 11.107 AV ROOM | HQ/11F/11F-2.jpg |  |  | HQ
FCU0125 | FCU | Not Included | 11.512 IDF ROOM | entity:HQ_11.512_IDF_ROOM |  |  | 11.512 IDF ROOM | HQ/11F/11F-2.jpg |  |  | HQ
FCU0126 | FCU | Not Included | 12.002 MCC CLOSET | entity:HQ_12.002_MCC_CLOSET |  | MCC HOUSING 01 12.002 | 12.002 MCC CLOSET | HQ/RF/RF-2.jpg |  |  | HQ
FCU0127 | FCU | Not Included | 12.002 MCC CLOSET | entity:HQ_12.002_MCC_CLOSET |  | MCC HOUSING 02 12.002 | 12.002 MCC CLOSET | HQ/RF/RF-2.jpg |  |  | HQ
FCU0128 | FCU | Not Included | 12.003 MCC CLOSET | entity:HQ_12.003_MCC_CLOSET |  | MCC HOUSING 03 12.003 | 12.003 MCC CLOSET | HQ/RF/RF-1.jpg |  |  | HQ
FCU0129 | FCU | Not Included | 12.003 MCC CLOSET | entity:HQ_12.003_MCC_CLOSET |  | MCC HOUSING 04 12.003 | 12.003 MCC CLOSET | HQ/RF/RF-1.jpg |  |  | HQ
FCU0130 | FCU | Not Included | 12.004 MCC CLOSET | entity:HQ_12.004_MCC_CLOSET |  | MCC HOUSING 05 12.004 | 12.004 MCC CLOSET | HQ/RF/RF-1.jpg |  |  | HQ
FCU0131 | FCU | Not Included | RF.002 ROOF PLANT WALKWAY | entity:HQ_RF.002_ROOF_PLANT_WALKWAY |  | CSRR & VSD ROOM 12 | ROOF PLANT / WALKWAY (NEAR CSRR-0008) | HQ/RF/RF-1.jpg |  |  | HQ
FCU0132 | FCU | Not Included | 9.112 AV ROOM IN VISITOR CENTER | entity:HQ_9.101_VISITORS_CENTER |  | AV ROOM IN VISITOR CENTER 09.112 | SOUTH WEST CORRIDOR | HQ/9F/9F-1.jpg |  |  | HQ
VAV0001 | VAV | Not Included | B1.103 STAFF LOBBY | entity:HQ_B1.004_STAFF_ENTRANCE |  | LOBBY B.103 | B.004 STAFF ENTRANCE | HQ/Basment Floor/BF-1.jpg |  |  | HQ
VAV0002 | VAV | Not Included | B1.103 STAFF LOBBY | entity:HQ_B1.103_STAFF_LOBBY |  |  | B.103 STAFF LOBBY | HQ/Basment Floor/BF-1.jpg |  |  | HQ
VAV0003 | VAV | Not Included | B1.103 STAFF LOBBY | entity:HQ_B1.103_STAFF_LOBBY |  |  | B.103 STAFF LOBBY | HQ/Basment Floor/BF-1.jpg |  |  | HQ
VAV0004 | VAV | Included | B1.110 MALE BREAK ROOM | entity:HQ_B1.110_SUPPORT_SPACE_MAIL_ROOM |  | MALE BREAK ROOM B.110 | B.116 LOBBY | HQ/Basment Floor/BF-2.jpg |  |  | HQ
VAV0005 | VAV | Not Included | B1.116 SHEIKHA LOBBY | entity:HQ_B1.116_SHEIKHA_LOBBY |  | HH LOBBY B.116 | B.116 LOBBY | HQ/Basment Floor/BF-2.jpg |  |  | HQ
VAV0006 | VAV | Not Included | B1.116 SHEIKHA LOBBY | entity:HQ_B1.116_SHEIKHA_LOBBY |  |  | B.116 LOBBY | HQ/Basment Floor/BF-2.jpg |  |  | HQ
VAV0007 | VAV | Not Included | G.008 CONTROL ROOM | entity:HQ_G.008_CONTROL_ROOM |  |  | G.008 CONTROL ROOM | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0008 | VAV | Not Included | G.009 PR AND MARKET MANAGER | entity:HQ_G.009_PR_&_MARKET_MANAGER |  |  | G.009 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0009 | VAV | Included | G.010 PR AND MARKET STAFF | entity:HQ_G.010_PR_&_MARKET_STAFF |  |  | G.010 PR & MARKET STAFF | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0011 | VAV | Included | G.011 PR AND MARKET MANAGER | entity:HQ_G.011_PR_&_MARKET_MANAGER |  | PR & MARKET MANAGER G.011 | G.011 PR & MARKET MANAG. | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0012 | VAV | Included | G.012 PR AND MARKET STAFF | entity:HQ_G.012_PR_&_MARKET_STAFF |  |  | G.012 PR & MARKET STAFF | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0013 | VAV | Not Included | G.014 VISITOR CENT OFFICE | entity:HQ_G.014_VISITOR_CENT_OFFICE |  | VISITORS CENT OFFICE G.014 | G.014 VISITOR OFFICE | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0014 | VAV | Included | G.015 PR AND MARKET STAFF | entity:HQ_G.015_PR_&_MARKET_STAFF |  |  | G.015 PR & MARKET STAFF | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0015 | VAV | Included | G.018 PR AND MARKET STAFF | entity:HQ_G.018_PR_&_MARKET_STAFF |  | PR & MARKET STAFF G.018 | G.018 PR & MARKET STAFF | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0016 | VAV | Included | G.019 PR AND MARKET STAFF | entity:HQ_G.019_PR_&_MARKET_STAFF |  | PR & MARKET STAFF G.019 | G.019 PR & MARKET STAFF | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0017 | VAV | Included | G.020 PR AND MARKET STAFF | entity:HQ_G.020_PR_&_MARKET_STAFF |  | PR & MARKET STAFF G.020 | G.020 PR & MARKET STAFF | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0018 | VAV | Included | G.021 PR AND MARKET STAFF | entity:HQ_G.021_PR_&_MARKET_STAFF |  | PR & MARKET STAFF G.021 | G.021 PR & MARKET STAFF | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0019 | VAV | Included | G.022 PR AND MARKET SECRETARY | entity:HQ_G.022_PR_&_MARKET!_SECRETARY |  | PR & MARKET SECRETARY G.022 | G.022 PR & MARKET SECRETARY | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0020 | VAV | Included | G.023 PR AND MARKET STAFF | entity:HQ_G.023_PR_&_MARKET_STAFF |  |  | G.023 PR & MARKET STAFF | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0021 | VAV | Not Included | G.601 CORRIDOR | entity:HQ_G.601_CORRIDOR |  | CORRIDOR NE | G.601 CORRIDOR | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0022 | VAV | Not Included | G.601 CORRIDOR | entity:HQ_G.601_CORRIDOR |  |  | G.601 CORRIDOR | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0023 | VAV | Included | G.105 SHOP | entity:HQ_G.105_SHOP |  |  | G.105 SHOP | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0024 | VAV | Not Included | G.104 LOBBY | entity:HQ_G.104_LOBBY |  | LOBBY NW | G.104 LOBBY | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0025 | VAV | Not Included | G.104 LOBBY | entity:HQ_G.104_LOBBY |  | AUDITORIUM STAIRS LOBBY G.006 | G.104 LOBBY | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0026 | VAV | Not Included | G.103 BMS | entity:HQ_G.103_BMS |  |  | G.103 BMS ROOM | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0027 | VAV | Not Included | G.004 PR AND MARKET MANAGER | entity:HQ_G.004_PR_&_MARKET_MANAGER |  |  | G.004 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0028 | VAV | Not Included | G.003 PR AND MARKET MANAGER | entity:HQ_G.003_PR_&_MARKET_MANAGER |  |  | G.003 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0029 | VAV | Not Included | G.002 PR AND MARKET MANAGER | entity:HQ_G.002_PR_&_MARKET_MANAGER |  |  | G.002 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0030 | VAV | Not Included | G.400 CORRIDOR SOUTH WEST SW | entity:HQ_G.400_CORRIDOR |  | CORRIDOR SOUTH WEST SW |  | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0031 | VAV | Included | G.001 PR AND MARKET STAFF | entity:HQ_G.001_PR_&_MARKET_STAFF |  |  | G.001 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0032 | VAV | Included | G.038 PR AND MARKET STAFF | entity:HQ_G.038_PR_&_MARKET_STAFF |  |  | G.038 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0033 | VAV | Included | G.037 PR AND MARKET STAFF | entity:HQ_G.037_PR_&_MARKET_STAFF |  |  | G.037 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0034 | VAV | Included | G.036 PR AND MARKET STAFF | entity:HQ_G.036_PR_&_MARKET_STAFF |  |  | G.036 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0035 | VAV | Included | G.035 PR AND MARKET STAFF | entity:HQ_G.035_PR_&_MARKET_STAFF |  |  | G.035 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0036 | VAV | Included | G.034 PR AND MARKET STAFF | entity:HQ_G.034_PR_&_MARKET_STAFF |  |  | G.034 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0037 | VAV | Included | G.033 PR AND MARKET STAFF | entity:HQ_G.033_PR_&_MARKET_STAFF |  |  | G.033 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0038 | VAV | Included | G.032 PR AND MARKET STAFF | entity:HQ_G.032_PR_&_MARKET_STAFF |  |  | G.032 | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0039 | VAV | Included | G.030 PR AND MARKET STAFF | entity:HQ_G.030_STAFF |  | PR & MARKET STAFF G.030 | G.030 PR & MARKET STAFF | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0040 | VAV | Included | G.029 PR AND MARKET STAFF | entity:HQ_G.029_PR_&_MARKET_STAFF |  | PR & MARKET STAFF G.029 | G.029 PR & MARKET STAFF | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0041 | VAV | Included | G.029 PR AND MARKET STAFF | entity:HQ_G.029_PR_&_MARKET_STAFF |  |  | G.029 PR & MARKET STAFF | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0042 | VAV | Not Included | G.028 PR AND MARKET DIRECTOR ENSUIT | entity:HQ_G.028_PR_&_MARKET_DIRECTOR_ENSUIT |  | PR & MARKET DIR ENSUIT G.028 | G.028 PR & MARKET DIR. ENSUIT | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0043 | VAV | Included | G.026 FINANCE CASHIER | entity:HQ_G.026_FINANCE_CASHIER |  |  | G.026 FINANCE CASHIER | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0044 | VAV | Not Included | G.025 VIP LOUNGE | entity:HQ_G.025_VIP_LOUNGE |  |  | G.025 VIP LOUNGE | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0045 | VAV | Not Included | G.107 E TOWER LOBBY | entity:HQ_G.107_E-TOWER_LOBBY |  | E-TOWER LOBBY SE | G.107 E-TOWER LOBBY | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0046 | VAV | Not Included | G.602 CORRIDOR SOUTH EAST | entity:HQ_G.602_CORRIDOR_(SOUTH_EAST) |  |  | CORRIDOR | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0047 | VAV | Not Included | G.603 CORRIDOR SOUTH EAST | entity:HQ_G.603_CORRIDOR_(SOUTH_EAST) |  |  | SOUTH EAST CORRIDOR | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0048 | VAV | Included | G.101 CONFERENCE ROOM | entity:HQ_G.101_CONFERENCE_ROOM |  |  | G.101 CONFERENCE ROOM | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0049 | VAV | Included | G.101 CONFERENCE ROOM | entity:HQ_G.101_CONFERENCE_ROOM |  |  | G.101 CONFERENCE ROOM | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0050 | VAV | Included | G.101 CONFERENCE ROOM | entity:HQ_G.101_CONFERENCE_ROOM |  |  | G.101 CONFERENCE ROOM | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0051 | VAV | Included | G.101 CONFERENCE ROOM | entity:HQ_G.101_CONFERENCE_ROOM |  |  | G.101 CONFERENCE ROOM | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0052 | VAV | Included | G.108 CONSULTANT SPACE TRAINEES | entity:HQ_G.108_CONSULTANT_SPACE_TRAINEES |  | CONSULTANT SPACE TRAINEES G.108 | G.108 CONSULTANT SPACE | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0053 | VAV | Included | G.108 CONSULTANT SPACE TRAINEES | entity:HQ_G.108_CONSULTANT_SPACE_TRAINEES |  |  |  | HQ/Ground Floor/GF-2.jpg |  |  | HQ
VAV0054 | VAV | Not Included | 1.011 FINANCE MANAGER | entity:HQ_1.011_FINANCE_MANAGER |  |  | 1.011 FINANCE MANAGER | HQ/1F/FF-2.jpg |  |  | HQ
VAV0055 | VAV | Not Included | 1.012 FINANCE MANAGER | entity:HQ_1.012_FINANCE_MANAGER |  |  | 1.012 FINANCE MANAGER | HQ/1F/FF-2.jpg |  |  | HQ
VAV0056 | VAV | Not Included | 1.013 FINANCE MANAGER | entity:HQ_1.013_FINANCE_MANAGER |  |  | 1.013 FINANCE MANAGER | HQ/1F/FF-2.jpg |  |  | HQ
VAV0057 | VAV | Included | 1.014 FINANCE PROFSTAFF | entity:HQ_1.014_FINANCE_PROFSTAFF |  | FINANCE PROFSTAFF 1.014 | 1.014 FINANCE STAFF | HQ/1F/FF-2.jpg |  |  | HQ
VAV0058 | VAV | Included | 1.015 FINANCE PROFSTAFF | entity:HQ_1.015_FINANCE_PROFSTAFF |  | FINANCE PROFSTAFF 1.015 | 1.015 FINANCE STAFF | HQ/1F/FF-2.jpg |  |  | HQ
VAV0059 | VAV | Included | 1.016 FINANCE SECRETARY | entity:HQ_1.016_FINANCE_SECRETARY |  |  | 1.016 FINANCE SECRETARY | HQ/1F/FF-2.jpg |  |  | HQ
VAV0060 | VAV | Not Included | 1.017 FINANCE DIRECTOR ENSUIT | entity:HQ_1.017_FINANCE_DIRECTOR_ENSUIT |  | FINANCE DIRENSUIT 1.017 | 1.017 FINANCE DIRECTOR | HQ/1F/FF-2.jpg |  |  | HQ
VAV0061 | VAV | Not Included | 1.018 FINANCE MANAGER | entity:HQ_1.018_FINANCE_MANAGER |  |  | 1.018 FINANCE MANAGER | HQ/1F/FF-2.jpg |  |  | HQ
VAV0062 | VAV | Not Included | 1.019 FINANCE MANAGER | entity:HQ_1.019_FINANCE_MANAGER |  |  | 1.019 FINANCE MANAGER | HQ/1F/FF-2.jpg |  |  | HQ
VAV0063 | VAV | Not Included | 1.020 FINANCE MANAGER | entity:HQ_1.02_FINANCE_MANAGER |  |  | 1.020 FINANCE MANAGER | HQ/1F/FF-2.jpg |  |  | HQ
VAV0064 | VAV | Included | 1.021 FINANCE SECRETARY | entity:HQ_1.021_FINANCE_SECRETARY |  | FINANCE SECRETARY 1.021 | 1.021 FINANCE SEC | HQ/1F/FF-2.jpg |  |  | HQ
VAV0065 | VAV | Included | 1.022 FINANCE SECRETARY | entity:HQ_1.022_FINANCE_SECRETARY |  | FINANCE SECRETARY 1.022 | 1.022 FINANCE SEC | HQ/1F/FF-1.jpg |  |  | HQ
VAV0066 | VAV | Included | 1.023 FINANCE AUDIT | entity:HQ_1.023_FINANCE_AUDITOR |  | FINANCE AUDITOR 1.023 | 1.023 FINANCE AUDIT | HQ/1F/FF-1.jpg |  |  | HQ
VAV0067 | VAV | Included | 1.024 FINANCE AUDIT | entity:HQ_1.024_FINANCE_AUDITOR |  | FINANCE AUDITOR 1.024 | 1.024 FINANCE AUDIT | HQ/1F/FF-1.jpg |  |  | HQ
VAV0068 | VAV | Included | 1.025 FINANCE PROFSTAFF | entity:HQ_1.025_FINANCE_PROFSTAFF |  | FINANCE PROFSTAFF 1.025 | 1.025 FINANCE STAFF | HQ/1F/FF-1.jpg |  |  | HQ
VAV0069 | VAV | Included | 1.026 FINANCE PROFSTAFF | entity:HQ_1.026_FINANCE_PROFSTAFF |  | FINANCE PROFSTAFF 1.026 | 1.026 FINANCE STAFF | HQ/1F/FF-1.jpg |  |  | HQ
VAV0070 | VAV | Not Included | 1.027 FINANCE AUDITOR | entity:HQ_1.027_FINANCE_AUDITOR |  | FINANCE AUDITOR 1.027 | 1.027 FINANCE MANAGER | HQ/1F/FF-1.jpg |  |  | HQ
VAV0071 | VAV | Not Included | 1.028 FINANCE MANAGER | entity:HQ_1.028_FINANCE_MANAGER |  |  | 1.028 FINANCE MANAGER | HQ/1F/FF-1.jpg |  |  | HQ
VAV0072 | VAV | Not Included | 1.029 FINANCE MANAGER | entity:HQ_1.029_FINANCE_MANAGER |  |  | 1.029 FINANCE MANAGER | HQ/1F/FF-1.jpg |  |  | HQ
VAV0073 | VAV | Included | 1.001 FINANCE CLERICAL SECRETARIES | entity:HQ_1.001_FINANCE_CLERICAL_SECRETARIES |  | FINANCE CLERICAL SEC 1.001 | 1.001 FINANCE SECRETARY | HQ/1F/FF-1.jpg |  |  | HQ
VAV0074 | VAV | Not Included | 1.002 FINANCE MANAGER | entity:HQ_1.002_FINANCE_MANAGERS |  | FINANCE MANAGERS 1.002 | 1.002 FINANCE MANAGER | HQ/1F/FF-1.jpg |  |  | HQ
VAV0075 | VAV | Not Included | 1.003 FINANCE MANAGER | entity:HQ_1.003_FINANCE_MANAGER |  |  | 1.003 FINANCE MANAGER | HQ/1F/FF-1.jpg |  |  | HQ
VAV0076 | VAV | Not Included | 1.004 FINANCE MANAGER | entity:HQ_1.004_FINANCE_MANAGER |  |  | 1.004 FINANCE MANAGER | HQ/1F/FF-1.jpg |  |  | HQ
VAV0077 | VAV | Included | 1.005 FINANCE SECRETARY | entity:HQ_1.005_FINANCE_SECRETARY |  |  | 1.005 FINANCE SECRETARY | HQ/1F/FF-1.jpg |  |  | HQ
VAV0078 | VAV | Included | 1.006 FINANCE PROFSTAFF | entity:HQ_1.006_FINANCE_PROFSTAFF |  | FINANCE PROFSTAFF 1.006 | 1.006 FINANCE STAFF | HQ/1F/FF-1.jpg |  |  | HQ
VAV0079 | VAV | Included | 1.007 FINANCE CLERICAL PROFSTAFF | entity:HQ_1.007_FINANCE_CLERICAL_PROFSTAFF |  | FINANCE CLERICAL PROFSTAFF 1.007 | 1.007 FINANCE STAFF | HQ/1F/FF-1.jpg |  |  | HQ
VAV0080 | VAV | Not Included | 1.401 GROUND FLOOR VIP ENTRANCE | entity:HQ_1.401_GROUND_FLOOR_VIP_ENTRANCE |  | VOID AREA, ROOM UNIT LOCATED @LVL 1 NORTH WEST AREA G.401 | 1.401 GROUND FLOOR VIP ENTRANCE | HQ/1F/FF-1.jpg |  |  | HQ
VAV0081 | VAV | Not Included | 1.401 GROUND FLOOR VIP ENTRANCE | entity:HQ_1.401_GROUND_FLOOR_VIP_ENTRANCE |  |  | 1.401 GROUND FLOOR VIP ENTRANCE | HQ/1F/FF-1.jpg |  |  | HQ
VAV0082 | VAV | Not Included | 1.401 GROUND FLOOR VIP ENTRANCE | entity:HQ_1.401_GROUND_FLOOR_VIP_ENTRANCE |  |  | 1.401 GROUND FLOOR VIP ENTRANCE | HQ/1F/FF-1.jpg |  |  | HQ
VAV0083 | VAV | Not Included | 1.101 STAFF LOUNGE | entity:HQ_1.101_STAFF_LOUNGE |  |  | 1.101 STAFF LOUNGE | HQ/1F/FF-1.jpg |  |  | HQ
VAV0084 | VAV | Not Included | 1.101 STAFF LOUNGE | entity:HQ_1.101_STAFF_LOUNGE |  |  | 1.101 STAFF LOUNGE | HQ/1F/FF-1.jpg |  |  | HQ
VAV0085 | VAV | Not Included | 1.101 STAFF LOUNGE | entity:HQ_1.101_STAFF_LOUNGE |  |  | 1.101 STAFF LOUNGE | HQ/1F/FF-1.jpg |  |  | HQ
VAV0086 | VAV | Not Included | 1.101 STAFF LOUNGE | entity:HQ_1.101_STAFF_LOUNGE |  |  | 1.101 STAFF LOUNGE | HQ/1F/FF-1.jpg |  |  | HQ
VAV0087 | VAV | Included | 1.108 FINANCE MEETING ROOM | entity:HQ_1.108_FINANCE_MEETING_ROOM |  | FINANCE METTING ROOM 1.108 | 1.108 FINANCE MEETING ROOM | HQ/1F/FF-1.jpg |  |  | HQ
VAV0088 | VAV | Included | 1.109 CONSULTANT SPACE TRAINEES | entity:HQ_1.109_CONSULTANT_SPACE_TRAINEES |  | COLSULTANT SPACE TRAINEES 1.109 | 1.109 CONSULTANT SPACE | HQ/1F/FF-1.jpg |  |  | HQ
VAV0089 | VAV | Included | 1.109 CONSULTANT SPACE TRAINEES | entity:HQ_1.109_CONSULTANT_SPACE_TRAINEES |  |  | 1.109 CONSULTANT SPACE | HQ/1F/FF-2.jpg |  |  | HQ
VAV0090 | VAV | Included | G.104 LOBBY | entity:HQ_1.11_CONFERENCE_ROOM |  |  | LOBBY (GROUND FLOOR) | HQ/1F/FF-2.jpg |  |  | HQ
VAV0091 | VAV | Not Included | 1.105 PRAYER ROOM | entity:HQ_1.105_PRAYER_ROOM |  | PRAYERS ROOM 1.105 | 1.105 PRAYER ROOM | HQ/1F/FF-1.jpg |  |  | HQ
VAV0092 | VAV | Included | 1.106 FINANCE CASHIER | entity:HQ_1.106_FINANCE_CASHIER |  |  | 1.117 FINANCE AUDITOR | HQ/1F/FF-1.jpg |  |  | HQ
VAV0093 | VAV | Included | 1.116 FINANCE SECURE ROOM | entity:HQ_1.116_FINANCE_SECURE_ROOM |  | FINANCE SECURE ROOM 1.116 | 1.106 FINANCE ROOM | HQ/1F/FF-1.jpg |  |  | HQ
VAV0094 | VAV | Included | 1.117 FINANCE AUDITOR | entity:HQ_1.117_FINANCE_AUDITOR |  |  | 1.116 FINANCE CASHIER | HQ/1F/FF-1.jpg |  |  | HQ
VAV0095 | VAV | Included | 1.115 FINANCE AUDITOR | entity:HQ_1.115_FINANCE_AUDITOR |  |  | 1.115 FINANCE AUDITOR | HQ/1F/FF-1.jpg |  |  | HQ
VAV0096 | VAV | Not Included | 1.101 STAFF LOUNGE | entity:HQ_1.101_STAFF_LOUNGE |  | CORRIDOR SOUTH WEST SW | 1.101 STAFF LOUNGE | HQ/1F/FF-1.jpg |  |  | HQ
VAV0097 | VAV | Not Included | 1.602 CORRIDOR | entity:HQ_1.602_CORRIDOR |  | CORRIDOR SOUTH WEST 1.602 | 1.602 CORRIDOR | HQ/1F/FF-1.jpg |  |  | HQ
VAV0098 | VAV | Not Included | 1.602 CORRIDOR | entity:HQ_1.602_CORRIDOR |  | CORRIDOR SOUTH EAST SE | 1.602 CORRIDOR | HQ/1F/FF-2.jpg |  |  | HQ
VAV0099 | VAV | Included | 1.601 CORRIDOR | entity:HQ_1.601_CORRIDOR |  | CORRIDOR SOUTH EAST | SOUTH EAST ZONE | HQ/1F/FF-2.jpg |  |  | HQ
VAV0100 | VAV | Included | 1.111 FINANCE RECORD STORAGE | entity:HQ_1.111_FINANCE_RECORD_STORAGE |  | FINANCE SECURE STO 1.111 | 1.111 FINANCE RECORD STORAGE | HQ/1F/FF-2.jpg |  |  | HQ
VAV0101 | VAV | Included | 1.702 FOOD HEAT UP | entity:HQ_1.702_FOOD_HEAT_UP |  |  | 1.702 FOOD HEAT UP | HQ/1F/FF-1.jpg |  |  | HQ
VAV0102 | VAV | Included | 1.706 WASHING AREA | entity:HQ_1.706_WASHING_AREA |  | STAFF CAFETERIA (WASHING ROOM) 01.705 | 1.706 WASHING AREA | HQ/1F/FF-2.jpg |  |  | HQ
VAV0103 | VAV | Not Included | G.104 LOBBY | entity:HQ_G.104_LOBBY |  | VOID AREA, ROOM UNIT LOCATED @LVL 1 NORTH EAST AREA NE CORE | LOBBY (GROUND FLOOR) | HQ/1F/FF-1.jpg |  |  | HQ
VAV0104 | VAV | Not Included | G.104 LOBBY | entity:HQ_G.104_LOBBY |  |  | LOBBY (GROUND FLOOR) | HQ/1F/FF-1.jpg |  |  | HQ
VAV0105 | VAV | Not Included | G.104 LOBBY | entity:HQ_G.104_LOBBY |  |  | LOBBY (GROUND FLOOR) | HQ/1F/FF-2.jpg |  |  | HQ
VAV0106 | VAV | Not Included | G.104 LOBBY | entity:HQ_G.104_LOBBY |  |  | LOBBY (GROUND FLOOR) | HQ/1F/FF-2.jpg |  |  | HQ
VAV0107 | VAV | Not Included | 1.701 STAFF CAFETERIA | entity:HQ_1.701_STAFF_CAFETERIA |  |  | 1.701 STAFF CAFETERIA | HQ/1F/FF-1.jpg |  |  | HQ
VAV0108 | VAV | Not Included | 1.701 STAFF CAFETERIA | entity:HQ_1.701_STAFF_CAFETERIA |  |  | 1.701 STAFF CAFETERIA | HQ/1F/FF-2.jpg |  |  | HQ
VAV0109 | VAV | Not Included | 2.018 SUPPSERV DIRECTOR ENSUIT | entity:HQ_2.018_SUPPSERVDIRECTOR_ENSUIT |  | SUPP SERVICEDIR ENSUIT 2.018 | 2.018 DIRECTOR ENSUIT | HQ/2F/SF-1.jpg |  |  | HQ
VAV0110 | VAV | Included | 2.019 SUPPSERVADMINIST | entity:HQ_2.019_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.019 | 2.019 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0111 | VAV | Included | 2.020 SUPPSERVADMINIST | entity:HQ_2.02_SUPPSERVADMINIST |  | SUPPT SERVICEADMINIST 2.020 | 2.020 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0112 | VAV | Included | 2.021 SUPPSERVADMINIST | entity:HQ_2.021_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.021 | 2.021 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0113 | VAV | Included | 2.022 SUPP SER SECRETARY | entity:HQ_2.022_SUPPSERVSECRETARY |  | SUPP SERVICESECRETARY 2.022 | 2.022 SUPP. SER. SECRETARY | HQ/2F/SF-1.jpg |  |  | HQ
VAV0114 | VAV | Included | 2.023 SUPPSERVADMINIST | entity:HQ_2.023_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.023 | 2.023 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0115 | VAV | Included | 2.024 SUPPSERVADMINIST | entity:HQ_2.024_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.024 | 2.024 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0116 | VAV | Included | 2.025 SUPPSERVADMINIST | entity:HQ_2.025_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.025 | 2.025 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0117 | VAV | Included | 2.026 SUPP SER SECRETARY | entity:HQ_2.026_SUPPSERVSECRETARY |  | SUPP SERVICESECRETARY 2.026 | 2.026 SUPP. SER. SECRETARY | HQ/2F/SF-1.jpg |  |  | HQ
VAV0118 | VAV | Included | 2.027 SUPPSERVADMINIST | entity:HQ_2.027_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.027 | 2.027 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0119 | VAV | Included | 2.028 SUPPSERVADMINIST | entity:HQ_2.028_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.028 | 2.028 SUPP. SER. ADMIN | HQ/2F/SF-2.jpg |  |  | HQ
VAV0120 | VAV | Included | 2.029 SUPPSERVADMINIST | entity:HQ_2.029_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.029 | 2.029 SUPP. SER. ADMIN | HQ/2F/SF-2.jpg |  |  | HQ
VAV0121 | VAV | Included | 2.030 SUPP SER SECRETARY | entity:HQ_2.03_SUPPSERVSECRETARY |  | SUPP SERVICESECRETARY 2.030 | 2.030 SUPP. SER. SECRETARY | HQ/2F/SF-2.jpg |  |  | HQ
VAV0122 | VAV | Included | 2.031 SUPPSERVADMINIST | entity:HQ_2.031_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.031 | 2.031 SUPP. SER. ADMIN | HQ/2F/SF-2.jpg |  |  | HQ
VAV0123 | VAV | Included | 2.032 SUPPSERVADMINIST | entity:HQ_2.032_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.032 | 2.032 SUPP. SER. ADMIN | HQ/2F/SF-2.jpg |  |  | HQ
VAV0124 | VAV | Included | 2.033 SUPPSERVADMINIST | entity:HQ_2.033_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.033 | 2.033 SUPP. SER. ADMIN | HQ/2F/SF-2.jpg |  |  | HQ
VAV0125 | VAV | Included | 2.034 SUPP SER SECRETARY | entity:HQ_2.034_SUPPSERVSECRETARY |  | SUPP SERVICESECRETARY 2.034 | 2.034 SUPP. SER. SECRETARY | HQ/2F/SF-2.jpg |  |  | HQ
VAV0126 | VAV | Included | 2.035 SUPPSERVADMINIST | entity:HQ_2.035_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.035 | 2.035 SUPP. SER. ADMIN | HQ/2F/SF-2.jpg |  |  | HQ
VAV0127 | VAV | Included | 2.036 SUPPSERVADMINIST | entity:HQ_2.036_SUPPSERVADMINIST |  | SUPP SERVICEADMINIST 2.036 | 2.036 SUPP. SER. ADMIN | HQ/2F/SF-2.jpg |  |  | HQ
VAV0128 | VAV | Included | 2.110A OFFICE SPACE | entity:HQ_2.110A_OFFICE_SPACE |  | SHELL SPACE 02.110 | 2.110A OFFICE SPACE | HQ/2F/SF-2.jpg |  |  | HQ
VAV0129 | VAV | Not Included | 2.601 S TOWER CORRIDOR | entity:HQ_2.601_S-TOWER_CORRIDOR |  | CORRIDOR NE | NORTH EAST CORRIDOR | HQ/2F/SF-2.jpg |  |  | HQ
VAV0130 | VAV | Not Included | 2.601 S TOWER CORRIDOR | entity:HQ_2.601_S-TOWER_CORRIDOR |  | CORRIDOR | NORTH EAST CORRIDOR | HQ/2F/SF-2.jpg |  |  | HQ
VAV0131 | VAV | Not Included | 2.109 SHELL SPACE | entity:HQ_2.109_SHELL_SPACE |  | SHELL SPACE 2.109 | 2.109 FEMALE PRAYER ROOM | HQ/2F/SF-1.jpg |  |  | HQ
VAV0132 | VAV | Included | 2.108 SUPPSERV MEETING ROOM | entity:HQ_2.108_SUPPSERVMEETING_ROOM |  | SUPPSERVMEETING ROOM 2.108 | 2.108 MEETING ROOM | HQ/2F/SF-1.jpg |  |  | HQ
VAV0133 | VAV | Included | 2.108 SUPPSERV MEETING ROOM | entity:HQ_2.108_SUPPSERVMEETING_ROOM |  |  | 2.108 MEETING ROOM | HQ/2F/SF-1.jpg |  |  | HQ
VAV0134 | VAV | Not Included | 2.105 LOUNGE | entity:HQ_2.105_LOUNGE |  |  | 2.105 LOUNGE | HQ/2F/SF-1.jpg |  |  | HQ
VAV0135 | VAV | Included | 2.104 CONSULTANTS SPACE OTHERS | entity:HQ_2.104_CONSULTANTS_SPACE-OTHERS |  | CONSULTANTS SPACE OTHERS 2.104 | 2.104 CONSULTANT SPACE | HQ/2F/SF-1.jpg |  |  | HQ
VAV0136 | VAV | Included | 2.104 CONSULTANTS SPACE OTHERS | entity:HQ_2.104_CONSULTANTS_SPACE-OTHERS |  |  | 2.104 CONSULTANT SPACE | HQ/2F/SF-1.jpg |  |  | HQ
VAV0137 | VAV | Included | 2.102 CONSULTANTS SPACE OTHERS | entity:HQ_2.102_CONSULTANTS_SPACE-OTHERS |  | CONSULTANTS SPACE OTHERS 2.102 | 2.102 CONSULTANT SPACE | HQ/2F/SF-1.jpg |  |  | HQ
VAV0138 | VAV | Included | 2.017 SUPP SER SECRETARY | entity:HQ_2.017_SUPPSERVSECRETARY |  | SUPPSERVSECRETARY 2.017 | 2.017 SUPP. SER. SECRETARY | HQ/2F/SF-1.jpg |  |  | HQ
VAV0139 | VAV | Included | 2.016 SUPPSERVADMINIST | entity:HQ_2.016_SUPPSERVADMINIST |  | SUPPSERVADMINIST 2.016 | 2.016 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0140 | VAV | Included | 2.015 SUPPSERVADMINIST | entity:HQ_2.015_SUPPSERVADMINIST |  | SUPPSERVADMINIST 2.015 | 2.015 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0141 | VAV | Included | 2.014 SUPPSERVADMINIST | entity:HQ_2.014_SUPPSERVADMINIST |  | SUPPSERVADMINIST 2.014 | 2.014 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0142 | VAV | Included | 2.013 SUPP SER SECRETARY | entity:HQ_2.013_SUPPSERVSECRETARY |  | SUPPSERVSECRETARY 2.013 | 2.013 SUPP. SER. SECRETARY | HQ/2F/SF-1.jpg |  |  | HQ
VAV0143 | VAV | Included | 2.012 SUPPSERVADMINIST | entity:HQ_2.012_SUPPSERVADMINIST |  | SUPPSERVADMINIST 2.012 | 2.012 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0144 | VAV | Included | 2.011 SUPPSERVADMINIST | entity:HQ_2.011_SUPPSERVADMINIST |  | SUPPSERVADMINIST 2.011 | 2.011 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0145 | VAV | Included | 2.010 SUPPSERVADMINIST | entity:HQ_2.01_SUPPSERVADMINIST |  | SUPPSERVADMINIST 2.010 | 2.010 SUPP. SER. ADMIN | HQ/2F/SF-1.jpg |  |  | HQ
VAV0146 | VAV | Included | 2.009 SUPP SER SECRETARY | entity:HQ_2.009_SUPPSERVSECRETARY |  | SUPPSERVSECRETARY 2.009 | 2.009 SUPP. SER. SECRETARY | HQ/2F/SF-1.jpg |  |  | HQ
VAV0147 | VAV | Not Included | 2.008 DOHA DEBATE EXECUTIVE | entity:HQ_2.008_DOHA_DEBATE_EXECUTIVE |  | DOHA DEBATE EXECUTIVE 2.008 | 2.008 DEBATE EXECUTIVE | HQ/2F/SF-1.jpg |  |  | HQ
VAV0148 | VAV | Not Included | 2.007 DOHA DEBATE EXECUTIVE | entity:HQ_2.007_DOHA_DEBATE_EXECUTIVE |  | DOHA DEBATE EXECUTIVE 2.007 | 2.007 DEBATE EXECUTIVE | HQ/2F/SF-1.jpg |  |  | HQ
VAV0149 | VAV | Not Included | 2.006 DOHA DEBATE EXECUTIVE | entity:HQ_2.006_DOHA_DEBATE_EXECUTIVE |  | DOHA DEBATE EXECUTIVE 2.006 | 2.006 DEBATE EXECUTIVE | HQ/2F/SF-1.jpg |  |  | HQ
VAV0150 | VAV | Not Included | 2.005 DOHA DEBATE EXECUTIVE | entity:HQ_2.005_DOHA_DEBATE_EXECUTIVE |  | DOHA DEBATE EXECUTIVE 2.005 | 2.005 DEBATE EXECUTIVE | HQ/2F/SF-1.jpg |  |  | HQ
VAV0151 | VAV | Included | 2.004 DOHA DEBATE SECRETARY | entity:HQ_2.004_DOHA_DEBATE_SECRETARY |  | DOHA DEBATE SECRETARY 2.004 | 2.004 DEBATE SECRETARY | HQ/2F/SF-1.jpg |  |  | HQ
VAV0152 | VAV | Not Included | 2.003 DOHA DEBATE EXECUTIVE | entity:HQ_2.003_DOHA_DEBATE_EXECUTIVE |  | DOHA DEBATE EXECUTIVE 2.003 | 2.003 DEBATE EXECUTIVE | HQ/2F/SF-1.jpg |  |  | HQ
VAV0153 | VAV | Not Included | 2.002 DOHA DEBATE EXECUTIVE | entity:HQ_2.002_DOHA_DEBATE_EXECUTIVE |  | DOHA DEBATE EXECUTIVE 2.002 | 2.002 DEBATE EXECUTIVE | HQ/2F/SF-1.jpg |  |  | HQ
VAV0154 | VAV | Included | 2.001 STORAGE ROOM | entity:HQ_2.001_STORAGE_ROOM |  |  | 2.001 STORAGE ROOM | HQ/2F/SF-1.jpg |  |  | HQ
VAV0155 | VAV | Included | 2.101A OFFICE SPACE | entity:HQ_2.101A_OFFICE_SPACE |  | SHELL SPACE 02.101 | 2.101A OFFICE SPACE | HQ/2F/SF-1.jpg |  |  | HQ
VAV0156 | VAV | Not Included | 2.601 S TOWER CORRIDOR | entity:HQ_2.601_S-TOWER_CORRIDOR |  | CORRIDOR SOUTH WEST SW | SOUTH WEST CORRIDOR | HQ/2F/SF-1.jpg |  |  | HQ
VAV0157 | VAV | Included | 3.017 HR IMMIG STAFF | entity:HQ_3.017_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.017 | 3.017 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0158 | VAV | Included | 3.018 HR IMMIG STAFF | entity:HQ_3.018_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.018 | 3.018 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0159 | VAV | Included | 3.019 HR IMMIG STAFF | entity:HQ_3.019_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.019 | 3.019 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0160 | VAV | Included | 3.020 HR IMMIG STAFF | entity:HQ_3.02_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.020 | 3.020 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0161 | VAV | Included | 3.021 HR IMMIG STAFF | entity:HQ_3.021_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.021 | 3.021 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0162 | VAV | Included | 3.022 HR IMMIG SECRETARY | entity:HQ_3.022_HR_IMMIG_SECRETARY |  | HR IMMIGSECRETARY 3.022 | 3.022 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0163 | VAV | Included | 3.023 HR IMMIG STAFF | entity:HQ_3.023_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.023 | 3.023 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0164 | VAV | Included | 3.024 HR IMMIG STAFF | entity:HQ_3.024_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.024 | 3.024 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0165 | VAV | Included | 3.025 HR IMMIG STAFF | entity:HQ_3.025_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.025 | 3.025 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0166 | VAV | Included | 3.026 HR IMMIG STAFF | entity:HQ_3.026_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.026 | 3.026 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0167 | VAV | Included | 3.027 HR IMMIG STAFF | entity:HQ_3.027_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.027 | 3.027 HR IMMIG STAFF | HQ/3F/3F-2.jpg |  |  | HQ
VAV0168 | VAV | Included | 3.028 HR IMMIG STAFF | entity:HQ_3.028_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.028 | 3.028 HR IMMIG STAFF | HQ/3F/3F-2.jpg |  |  | HQ
VAV0169 | VAV | Included | 3.029 HR IMMIG STAFF | entity:HQ_3.029_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.029 | 3.029 HR IMMIG STAFF | HQ/3F/3F-2.jpg |  |  | HQ
VAV0170 | VAV | Included | 3.030 HR IMMIG STAFF | entity:HQ_3.03_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.030 | 3.030 HR IMMIG STAFF | HQ/3F/3F-2.jpg |  |  | HQ
VAV0171 | VAV | Included | 3.031 HR IMMIG STAFF | entity:HQ_3.031_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.031 | 3.031 HR IMMIG STAFF | HQ/3F/3F-2.jpg |  |  | HQ
VAV0172 | VAV | Included | 3.032 HR IMMIG SECRETARY | entity:HQ_3.032_HR_IMMIG_SECRETARY |  | HR IMMIGSTAFF 3.032 | 3.032 HR IMMIG STAFF | HQ/3F/3F-2.jpg |  |  | HQ
VAV0173 | VAV | Included | 3.033 MEETING ROOM | entity:HQ_3.033_MEETING_ROOM |  |  | 3.033 MEETING ROOM | HQ/3F/3F-2.jpg |  |  | HQ
VAV0174 | VAV | Included | 3.033 MEETING ROOM | entity:HQ_3.033_MEETING_ROOM |  |  | 3.033 MEETING ROOM | HQ/3F/3F-2.jpg |  |  | HQ
VAV0175 | VAV | Included | 3.105B OFFICE SPACE | entity:HQ_3.105B_OFFICE_SPACE |  | SHELL SPACE 03.108 | 3.105B OFFICE SPACE | HQ/3F/3F-2.jpg |  |  | HQ
VAV0176 | VAV | Not Included | 3.601 S TOWER CORRIDOR | entity:HQ_3.601_S-TOWER_CORRIDOR |  | CORRIDOR NE | NORTH EAST CORRIDOR | HQ/3F/3F-2.jpg |  |  | HQ
VAV0177 | VAV | Not Included | 3.360 ABLUTION ROOM | entity:HQ_3.36_ABLUTION_ROOM |  | SHELL SPACE 03.105 | 3.36 ABLUTION ROOM | HQ/3F/3F-1.jpg |  |  | HQ
VAV0178 | VAV | Not Included | 3.105A FEMALE PRAYER ROOM | entity:HQ_3.105A_FEMALE_PRAYER_ROOM |  |  | 3.105A FEMALE PRAYER ROOM | HQ/3F/3F-1.jpg |  |  | HQ
VAV0179 | VAV | Not Included | 3.601 S TOWER CORRIDOR | entity:HQ_3.601_S-TOWER_CORRIDOR |  | CORRIDOR | NORTH EAST CORRIDOR | HQ/3F/3F-2.jpg |  |  | HQ
VAV0180 | VAV | Not Included | 3.001 LOUNGE | entity:HQ_3.001_LOUNGE |  |  | 3.001 LOUNGE | HQ/3F/3F-1.jpg |  |  | HQ
VAV0181 | VAV | Included | 3.102 CONSULTANT SPACE TRAINEES | entity:HQ_3.102_CONSULTANT_SPACE_TRAINEES |  |  | 3.102 CONSULTANT SPACE TRAINEES | HQ/3F/3F-1.jpg |  |  | HQ
VAV0182 | VAV | Included | 3.102 CONSULTANT SPACE TRAINEES | entity:HQ_3.102_CONSULTANT_SPACE_TRAINEES |  |  | 3.102 CONSULTANT SPACE TRAINEES | HQ/3F/3F-1.jpg |  |  | HQ
VAV0183 | VAV | Included | 3.102 CONSULTANT SPACE TRAINEES | entity:HQ_3.102_CONSULTANT_SPACE_TRAINEES |  |  | 3.102 CONSULTANT SPACE TRAINEES | HQ/3F/3F-1.jpg |  |  | HQ
VAV0184 | VAV | Included | 3.104 HR IMMG SECRETARY | entity:HQ_3.104_HR_IMMIG_SECRETARY |  | HR IMMIGSECRETARY 3.104 | 3.104 HR IMMG SECRETARY | HQ/3F/3F-1.jpg |  |  | HQ
VAV0185 | VAV | Included | 3.012 HR IMMIG STAFF | entity:HQ_3.012_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.012 | 3.012 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0186 | VAV | Included | 3.013 HR IMMIG STAFF | entity:HQ_3.013_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.013 | 3.013 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0187 | VAV | Included | 3.014 HR IMMIG STAFF | entity:HQ_3.014_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.014 | 3.014 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0188 | VAV | Included | 3.015 HR IMMIG STAFF | entity:HQ_3.015_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.015 | 3.015 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0189 | VAV | Included | 3.016 HR IMMIG STAFF | entity:HQ_3.016_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.016 | 3.016 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0190 | VAV | Included | 3.003 HR IMMIG STAFF | entity:HQ_3.003_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.003 | 3.003 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0191 | VAV | Included | 3.004 HR IMMIG STAFF | entity:HQ_3.004_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.004 | 3.004 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0192 | VAV | Included | 3.005 HR IMMIG STAFF | entity:HQ_3.005_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.005 | 3.005 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0193 | VAV | Included | 3.006 HR IMMIG STAFF | entity:HQ_3.006_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.006 | 3.006 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0194 | VAV | Included | 3.007 HR IMMIG STAFF | entity:HQ_3.007_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.007 | 3.007 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0195 | VAV | Included | 3.008 HR IMMIG STAFF | entity:HQ_3.008_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.008 | 3.008 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0196 | VAV | Included | 3.009 HR IMMIG STORAGE | entity:HQ_3.009_HR_IMMIG_STORAGE |  | HR IMMIGSTORAGE 3.009 | 3.009 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0197 | VAV | Included | 3.010 HR IMMIG STAFF | entity:HQ_3.01_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.010 | 3.010 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0198 | VAV | Included | 3.011 HR IMMIG STAFF | entity:HQ_3.011_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.011 | 3.011 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0199 | VAV | Included | 3.101 SHELL SPACE | entity:HQ_3.101_SHELL_SPACE |  | SHELL SPACE 3.101 | 3.101 OFFICE SPACE | HQ/3F/3F-1.jpg |  |  | HQ
VAV0200 | VAV | Included | 3.002 HR IMMIG STAFF | entity:HQ_3.002_HR_IMMIG_STAFF |  | HR IMMIGSTAFF 3.002 | 3.002 HR IMMIG STAFF | HQ/3F/3F-1.jpg |  |  | HQ
VAV0201 | VAV | Not Included | 3.601 S TOWER CORRIDOR | entity:HQ_3.601_S-TOWER_CORRIDOR |  | CORRIDOR SW | SOUTH WEST CORRIDOR | HQ/3F/3F-1.jpg |  |  | HQ
VAV0202 | VAV | Included | 3.202A OFFICE SPACE | entity:HQ_3.202A_OFFICE_SPACE |  | SHELL SPACE B 03.202B | 3.202A OFFICE SPACE | HQ/3F/3F-1.jpg |  |  | HQ
VAV0203 | VAV | Included | 3.202B OFFICE SPACE | entity:HQ_3.202B_OFFICE_SPACE |  | SHELL SPACE A 03.202A | 3.202B OFFICE SPACE | HQ/3F/3F-1.jpg |  |  | HQ
VAV0204 | VAV | Included | 3.205 HR IMMIG IMMIGRATION | entity:HQ_3.205_HR_IMMIG_IMMIGRATION |  | HR IMMIGIMMIGRATION 3.205 | 3.205 HR IMMIGRATION | HQ/3F/3F-1.jpg |  |  | HQ
VAV0205 | VAV | Not Included | 3.206 HR IMMIG MANAGER | entity:HQ_3.206_HR_IMMIG_MANAGER |  | HR IMMIGMANAGER 3.206 | 3.206 HR IMMIG MANAGER | HQ/3F/3F-2.jpg |  |  | HQ
VAV0206 | VAV | Not Included | 3.207 HR IMMIG MANAGER | entity:HQ_3.207_HR_IMMIG_MANAGER |  | HR IMMIGMANAGER 3.207 | 3.207 HR IMMIG MANAGER | HQ/3F/3F-2.jpg |  |  | HQ
VAV0207 | VAV | Not Included | 3.208 HR IMMIG MANAGER | entity:HQ_3.208_HR_IMMIG_MANAGER |  | HR IMMIGMANAGER 3.208 | 3.208 HR IMMIG MANAGER | HQ/3F/3F-2.jpg |  |  | HQ
VAV0208 | VAV | Not Included | 3.209 HR IMMIG MANAGER | entity:HQ_3.209_HR_IMMIG_MANAGER |  | HR IMMIGMANAGER 3.209 | 3.209 HR IMMIG MANAGER | HQ/3F/3F-2.jpg |  |  | HQ
VAV0209 | VAV | Included | 3.210 HR IMMIG OFFICER | entity:HQ_3.21_HR_IMMIG_OFFICERS |  | HR IMMIG OFFICERS 3.210 | 3.210 HR IMMIG OFFICER | HQ/3F/3F-2.jpg |  |  | HQ
VAV0210 | VAV | Included | 3.210 HR IMMIG OFFICER | entity:HQ_3.21_HR_IMMIG_OFFICERS |  |  | 3.210 HR IMMIG OFFICER | HQ/3F/3F-2.jpg |  |  | HQ
VAV0211 | VAV | Not Included | 3.211 HR IMMIG MANAGER | entity:HQ_3.211_HR_IMMIG_MANAGER |  | HR IMMIGMANAGER 3.211 | 3.211 HR IMMIG MANAGER | HQ/3F/3F-2.jpg |  |  | HQ
VAV0212 | VAV | Included | 3.212 HR IMMIG SECRETARIES | entity:HQ_3.212_HR_IMMIG_SECRETARIES |  | HR IMMIGSECRETARY 3.212 | 3.212 HR IMMIG SEC. | HQ/3F/3F-2.jpg |  |  | HQ
VAV0213 | VAV | Not Included | 3.213 HR IMMIG DIR ENSUIT | entity:HQ_3.213_HR_IMMIG_DIRENSUIT |  | HR IMMIGDIRENSUIT 3.213 | 3.213 HR IMMIG DIR. ENSUIT | HQ/3F/3F-2.jpg |  |  | HQ
VAV0214 | VAV | Not Included | 3.214 IT SECRETARY | entity:HQ_3.214_IT_SECRETARY |  | IT SECRETARY 3.214 | 3.214 IT DIR. ENSUIT | HQ/3F/3F-2.jpg |  |  | HQ
VAV0215 | VAV | Not Included | 3.215 IT DIR ENSUIT | entity:HQ_3.215_IT_DIRENSUIT |  | IT DIRECTOR ENSUIT 3.215 | 3.215 IT DIR. ENSUIT | HQ/3F/3F-2.jpg |  |  | HQ
VAV0216 | VAV | Included | 3.216 PROC CONTR SECRETARY | entity:HQ_3.216_PROC&CONTRSECRETARY |  | PROC& CONTRLSECRETARY 3.216 | 3.216 PROC. CONTR. SECRETARY | HQ/3F/3F-2.jpg |  |  | HQ
VAV0217 | VAV | Not Included | 3.201 PROC AND CONTRLDIRENSUIT | entity:HQ_3.201_PROC&CONTRDIRENSUIT |  | PROC& CONTRLDIRENSUIT 3.201 | 3.201 PROC. & CONTR. DIR. E | HQ/3F/3F-1.jpg |  |  | HQ
VAV0218 | VAV | Included | 3.301 PROC AND CONTR MEETING ROOM | entity:HQ_3.301_PROC&CONTRMEETING_ROOM |  | HR IMMIGMEETING ROOM 3.301 | 3.301 PROC. & CONTR. MEETING ROOM | HQ/3F/3F-2.jpg |  |  | HQ
VAV0219 | VAV | Included | 3.301 PROC AND CONTR MEETING ROOM | entity:HQ_3.301_PROC&CONTRMEETING_ROOM |  |  | 3.301 PROC. & CONTR. MEETING ROOM | HQ/3F/3F-2.jpg |  |  | HQ
VAV0220 | VAV | Included | 3.302 HR IMMG MEETING ROOM | entity:HQ_3.302_HR_IMMIG_MEETING_ROOM |  | HR IMMIGMEETING ROOM 3.302 | 3.302 HR IMMG. MEETING ROOM | HQ/3F/3F-2.jpg |  |  | HQ
VAV0221 | VAV | Not Included | 3.602 E TOWER CORRIDOR | entity:HQ_3.602_E-TOWER_CORRIDOR |  | E-TOWER LOBBY SE | 3.602 SOUTH EAST CORRIDOR | HQ/3F/3F-2.jpg |  |  | HQ
VAV0222 | VAV | Not Included | 4.004 STR PL DIR ENSUIT | entity:HQ_4.004_STR_PL_DIR_ENSUIT |  |  | 4.004 STR. PL. DIR. ENSUIT | HQ/4F/4F-1.jpg |  |  | HQ
VAV0223 | VAV | Not Included | 4.005 STR PL DIR MEETING ROOM | entity:HQ_4.005_STRPLDIRMEETING_ROOM |  | STR PL DIR ENSUIT 04.005 | 4.005 STR.PL.DIR.MEETING ROOM | HQ/4F/4F-1.jpg |  |  | HQ
VAV0224 | VAV | Not Included | 4.006 STR PL DIR MANAGER | entity:HQ_4.006_STRPLDIRMANAGER |  |  | 4.006 STR. PL. DIR. MANAGER | HQ/4F/4F-1.jpg |  |  | HQ
VAV0225 | VAV | Not Included | 4.007 STR PL DIR MANAGER | entity:HQ_4.007_STRPLDIRMANAGER |  |  | 4.007 STR. PL. DIR. MANAGER | HQ/4F/4F-1.jpg |  |  | HQ
VAV0226 | VAV | Not Included | 4.008 STR PL DIR MANAGER | entity:HQ_4.008_STRPLDIRMANAGER |  |  | 4.008 STR. PL. DIR. MANAGER | HQ/4F/4F-1.jpg |  |  | HQ
VAV0227 | VAV | Not Included | 4.009 STR PL DIR HEAD OF PL | entity:HQ_4.009_STRPLDIRHEAD_OF_PL |  |  | 4.009 STR. PL. DIR. HEAD OF PL. | HQ/4F/4F-1.jpg |  |  | HQ
VAV0228 | VAV | Not Included | 4.010 STR PL DIR HEAD OF PL | entity:HQ_4.01_STRPLDIRHEAD_OF_PL |  |  | 4.010 STR. PL. DIR. HEAD OF PL. | HQ/4F/4F-2.jpg |  |  | HQ
VAV0229 | VAV | Not Included | 4.011 STR PL DIR HEAD OF PL | entity:HQ_4.011_STRPLDIRHEAD_OF_PL |  |  | 4.011 STR. PL. DIR. HEAD OF PL. | HQ/4F/4F-2.jpg |  |  | HQ
VAV0230 | VAV | Not Included | 4.012 STR PL DIR HEAD OF PL | entity:HQ_4.012_STRPLDIRHEAD_OF_PL |  |  | 4.012 STR. PL. DIR. HEAD OF PL. | HQ/4F/4F-2.jpg |  |  | HQ
VAV0231 | VAV | Not Included | 4.013 STR PL DIR HEAD OF PL | entity:HQ_4.013_STRPLDIRHEAD_OF_PL |  |  | 4.013 STR. PL. DIR. HEAD OF PL. | HQ/4F/4F-2.jpg |  |  | HQ
VAV0232 | VAV | Not Included | 4.014 STR PL DIR MANAGER | entity:HQ_4.014_STRPLDIRMANAGER |  |  | 4.014 STR. PL. DIR. MANAGER | HQ/4F/4F-2.jpg |  |  | HQ
VAV0233 | VAV | Included | 4.015A OFFICE SPACE | entity:HQ_4.015C_OFFICE_SPACE |  | SHELL SPACE C 04.015C | 4.015A OFFICE SPACE | HQ/4F/4F-2.jpg |  |  | HQ
VAV0234 | VAV | Included | 4.015C OFFICE SPACE | entity:HQ_4.015A_OFFICE_SPACE |  | SHELL SPACE A 04.015A | 4.015C OFFICE SPACE | HQ/4F/4F-2.jpg |  |  | HQ
VAV0235 | VAV | Not Included | 4.601 S TOWER CORRIDOR | entity:HQ_4.601_S-TOWER_CORRIDOR |  | CORRIDOR NE | NORTH EAST CORRIDOR | HQ/4F/4F-2.jpg |  |  | HQ
VAV0236 | VAV | Not Included | 4.109 VP EDU STORAGE | entity:HQ_4.109_VP_EDU_STORAGE |  | VP EDU STORGE 04.109 | 4.109 VP EDU STORAGE | HQ/4F/4F-2.jpg |  |  | HQ
VAV0237 | VAV | Not Included | 4.601 S TOWER CORRIDOR | entity:HQ_4.601_S-TOWER_CORRIDOR |  | CORRIDOR NE | NORTH EAST CORRIDOR | HQ/4F/4F-2.jpg |  |  | HQ
VAV0238 | VAV | Included | 4.108 STR PL DIR ARCHIVE ROOM | entity:HQ_4.108_STRPLDIRARCHIVE_ROOM |  | STR PL DIR ARCHIVE ROOM 04.108 | 4.108 STR. PL. DIR. TECH. STAFF | HQ/4F/4F-1.jpg |  |  | HQ
VAV0239 | VAV | Included | 4.107 STR PL DIR TECH STAFF | entity:HQ_4.107_STRPLDIRTECHNSTAFF |  | STR PL DIR TECHNSTAFF 04.107 | 4.107 STR. PL. DIR. TECH. STAFF | HQ/4F/4F-1.jpg |  |  | HQ
VAV0240 | VAV | Not Included | 4.104 WAITING LOUNGE | entity:HQ_4.104_WAITING_LOUNGE |  |  | 4.104 WAITING LOUNGE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0241 | VAV | Not Included | 4.104 WAITING LOUNGE | entity:HQ_4.104_WAITING_LOUNGE |  |  | 4.104 WAITING LOUNGE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0242 | VAV | Not Included | 4.002 STR PL DIR MANAGER | entity:HQ_4.002_STRPLDIRMANAGER |  |  | 4.002 MANAGER | HQ/4F/4F-1.jpg |  |  | HQ
VAV0243 | VAV | Included | 4.003 STR PL DIR EXEC SECRE | entity:HQ_4.003_STR_PL_DIR_EXEC_SECRE |  | STR PL DIREXECSECRETARY 04.003 | 4.003 SECRETARY | HQ/4F/4F-1.jpg |  |  | HQ
VAV0244 | VAV | Included | 4.001B OFFICE SPACE | entity:HQ_4.001B_OFFICE_SPACE |  | SHELL SPACE B 04.001B | 4.001B OFFICE SPACE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0245 | VAV | Included | 4.001D OFFICE SPACE | entity:HQ_4.001D_OFFICE_SPACE |  | SHELL SPACE D 04.001D | 4.001D OFFICE SPACE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0246 | VAV | Included | 4.001F OFFICE SPACE | entity:HQ_4.001F_OFFICE_SPACE |  | SHELL SPACE F 04.001F | 4.001F OFFICE SPACE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0247 | VAV | Included | 4.001G OFFICE SPACE | entity:HQ_4.001G_OFFICE_SPACE |  | SHELL SPACE G 04.001G | 4.001G OFFICE SPACE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0248 | VAV | Included | 4.103 STORAGE SPACE | entity:HQ_4.103_STORAGE_SPACE |  |  | 4.103 STORAGE SPACE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0249 | VAV | Included | 4.102 SHELL SPACE | entity:HQ_4.102_SHELL_SPACE |  | SHELL SPACE 04.102 | 4.102 OFFICE SPACE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0250 | VAV | Included | 4.101 SHELL SPACE | entity:HQ_4.101_SHELL_SPACE |  | SHELL SPACE 04.101 | 4.101 OFFICE SPACE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0251 | VAV | Not Included | 4.601 S TOWER CORRIDOR | entity:HQ_4.601_S-TOWER_CORRIDOR |  | CORRIDOR SW | SOUTH WEST CORRIDOR | HQ/4F/4F-1.jpg |  |  | HQ
VAV0252 | VAV | Included | 4.201 SHELL SPACE | entity:HQ_4.201_SHELL_SPACE |  | SHELL SPACE 04.201 | 4.201 OFFICE SPACE | HQ/4F/4F-2.jpg |  |  | HQ
VAV0253 | VAV | Included | 4.204 SHELL SPACE | entity:HQ_4.204_SHELL_SPACE |  | SHELL SPACE 04.204 | 4.204 OFFICE SPACE | HQ/4F/4F-2.jpg |  |  | HQ
VAV0254 | VAV | Not Included | 4.205 VP ADM MANAGER | entity:HQ_4.205_VP_ADM_MANAGER |  | VP ADMN MANAGER 04.205 | 4.205 VP ADM MANAGER | HQ/4F/4F-2.jpg |  |  | HQ
VAV0255 | VAV | Not Included | 4.206 VP ADM MANAGER | entity:HQ_4.206_VP_ADM_MANAGER |  | VP ADMN MANAGER 04.206 | 4.206 VP ADM MANAGER | HQ/4F/4F-2.jpg |  |  | HQ
VAV0256 | VAV | Included | 4.208 VP ADM EXECSECRET | entity:HQ_4.208_VP_ADM_EXECSECRET |  | VP ADMN SUPPSECRET 04.208 | 4.208 VP ADM SEC. | HQ/4F/4F-2.jpg |  |  | HQ
VAV0257 | VAV | Included | 4.208 VP ADM EXECSECRET | entity:HQ_4.208_VP_ADM_EXECSECRET |  |  | 4.208 VP ADM SEC. | HQ/4F/4F-2.jpg |  |  | HQ
VAV0258 | VAV | Not Included | 4.209 VP ADM MANAGER | entity:HQ_4.209_VP_ADM_MANAGER |  | VP ADMN MANAGER 04.209 | 4.209 VP ADM MANAGER | HQ/4F/4F-2.jpg |  |  | HQ
VAV0259 | VAV | Not Included | 4.210 VP ADM MANAGER | entity:HQ_4.21_VP_ADM_MANAGER |  | VP ADMN MANAGER 04.210 | 4.210 MANAGER | HQ/4F/4F-2.jpg |  |  | HQ
VAV0260 | VAV | Not Included | 4.211 VP ADM MANAGER | entity:HQ_4.211_VP_ADM_MANAGER |  | VP ADMN MANAGER 04.211 | 4.211 VP ADMIN | HQ/4F/4F-2.jpg |  |  | HQ
VAV0261 | VAV | Included | 4.212 VP ADM PERSASSIST | entity:HQ_4.212_VP_ADM_PERSASSIST |  | VP ADMNPERSASSIST 04.212 | 4.212 VP ADM PERS. ASS. | HQ/4F/4F-2.jpg |  |  | HQ
VAV0262 | VAV | Not Included | 4.213 VP ADM ENSUIT | entity:HQ_4.213_VP_ADM_ENSUIT |  | VP ADMNENSUIT 04.213 | 4.213 VP ADM ENSUIT | HQ/4F/4F-2.jpg |  |  | HQ
VAV0263 | VAV | Not Included | 4.301 VP ADM MEETING ROOM | entity:HQ_4.301_VP_ADM_MEETING_ROOM |  | VP ADMNMEETING ROOM 04.301 | 4.301 VP ADM MEETING ROOM | HQ/4F/4F-2.jpg |  |  | HQ
VAV0264 | VAV | Not Included | 4.301 VP ADM MEETING ROOM | entity:HQ_4.301_VP_ADM_MEETING_ROOM |  |  | 4.301 VP ADM MEETING ROOM | HQ/4F/4F-2.jpg |  |  | HQ
VAV0265 | VAV | Not Included | 4.603 E TOWER CORRIDOR | entity:HQ_4.603_E-TOWER_CORRIDOR |  | CORRIDOR SE | SOUTH EAST CORRIDOR | HQ/4F/4F-2.jpg |  |  | HQ
VAV0266 | VAV | Not Included | 4.603 E TOWER CORRIDOR | entity:HQ_4.603_E-TOWER_CORRIDOR |  | CORRIDOR SE | SOUTH EAST CORRIDOR | HQ/4F/4F-2.jpg |  |  | HQ
VAV0267 | VAV | Not Included | 5.012 VP EDU OFFICE DIRECTOR ENSUIT | entity:HQ_5.012_VP_EDU_OFFICE_DIRECTOR_ENSUIT |  | VP EDU OFCDIRENSUIT 5.012 | 5.012 VP EDU DIR ENSUIT | HQ/5F/5F-1.jpg |  |  | HQ
VAV0268 | VAV | Not Included | 5.013 VP EDU SECRETARY | entity:HQ_5.013_VP_EDU_SECRETARY |  | VP EDU SECRETARY 5.013 | 5.013 VP EDU SECR. | HQ/5F/5F-1.jpg |  |  | HQ
VAV0269 | VAV | Included | 5.014 VP EDU ASSISTANT | entity:HQ_5.014_VP_EDU_ASSISTANT |  | VP EDU ASSISTANT 5.014 | 5.014 VP EDU ASSIS. | HQ/5F/5F-1.jpg |  |  | HQ
VAV0270 | VAV | Included | 5.015 VP EDU ASSISTANT | entity:HQ_5.015_VP_EDU_ASSISTANT |  | VP EDU ASSISTANT 5.015 | 5.015 VP EDU ASSIS. | HQ/5F/5F-1.jpg |  |  | HQ
VAV0271 | VAV | Included | 5.016 VP EDU ASSISTANT | entity:HQ_5.016_VP_EDU_ASSISTANT |  | VP EDU ASSISTANT 5.016 | 5.016 VP EDU ASSIS. | HQ/5F/5F-1.jpg |  |  | HQ
VAV0272 | VAV | Included | 5.017 VP EDU ASSISTANT | entity:HQ_5.017_VP_EDU_ASSISTANT |  | VP EDU ASSISTANT 5.017 | 5.017 VP EDU ASSIS. | HQ/5F/5F-1.jpg |  |  | HQ
VAV0273 | VAV | Not Included | 5.018 VP EDU OFFICERS | entity:HQ_5.018_VP_EDU_OFFICERS |  | VP EDU OFFICERS 5.018 | 5.018 VP EDU OFF. | HQ/5F/5F-1.jpg |  |  | HQ
VAV0274 | VAV | Not Included | 5.019 VP EDU OFFICERS | entity:HQ_5.019_VP_EDU_OFFICERS |  | VP EDU OFFICERS 5.019 | 5.019 VP EDU OFF. | HQ/5F/5F-1.jpg |  |  | HQ
VAV0275 | VAV | Not Included | 5.020 VP EDU OFFICERS | entity:HQ_5.020_VP_EDU_OFFICERS |  | VP EDU OFFICERS 5.020 | 5.020 VP EDU OFF. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0276 | VAV | Not Included | 5.021 VP EDU OFFICERS | entity:HQ_5.021_VP_EDU_OFFICERS |  | VP EDU OFFICERS 5.021 | 5.021 VP EDU OFF. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0277 | VAV | Not Included | 5.022 VP EDU OFFICERS | entity:HQ_5.022_VP_EDU_OFFICERS |  | VP EDU OFFICERS 5.022 | 5.022 VP EDU OFF. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0278 | VAV | Not Included | 5.023 VP EDU OFFICERS | entity:HQ_5.023_VP_EDU_OFFICERS |  | VP EDU OFFICERS 5.023 | 5.023 VP EDU OFF. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0279 | VAV | Included | 5.024 VP EDU SECRETARY | entity:HQ_5.024_VP_EDU_SECRETARY |  | VP EDU SECRETARY 5.024 | 5.024 VP EDU SEC. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0280 | VAV | Not Included | 5.025 VP EDU OFFICE DIRECTOR ENSUIT | entity:HQ_5.025_VP_EDU_OFFICE_DIRECTOR_ENSUIT |  | VP EDU OFCDIRENSUIT 5.025 | 5.025 VP EDU DIR ENSUIT | HQ/5F/5F-2.jpg |  |  | HQ
VAV0281 | VAV | Included | 5.026 VP EDU ASSISTANT | entity:HQ_5.026_VP_EDU_ASSISTANT |  | VP EDU ASSISTANT 5.026 | 5.026 VP EDU ASS. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0282 | VAV | Not Included | 5.601 S TOWER CORRIDOR | entity:HQ_5.601_S-TOWER_CORRIDOR |  | CORRIDOR - | NORTH EAST CORRIDOR | HQ/5F/5F-2.jpg |  |  | HQ
VAV0283 | VAV | Not Included | 5.110 VP EDU OFFICERS | entity:HQ_5.110_VP_EDU_OFFICERS |  | VP EDU OFFICERS 5.110 | 5.110 VP EDU OFF. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0284 | VAV | Included | 5.109 ELECTRICAL CABINET | entity:HQ_5.109_ELECTRICAL_CABINET |  | VP EDU ASSISTANT 5.109 | 5.109 VP EDU ASS. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0285 | VAV | Included | 5.108 VP EDU ASSISTANT | entity:HQ_5.108_VP_EDU_ASSISTANT |  | VP EDU ASSISTANT 5.108 | 5.108 VP EDU SEC. | HQ/5F/5F-1.jpg |  |  | HQ
VAV0286 | VAV | Included | 5.107 VP EDUCATION SUPPSECRET | entity:HQ_5.107_VP_EDUCATION_SUPPSECRET |  | VP EDU SUPPSECRETARIES 5.107 | 5.107 VP EDU SEC. | HQ/5F/5F-1.jpg |  |  | HQ
VAV0287 | VAV | Included | 5.107 VP EDUCATION SUPPSECRET | entity:HQ_5.107_VP_EDUCATION_SUPPSECRET |  |  | 5.107 VP EDU SEC. | HQ/5F/5F-1.jpg |  |  | HQ
VAV0288 | VAV | Not Included | 5.104 VP EDU LOUNGE WAITING | entity:HQ_5.104_VP_EDU_LOUNGE_WAITING |  |  | 5.104 VP EDU LOUNGE WAITING | HQ/5F/5F-1.jpg |  |  | HQ
VAV0289 | VAV | Not Included | 5.104 VP EDU LOUNGE WAITING | entity:HQ_5.104_VP_EDU_LOUNGE_WAITING |  |  | 5.104 VP EDU LOUNGE WAITING | HQ/5F/5F-1.jpg |  |  | HQ
VAV0290 | VAV | Included | 5.009 VP1 VP EDU OFFICERS | entity:HQ_5.009_VP1_VP_EDU_OFFICERS |  |  | 5.009 VP EDU OFFICERS | HQ/5F/5F-1.jpg |  |  | HQ
VAV0291 | VAV | Included | 5.010 VP EDU OFFICERS | entity:HQ_5.010_VP_EDU_OFFICERS |  |  | 5.010 VP EDU OFFICERS | HQ/5F/5F-1.jpg |  |  | HQ
VAV0292 | VAV | Included | 5.011 VP EDU ASSISTANT | entity:HQ_5.011_VP_EDU_ASSISTANT |  |  | 5.011 VP EDU ASSISTANT | HQ/5F/5F-1.jpg |  |  | HQ
VAV0293 | VAV | Not Included | 5.002 VP EDU OFF DIR ENSUIT | entity:HQ_5.002_VP_EDU_OFFDIRENSUIT |  | VP EDU OFFDIRENSUIT 5.002 | 5.002 VP EDU OFF. DIR ENSUIT | HQ/5F/5F-1.jpg |  |  | HQ
VAV0294 | VAV | Included | 5.003 VP EDU SECRETARY | entity:HQ_5.003_VP_EDU_SECRETARY |  | VP EDU SECRETARY 5.003 | 5.003 VP EDU SECRE. | HQ/5F/5F-1.jpg |  |  | HQ
VAV0295 | VAV | Included | 5.004 VP EDU ASSISTANT | entity:HQ_5.004_VP_EDU_ASSISTANT |  |  | 5.004 VP EDU ASSISTANT | HQ/5F/5F-1.jpg |  |  | HQ
VAV0296 | VAV | Included | 5.005 VP EDU OFFICERS | entity:HQ_5.005_VP_EDU_OFFICERS |  |  | 5.005 VP EDU OFFICERS | HQ/5F/5F-1.jpg |  |  | HQ
VAV0297 | VAV | Included | 5.006 VP EDU OFFICERS | entity:HQ_5.006_VP_EDU_OFFICERS |  |  | 5.006 VP EDU OFFICERS | HQ/5F/5F-1.jpg |  |  | HQ
VAV0298 | VAV | Included | 5.007 VP EDU OFFICERS | entity:HQ_5.007_VP_EDU_OFFICERS |  |  | 5.007 VP EDU ASSISTANT | HQ/5F/5F-1.jpg |  |  | HQ
VAV0299 | VAV | Included | 5.008 VP EDU ASSISTANT | entity:HQ_5.008_VP_EDU_ASSISTANT |  |  | 5.008 VP EDU ASSISTANT | HQ/5F/5F-1.jpg |  |  | HQ
VAV0300 | VAV | Included | 5.102 MEETING ROOM | entity:HQ_5.102_MEETING_ROOM |  |  | 5.102 MEETING ROOM | HQ/5F/5F-1.jpg |  |  | HQ
VAV0301 | VAV | Included | 5.102 MEETING ROOM | entity:HQ_5.102_MEETING_ROOM |  |  | 5.102 MEETING ROOM | HQ/5F/5F-1.jpg |  |  | HQ
VAV0302 | VAV | Included | 5.101 VP EDU SECRET | entity:HQ_5.101_VP_EDU_SECRET |  |  | 5.101 VP EDU SECRETARY | HQ/5F/5F-1.jpg |  |  | HQ
VAV0303 | VAV | Included | 5.001 VP EDU ASSISTANT | entity:HQ_5.001_VP_EDU_ASSISTANT |  |  | 5.001 VP EDU ASSISTANT | HQ/5F/5F-1.jpg |  |  | HQ
VAV0304 | VAV | Not Included | 5.601 S TOWER CORRIDOR | entity:HQ_5.601_S-TOWER_CORRIDOR |  | CORRIDOR SW | SOUTH WEST CORRIDOR | HQ/5F/5F-1.jpg |  |  | HQ
VAV0305 | VAV | Included | 5.201 VP EDU MEMBERS OF EDU | entity:HQ_5.201_VP_EDU_MEMBERS_OF_EDU |  | VP EDU MEMBERS OF EDU 5.201 | 5.201 VP EDU MEMB. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0306 | VAV | Included | 5.202 VP EDU MEMBERS OF EDU | entity:HQ_5.202_VP_EDU_MEMBERS_OF_EDU |  | VP EDU MEMBERS OF EDU 5.202 | 5.202 VP EDU MEMB. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0307 | VAV | Included | 5.203 VP EDU MEMBERS OF EDU | entity:HQ_5.203_VP_EDU_MEMBERS_OF_EDU |  | VP EDU MEMBERS OF EDU 5.203 | 5.203 VP EDU MEMB. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0308 | VAV | Included | 5.205 VP EDU MEETING ROOM | entity:HQ_5.205_VP_EDU_MEETING_ROOM |  | VP EDU MEETING ROOM 5.205 | 5.205 VP EDU MEMB. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0309 | VAV | Included | 5.205 VP EDU MEETING ROOM | entity:HQ_5.205_VP_EDU_MEETING_ROOM |  |  | 5.205 VP EDU MEMB. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0310 | VAV | Included | 5.206 VP EDU MEMBERS OF EDU | entity:HQ_5.206_VP_EDU_MEMBERS_OF_EDU |  | VP EDU MEMBERS OF EDU 5.206 | 5.206 VP EDU MEMB. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0311 | VAV | Included | 5.207 VP EDU MEMBERS OF EDU | entity:HQ_5.207_VP_EDU_MEMBERS_OF_EDU |  | VP EDU MEMBERS OF EDU 5.207 | 5.207 VP EDU MEMB. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0312 | VAV | Included | 5.208 VP EDU MEMBERS OF EDU | entity:HQ_5.208_VP_EDU_MEMBERS_OF_EDU |  | VP EDU MEMBERS OF EDU 5.208 | 5.208 VP EDU MEMB. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0313 | VAV | Included | 5.209 VP EDU MEMBERS OF EDU | entity:HQ_5.209_VP_EDU_MEMBERS_OF_EDU |  | VP EDU MEMBERS OF EDU 5.209 | 5.209 VP EDU MEMB. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0314 | VAV | Not Included | 5.210 VP EDU ENSUIT | entity:HQ_5.210_VP_EDU_ENSUIT |  |  | 5.210 VP EDU ENSUIT | HQ/5F/5F-2.jpg |  |  | HQ
VAV0315 | VAV | Included | 5.211 VP EDU CHPEXECSECRET | entity:HQ_5.211_VP_EDU_CHPEXECSECRET |  | VP EDU CHPEXECSECRET 5.211 | 5.211 VP EDU SEC. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0316 | VAV | Included | 5.212 VP EDU MEMBERS OF EDU | entity:HQ_5.212_VP_EDU_MEMBERS_OF_EDU |  | VP EDU MEMBERS OF EDU 5.212 | 5.212 VP EDU MEMB. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0317 | VAV | Not Included | 5.213 VP EDU OFFICE DIRECTOR ENSUIT | entity:HQ_5.213_VP_EDU_OFFICE_DIRECTOR_ENSUIT |  | VP EDU OFCDIRENSUIT 5.213 | 5.213 VP EDU DIR. ENSUIT | HQ/5F/5F-2.jpg |  |  | HQ
VAV0318 | VAV | Not Included | 5.350 CORRIDOR | entity:HQ_5.350_CORRIDOR |  | CORRIDOR SE | SOUTH EAST CORRIDOR | HQ/5F/5F-2.jpg |  |  | HQ
VAV0319 | VAV | Not Included | 5.350 CORRIDOR | entity:HQ_5.350_CORRIDOR |  | CORRIDOR SE | SOUTH EAST CORRIDOR | HQ/5F/5F-2.jpg |  |  | HQ
VAV0320 | VAV | Not Included | 5.350 CORRIDOR | entity:HQ_5.350_CORRIDOR |  | CORRIDOR SE | SOUTH EAST CORRIDOR | HQ/5F/5F-2.jpg |  |  | HQ
VAV0321 | VAV | Not Included | 5.350 CORRIDOR | entity:HQ_5.350_CORRIDOR |  | CORRIDOR NE | NORTH EAST CORRIDOR | HQ/5F/5F-2.jpg |  |  | HQ
VAV0322 | VAV | Not Included | 5.027 VP EDU OFFICERS | entity:HQ_5.027_VP_EDU_OFFICERS |  | VP EDU OFFICERS 5.027 | 5.027 VP EDU OFF. | HQ/5F/5F-2.jpg |  |  | HQ
VAV0323 | VAV | Included | 6.012 INTAUDIT SEN JNTAUD | entity:HQ_6.012_INTAUDIT_SEN_JNTAUD |  | INTAUDIT SENJNTAUD 06.012 | 6.012 INT. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0324 | VAV | Included | 6.013 INTAUDIT SECRETARY | entity:HQ_6.013_INTAUDIT_SECRETARY |  | INTAUDIT SECRETARY 06.013 | 6.013 INT. AUDIT SEC. | HQ/6F/6F-1.jpg |  |  | HQ
VAV0325 | VAV | Included | 6.014 ACA AUDIT SUPP AUDIT | entity:HQ_6.014_ACAAUDIT_SUPPAUDIT |  | ACA AUDIT SUPP AUDIT 06.014 | 6.014 ACA. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0326 | VAV | Included | 6.015 ACA AUDIT SUPP AUDIT | entity:HQ_6.015_ACAAUDIT_SUPPAUDIT |  | ACA AUDIT SUPP AUDIT 06.015 | 6.015 ACA. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0327 | VAV | Included | 6.016 ACA AUDIT SUPP AUDIT | entity:HQ_6.016_ACAAUDIT_SUPPAUDIT |  | ACA AUDIT SUPP AUDIT 06.016 | 6.016 ACA. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0328 | VAV | Included | 6.017 ACA AUDIT SUPP AUDIT | entity:HQ_6.017_ACAAUDIT_SUPPAUDIT |  | ACA AUDIT SUPP AUDIT 06.017 | 6.017 ACA. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0329 | VAV | Included | 6.018 ACA AUDIT SUPP AUDIT | entity:HQ_6.018_ACAAUDIT_SUPPAUDIT |  | ACA AUDIT SUPP AUDIT 06.018 | 6.018 ACA. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0330 | VAV | Included | 6.019 ACA AUDIT SUPP AUDIT | entity:HQ_6.019_ACAAUDIT_SUPPAUDIT |  | ACA AUDIT SUPP AUDIT 06.019 | 6.019 ACA. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0331 | VAV | Included | 6.020 ACA AUDIT SUPP AUDIT | entity:HQ_6.02_ACAAUDIT_SUPPAUDIT |  | ACA AUDIT SUPP AUDIT 06.020 | 6.020 ACA. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0332 | VAV | Included | 6.021 ACA AUDIT SECRETARY | entity:HQ_6.021_ACAAUDIT_SECRETARY |  | ACA AUDIT SECRETARY 06.021 | 6.021 ACA. AUDIT SEC. | HQ/6F/6F-2.jpg |  |  | HQ
VAV0333 | VAV | Included | 6.022 ACA AUDIT SECRETARY | entity:HQ_6.022_ACAAUDIT_SECRETARY |  | ACA AUDIT SECRETARY 06.022 | 6.022 ACA. AUDIT SEC. | HQ/6F/6F-2.jpg |  |  | HQ
VAV0334 | VAV | Included | 6.023 ACA AUDIT ACA SENAUD | entity:HQ_6.023_ACAAUDIT_ACASENAUD |  | ACA AUDIT ACA SENAUD 06.023 | 6.023 ACA. SEN. AUDIT | HQ/6F/6F-2.jpg |  |  | HQ
VAV0335 | VAV | Included | 6.024 ACA AUDIT ACA SENAUD | entity:HQ_6.024_ACAAUDIT_ACASENAUD |  | ACA AUDIT ACA SENAUD 06.024 | 6.024 ACA. SEN. AUDIT | HQ/6F/6F-2.jpg |  |  | HQ
VAV0336 | VAV | Included | 6.025 FACILITY MANAGSECRETARY | entity:HQ_6.025_FACILITY_MANAGSECRETARY |  | FACILITY MANAGER SEC 06.025 | 6.025 FACI. MANA. SEC. | HQ/6F/6F-2.jpg |  |  | HQ
VAV0337 | VAV | Not Included | 6.026 FACILITY MANAG DIR ENSUIT | entity:HQ_6.026_VACILITY_MANAGDIRENSUIT |  | FACILITY MANDIRENSUIT 06.026 | 6.026 FACILITY MANAG. DIR. ENSUIT | HQ/6F/6F-2.jpg |  |  | HQ
VAV0338 | VAV | Included | 6.027 VP CAPITAL CONSULTANT | entity:HQ_6.027_VP_CAPITAL_CONSULTANT |  | VP CAPITAL CONSULTANT 06.027 | 6.027 VP CAPITAL CONSUL. | HQ/6F/6F-2.jpg |  |  | HQ
VAV0339 | VAV | Included | 6.028 VP CAPITAL CONSULTANT | entity:HQ_6.028_VP_CAPITAL_CONSULTANT |  | VP CAPITAL CONSULTANT 06.028 | 6.028 VP CAPITAL CONSUL. | HQ/6F/6F-2.jpg |  |  | HQ
VAV0340 | VAV | Not Included | 6.601 S TOWER CORRIDOR | entity:HQ_6.601_S-TOWER_CORRIDOR |  | CORRIDOR NE | NORTH EAST CORRIDOR | HQ/6F/6F-2.jpg |  |  | HQ
VAV0341 | VAV | Included | 6.109 VP CAPITAL WORK ASSIST | entity:HQ_6.109_VP_CAPITAL_WORK_ASSIST |  | VP CAPITAL WORK ASST 06.109 | 6.109 VP CAPITAL WORK ASSIST | HQ/6F/6F-2.jpg |  |  | HQ
VAV0342 | VAV | Not Included | 6.108 VP CAPITAL PROJ COORD | entity:HQ_6.108_VP_CAPITAL_PROJCOORD |  | VP CAPITAL PROJCOOR 06.108 | 6.108 VP CAPITAL PROJ. COORD | HQ/6F/6F-1.jpg |  |  | HQ
VAV0343 | VAV | Not Included | 6.601 S TOWER CORRIDOR | entity:HQ_6.601_S-TOWER_CORRIDOR |  | CORRIDOR NE | NORTH EAST CORRIDOR | HQ/6F/6F-2.jpg |  |  | HQ
VAV0344 | VAV | Not Included | 6.105 LOUNGE | entity:HQ_6.105_LOUNGE |  |  | 6.105 LOUNGE | HQ/6F/6F-1.jpg |  |  | HQ
VAV0345 | VAV | Not Included | 6.105 LOUNGE | entity:HQ_6.105_LOUNGE |  |  | 6.105 LOUNGE | HQ/6F/6F-1.jpg |  |  | HQ
VAV0346 | VAV | Included | 6.009 INT AUDIT SUPP AUDIT | entity:HQ_6.009_INTAUDIT_SUPPAUDIT |  | INTAUDIT SUPPAUDIT 06.009 | 6.009 INT. AUDIT SUPP. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0347 | VAV | Included | 6.010 INTAUDIT SECRETARY | entity:HQ_6.01_INTAUDIT_SECRETARY |  | INTAUDIT SECRETARY 06.010 | 6.010 INT. AUDIT SEC. | HQ/6F/6F-1.jpg |  |  | HQ
VAV0348 | VAV | Included | 6.011 INTAUDIT SEN JNTAUD | entity:HQ_6.011_INTAUDIT_SEN_JNTAUD |  | INTAUDIT SENJNTAUD 06.011 | 6.011 INT. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0349 | VAV | Included | 6.002 INT AUDIT ARCHIVE ROOM | entity:HQ_6.002_INTAUDIT_ARCHIVE_ROOM |  | INTAUDSUPPAUDIT 06.002 | 6.002 INT. AUDIT ARCHIVE ROOM | HQ/6F/6F-1.jpg |  |  | HQ
VAV0350 | VAV | Included | 6.003 INT AUDIT SUPP AUDIT | entity:HQ_6.003_INTAUDIT_SUPPAUDIT |  | INTAUDSUPPAUDIT 06.003 | 6.003 INT. AUDIT SUPP. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0351 | VAV | Included | 6.004 INT AUDIT SUPP AUDIT | entity:HQ_6.004_INTAUDIT_SUPPAUDIT |  | INTAUDSUPPAUDIT 06.004 | 6.004 INT. AUDIT SUPP. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0352 | VAV | Included | 6.005 INT AUDIT SUPP AUDIT | entity:HQ_6.005_INTAUDIT_SUPPAUDIT |  | INTAUDSUPPAUDIT 06.005 | 6.005 INT. AUDIT SUPP. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0353 | VAV | Included | 6.006 INT AUDIT SUPP AUDIT | entity:HQ_6.006_INTAUDIT_SUPPAUDIT |  | INTAUDSUPPAUDIT 06.006 | 6.006 INT. AUDIT SUPP. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0354 | VAV | Included | 6.007 INT AUDIT SUPP AUDIT | entity:HQ_6.007_INTAUDIT_SUPPAUDIT |  | INTAUDSUPPAUDIT 06.007 | 6.007 INT. AUDIT SUPP. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0355 | VAV | Included | 6.008 INT AUDIT SUPP AUDIT | entity:HQ_6.008_INTAUDIT_SUPPAUDIT |  | INTAUDSUPPAUDIT 06.008 | 6.008 INT. AUDIT SUPP. AUDIT | HQ/6F/6F-1.jpg |  |  | HQ
VAV0356 | VAV | Included | 6.103 SHELL SPACE | entity:HQ_6.103_SHELL_SPACE |  | SHELL SPACE 06.103 | 6.103 OFFICE SPACE | HQ/6F/6F-1.jpg |  |  | HQ
VAV0357 | VAV | Included | 6.102 SHELL SPACE | entity:HQ_6.102_SHELL_SPACE |  | SHELL SPACE 06.102 | 6.102 OFFICE SPACE | HQ/6F/6F-1.jpg |  |  | HQ
VAV0358 | VAV | Included | 6.101 SHELL SPACE | entity:HQ_6.101_SHELL_SPACE |  | SHELL SPACE 06.101 | 6.101 OFFICE SPACE | HQ/6F/6F-1.jpg |  |  | HQ
VAV0359 | VAV | Included | 6.001 ACA AUDIT ARCHIVE | entity:HQ_6.001_ACA_AUDIT_ARCHIVE |  | ACA AUDIT ARCHIVE 06.001 | 6.001 AUDIT ARCHIVE | HQ/6F/6F-1.jpg |  |  | HQ
VAV0360 | VAV | Not Included | 6.601 S TOWER CORRIDOR | entity:HQ_6.601_S-TOWER_CORRIDOR |  | CORRIDOR SW | SOUTH WEST CORRIDOR | HQ/6F/6F-1.jpg |  |  | HQ
VAV0361 | VAV | Not Included | 6.201 VP CAPITAL PROJ MANAGER | entity:HQ_6.201_VP_CAPITAL_PROJMANAGER |  | VP CAPITAL PROJMANAGER 06.201 | 6.201 VP CAPITAL PROJ. MANAGER | HQ/6F/6F-2.jpg |  |  | HQ
VAV0362 | VAV | Not Included | 6.202 VP CAPITAL PROJ MANAGER | entity:HQ_6.202_VP_CAPITAL_PROJMANAGER |  | VP CAPITAL PROJMANAGER 06.202 | 6.202 VP CAPITAL PROJ. MANAGER | HQ/6F/6F-2.jpg |  |  | HQ
VAV0363 | VAV | Not Included | 6.204 VP CAPITAL PROJ MANAGER | entity:HQ_6.204_VP_CAPITAL_PROJMANAGER |  | VP CAPITAL PROJMANAGER 06.204 | 6.204 VP CAPITAL PROJ. MANAGER | HQ/6F/6F-2.jpg |  |  | HQ
VAV0364 | VAV | Not Included | 6.205 VP CAPITAL CONSULTANT | entity:HQ_6.205_VP_CAPITAL_CONSULTANT |  | VP CAPITAL CONSULTANT 06.205 | 6.205 VP CAPITAL CONSU. | HQ/6F/6F-2.jpg |  |  | HQ
VAV0365 | VAV | Not Included | 6.206 VP CAPITAL STORAGE | entity:HQ_6.206_VP_CAPITAL_STORAGE |  |  | 6.206 VP CAPITAL STORAGE | HQ/6F/6F-2.jpg |  |  | HQ
VAV0366 | VAV | Included | 6.207 VP CAPITAL SECRETARIES | entity:HQ_6.207_VP_CAPITAL_SECRETARIES |  | VP CAPITAL SECRETARIES 06.207 | 6.207 VP CAPITAL SEC. | HQ/6F/6F-2.jpg |  |  | HQ
VAV0367 | VAV | Not Included | 6.209 VP CAPITAL ENSUIT | entity:HQ_6.209_VP_CAPITAL_ENSUIT |  |  | 6.209 VP CAPITAL ENSUIT | HQ/6F/6F-2.jpg |  |  | HQ
VAV0368 | VAV | Included | 6.210 VP CAPITAL SECRETARIES | entity:HQ_6.21_VP_CAPITAL_SECRETARIES |  | VP CAPITAL SECRETARIES 06.210 | 6.210 VP CAPITAL SEC. | HQ/6F/6F-2.jpg |  |  | HQ
VAV0369 | VAV | Included | 6.211 VP CAPITAL SECRETARIES | entity:HQ_6.211_VP_CAPITAL_SECRETARIES |  | VP CAPITAL SECRETARIES 06.211 | 6.211 VP CAPITAL SEC. | HQ/6F/6F-2.jpg |  |  | HQ
VAV0370 | VAV | Not Included | 6.212 VP CAPITAL DIRECTOR ENSUIT | entity:HQ_6.212_VP_CAPITAL_DIRECTOR_ENSUIT |  | VP CAPITAL DIRENSUIT 06.212 | 6.212 VP CAPITAL DIR. ENSUIT | HQ/6F/6F-2.jpg |  |  | HQ
VAV0371 | VAV | Not Included | 6.603 E TOWER CORRIDOR | entity:HQ_6.603_E-TOWER_CORRIDOR |  | CORRIDOR SE | E-TOWER CORRIDOR | HQ/6F/6F-2.jpg |  |  | HQ
VAV0372 | VAV | Not Included | 6.603 E TOWER CORRIDOR | entity:HQ_6.603_E-TOWER_CORRIDOR |  | CORRIDOR 6.603 | E-TOWER CORRIDOR | HQ/6F/6F-2.jpg |  |  | HQ
VAV0373 | VAV | Included | 7.017 CA ENSUIT | entity:HQ_7.017_CA_ENSUIT |  |  | 7.017 CA ENSUIT | HQ/7F/7F-1.jpg |  |  | HQ
VAV0374 | VAV | Included | 7.018 CA SECRETARY | entity:HQ_7.018_CA_SECRETARY |  | CA SECRETARY 7.018 | 7.018 CA SEC. | HQ/7F/7F-1.jpg |  |  | HQ
VAV0375 | VAV | Included | 7.019 BD UNIT SECRETARY | entity:HQ_7.019_BD_UNIT_SECRETARY |  | BD UNIT SECRETARY 7.019 | 7.019 BD UNIT SEC. | HQ/7F/7F-1.jpg |  |  | HQ
VAV0376 | VAV | Included | 7.020 BD UNIT EXECUTIVE | entity:HQ_7.02_BD_UNIT_EXECUTIVE |  | BD UNIT EXECUTIVE 7.020 | 7.020 BD UNIT EXECU. | HQ/7F/7F-1.jpg |  |  | HQ
VAV0377 | VAV | Included | 7.021 BD UNIT EXECUTIVE | entity:HQ_7.021_BD_UNIT_EXECUTIVE |  | BD UNIT EXECUTIVE 7.021 | 7.021 BD UNIT EXECU. | HQ/7F/7F-1.jpg |  |  | HQ
VAV0378 | VAV | Included | 7.022 BD UNIT EXECUTIVE | entity:HQ_7.022_BD_UNIT_EXECUTIVE |  | BD UNIT EXECUTIVE 7.022 | 7.022 BD UNIT EXECU. | HQ/7F/7F-1.jpg |  |  | HQ
VAV0379 | VAV | Included | 7.023 BD UNIT EXECUTIVE | entity:HQ_7.023_BD_UNIT_EXECUTIVE |  | BD UNIT EXECUTIVE 7.023 | 7.023 BD UNIT EXECU. | HQ/7F/7F-1.jpg |  |  | HQ
VAV0380 | VAV | Included | 7.024 BD UNIT EXECUTIVE | entity:HQ_7.024_BD_UNIT_EXECUTIVE |  | BD UNIT EXECUTIVE 7.024 | 7.024 BD UNIT EXECU. | HQ/7F/7F-1.jpg |  |  | HQ
VAV0381 | VAV | Included | 7.025 BD UNIT EXECUTIVE | entity:HQ_7.025_BD_UNIT_EXECUTIVE |  | BD UNIT EXECUTIVE 7.025 | 7.025 BD UNIT EXECU. | HQ/7F/7F-2.jpg |  |  | HQ
VAV0382 | VAV | Included | 7.026 BD UNIT EXECUTIVE | entity:HQ_7.026_BD_UNIT_EXECUTIVE |  | BD UNIT EXECUTIVE 7.026 | 7.026 BD UNIT EXECU. | HQ/7F/7F-2.jpg |  |  | HQ
VAV0383 | VAV | Included | 7.027 BD UNIT EXECUTIVE | entity:HQ_7.027_BD_UNIT_EXECUTIVE |  | BD UNIT EXECUTIVE 7.027 | 7.027 BD UNIT EXECU. | HQ/7F/7F-2.jpg |  |  | HQ
VAV0384 | VAV | Included | 7.028 BD UNIT EXECUTIVE | entity:HQ_7.028_BD_UNIT_EXECUTIVE |  | BD UNIT EXECUTIVE 7.028 | 7.028 BD UNIT EXECU. | HQ/7F/7F-2.jpg |  |  | HQ
VAV0385 | VAV | Included | 7.029 MEETING ROOM | entity:HQ_7.029_MEETING_ROOM |  |  | 7.029 MEETING ROOM | HQ/7F/7F-2.jpg |  |  | HQ
VAV0386 | VAV | Included | 7.029 MEETING ROOM | entity:HQ_7.029_MEETING_ROOM |  |  | 7.029 MEETING ROOM | HQ/7F/7F-2.jpg |  |  | HQ
VAV0387 | VAV | Included | 7.030 SHELL SPACE | entity:HQ_7.03_SHELL_SPACE |  | SHELL SPACE 7.030 | 7.030 OFFICE SPACE | HQ/7F/7F-2.jpg |  |  | HQ
VAV0388 | VAV | Included | 7.031A OFFICE SPACE | entity:HQ_7.031A_OFFICE_SPACE |  | SHELL SPACE 7.031A | 7.031A OFFICE SPACE | HQ/7F/7F-2.jpg |  |  | HQ
VAV0389 | VAV | Not Included | 7.601 S TOWER CORRIDOR | entity:HQ_7.601_S-TOWER_CORRIDOR |  | CORRIDOR NE | NORTH EAST CORRIDOR | HQ/7F/7F-2.jpg |  |  | HQ
VAV0390 | VAV | Not Included | 7.601 S TOWER CORRIDOR | entity:HQ_7.601_S-TOWER_CORRIDOR |  | CORRIDOR 7.601 | NORTH EAST CORRIDOR | HQ/7F/7F-2.jpg |  |  | HQ
VAV0391 | VAV | Included | 7.032 SHELL SPACE | entity:HQ_7.032_SHELL_SPACE |  | SHELL SPACE 7.032 | 7.032 OFFICE SPACE | HQ/7F/7F-1.jpg |  |  | HQ
VAV0392 | VAV | Included | 7.032 SHELL SPACE | entity:HQ_7.032_SHELL_SPACE |  |  | 7.032 OFFICE SPACE | HQ/7F/7F-1.jpg |  |  | HQ
VAV0393 | VAV | Not Included | 7.106 LOUNGE | entity:HQ_7.106_LOUNGE |  |  | 7.106 LOUNGE | HQ/7F/7F-1.jpg |  |  | HQ
VAV0394 | VAV | Included | 7.105 CA SECRETARY | entity:HQ_7.105_CA_SECRETARY |  |  | 7.105 CA SECRETARY | HQ/7F/7F-1.jpg |  |  | HQ
VAV0395 | VAV | Included | 7.103 CA SECRETARY | entity:HQ_7.103_CA_SECRETARY |  |  | 7.103 CA SECRETARY | HQ/7F/7F-1.jpg |  |  | HQ
VAV0396 | VAV | Included | 7.102 CA SECRETARY | entity:HQ_7.102_CA_SECRETARY |  |  | 7.102 CA SECRETARY | HQ/7F/7F-1.jpg |  |  | HQ
VAV0397 | VAV | Included | 7.001 DOC UNIT EMPLOYEE | entity:HQ_7.001_DOCUNIT_EMPLOYEE |  | DOCS UNIT EMPLOYEE 07.001 | 7.001 DOC. UNIT EMPLOYEE | HQ/7F/7F-1.jpg |  |  | HQ
VAV0398 | VAV | Included | 7.002 DOC UNIT MULTIMEDIA STUDIO | entity:HQ_7.002_DOCUNIT_MULTIMEDIA_STUDIO |  | DOCS UNIT MULTIMEDIA STU 07.002 | 7.002 DOC. UNIT MULTIMEDIA STUDIO | HQ/7F/7F-1.jpg |  |  | HQ
VAV0399 | VAV | Not Included | 7.601 S TOWER CORRIDOR | entity:HQ_7.601_S-TOWER_CORRIDOR |  | CORRIDOR SW | SOUTH WEST CORRIDOR | HQ/7F/7F-1.jpg |  |  | HQ
VAV0400 | VAV | Included | 7.002 DOC UNIT MULTIMEDIA STUDIO | entity:HQ_7.002_DOCUNIT_MULTIMEDIA_STUDIO |  |  | 7.002 DOC. UNIT MULTIMEDIA STUDIO | HQ/7F/7F-1.jpg |  |  | HQ
VAV0401 | VAV | Included | 7.003 DOC UNIT EMPLOYEE | entity:HQ_7.003_DOCUNIT_EMPLOYEE |  | DOCS UNIT EMPLOYEE 7.003 | 7.003 DOC. UNIT EMPLOYEE | HQ/7F/7F-1.jpg |  |  | HQ
VAV0402 | VAV | Included | 7.004 DOC UNIT EMPLOYEE | entity:HQ_7.004_DOCUNIT_EMPLOYEE |  | DOCS UNIT EMPLOYEE 7.004 | 7.004 DOC. UNIT EMPLOYEE | HQ/7F/7F-1.jpg |  |  | HQ
VAV0403 | VAV | Included | 7.005 DOC UNIT EMPLOYEE | entity:HQ_7.005_DOCUNIT_EMPLOYEE |  | DOCS UNIT EMPLOYEE 7.005 | 7.005 DOC. UNIT EMPLOYEE | HQ/7F/7F-1.jpg |  |  | HQ
VAV0404 | VAV | Included | 7.006 DOC UNIT EMPLOYEE | entity:HQ_7.006_DOCUNIT_EMPLOYEE |  | DOCS UNIT EMPLOYEE 7.006 | 7.006 DOC. UNIT EMPLOYEE | HQ/7F/7F-1.jpg |  |  | HQ
VAV0405 | VAV | Included | 7.007 CA COORD | entity:HQ_7.007_CA_COORD |  |  | 7.007 CA COORD | HQ/7F/7F-1.jpg |  |  | HQ
VAV0406 | VAV | Included | 7.008 CA COORD | entity:HQ_7.008_CA_COORD |  |  | 7.008 CA COORD | HQ/7F/7F-1.jpg |  |  | HQ
VAV0407 | VAV | Included | 7.009 CA COORD | entity:HQ_7.009_CA_COORD |  |  | 7.009 CA COORD | HQ/7F/7F-1.jpg |  |  | HQ
VAV0408 | VAV | Included | 7.010 CA COORD | entity:HQ_7.01_CA_COORD |  |  | 7.010 CA COORD | HQ/7F/7F-1.jpg |  |  | HQ
VAV0409 | VAV | Included | 7.011 CA COORD | entity:HQ_7.011_CA_COORD |  |  | 7.011 CA COORD | HQ/7F/7F-1.jpg |  |  | HQ
VAV0410 | VAV | Included | 7.012 CA COORD | entity:HQ_7.012_CA_COORD |  |  | 7.012 CA COORD | HQ/7F/7F-1.jpg |  |  | HQ
VAV0411 | VAV | Included | 7.013 CA COORD | entity:HQ_7.013_CA_COORD |  |  | 7.013 CA COORD | HQ/7F/7F-1.jpg |  |  | HQ
VAV0412 | VAV | Included | 7.014 CA COORD | entity:HQ_7.014_CA_COORD |  |  | 7.014 CA COORD | HQ/7F/7F-1.jpg |  |  | HQ
VAV0413 | VAV | Included | 7.015 CA COORD | entity:HQ_7.015_CA_COORD |  |  | 7.015 CA COORD | HQ/7F/7F-1.jpg |  |  | HQ
VAV0414 | VAV | Included | 7.016 CA COORD | entity:HQ_7.016_CA_COORD |  |  | 7.016 CA COORD | HQ/7F/7F-1.jpg |  |  | HQ
VAV0415 | VAV | Included | 7.201 CONSULTANT SPACE | entity:HQ_7.201_CONSULTANTS_SPACE |  |  | 7.201 CONSULTANT SPACE | HQ/7F/7F-2.jpg |  |  | HQ
VAV0416 | VAV | Not Included | 7.202 PRESIDENT EXECOFFICE | entity:HQ_7.202_PRESIDENT_EXECOFFICE |  | PRESIDENT EXECOFF 7.202 | 7.202 PRE. EXEC. OFFICE | HQ/7F/7F-2.jpg |  |  | HQ
VAV0417 | VAV | Not Included | 7.204 PRESIDENT EXECOFFICE | entity:HQ_7.204_PRESIDENT_EXECOFFICE |  | PRESSEXECOFFICE 7.204 | 7.204 PRE. EXEC. OFFICE | HQ/7F/7F-2.jpg |  |  | HQ
VAV0418 | VAV | Not Included | 7.204 PRESIDENT EXECOFFICE | entity:HQ_7.204_PRESIDENT_EXECOFFICE |  | PRESSEXECOFFICE 7.204 | 7.204 PRE. EXEC. OFFICE | HQ/7F/7F-2.jpg |  |  | HQ
VAV0419 | VAV | Not Included | 7.205 PRESIDENT EXECOFFICE | entity:HQ_7.205_PRESIDENT_EXECOFFICE |  | PRESSEXECOFFICE 07.206 | 7.205 PRE. EXEC. OFFICE | HQ/7F/7F-2.jpg |  |  | HQ
VAV0420 | VAV | Not Included | 7.205 PRESIDENT EXECOFFICE | entity:HQ_7.205_PRESIDENT_EXECOFFICE |  | PRESSEXECOFFICE 7.205 | 7.205 PRE. EXEC. OFFICE | HQ/7F/7F-2.jpg |  |  | HQ
VAV0421 | VAV | Included | 7.208 PRESIDENT SUPPORT SECRET | entity:HQ_7.208_PRESIDENT_SUPPORT_SECRET |  | PRESSSUPPSECRET 7.208 | 7.208 PRESIDENT SUPP. SEC. | HQ/7F/7F-2.jpg |  |  | HQ
VAV0422 | VAV | Not Included | 7.603 E TOWER CORRIDOR | entity:HQ_7.603_E-TOWER_CORRIDOR |  | CORRIDOR SE | E-TOWER CORRIDOR 7.603 | HQ/7F/7F-2.jpg |  |  | HQ
VAV0423 | VAV | Included | 7.209 PRESIDENT EXECSECRET | entity:HQ_7.209_PRESIDENT_EXECSECRET |  | PRESSEXECSECRET 7.209 | 7.209 PRESIDENT EXEC. SEC. | HQ/7F/7F-2.jpg |  |  | HQ
VAV0424 | VAV | Included | 7.210 PRESIDENT EXECSECRET | entity:HQ_7.21_PRESIDENT_EXECSECRET |  | PRESSEXECSECRET 7.210 | 7.210 PRESIDENT EXEC. SEC. | HQ/7F/7F-2.jpg |  |  | HQ
VAV0425 | VAV | Not Included | 7.211 PRESIDENT ENSUIT | entity:HQ_7.211_PRESIDENT_ENSUIT |  | PRESSIDENT ENSUIT 7.211 | 7.211 PRESIDENT ENSUIT | HQ/7F/7F-2.jpg |  |  | HQ
VAV0426 | VAV | Not Included | 7.212 PRESIDENT MEETING ROOM | entity:HQ_7.212_PRESIDENT_MEETING_ROOM |  | PRESSIDENT MEETINF RM 7.212 | 7.212 PRESIDENT MEETING ROOM | HQ/7F/7F-2.jpg |  |  | HQ
VAV0427 | VAV | Included | 7.213 VICE CHAIRPERSON ENSULT | entity:HQ_7.213_VICE_CHAIRPERSON_ENSUIT |  | VICE CHAIRPENSUIT 7.213 | 7.213 VICE CHAIRPERSON ENSUIT | HQ/7F/7F-2.jpg |  |  | HQ
VAV0428 | VAV | Included | 7.214 VICE CHAIRSECRETARY | entity:HQ_7.214_VICE_CHAIRSECRETARY |  | VICE CHAIRPSECT 7.214 | 7.214 VICE CHAIRPERSON SEC. | HQ/7F/7F-2.jpg |  |  | HQ
VAV0429 | VAV | Included | 7.215 VICE CHAIRPERSON MEETING ROOM | entity:HQ_7.215_VICE_CHAIRPERSON_MEETING_ROOM |  | VICE CHAIRPMEETING RM 7.215 | 7.215 MEETING ROOM | HQ/7F/7F-2.jpg |  |  | HQ
VAV0430 | VAV | Included | 7.301 MEETING ROOM | entity:HQ_7.301_MEETING_ROOM |  | E-TOWER CORRIDOR 06.301 | 7.301 MEETING ROOM | HQ/7F/7F-2.jpg |  |  | HQ
VAV0431 | VAV | Included | 7.301 MEETING ROOM | entity:HQ_7.301_MEETING_ROOM |  |  | 7.301 MEETING ROOM | HQ/7F/7F-2.jpg |  |  | HQ
VAV0432 | VAV | Included | 7.301 MEETING ROOM | entity:HQ_7.301_MEETING_ROOM |  |  | 7.301 MEETING ROOM | HQ/7F/7F-2.jpg |  |  | HQ
VAV0433 | VAV | Not Included | 8.001 OBSERVATION SPACE | entity:HQ_8.001_OBSERVATION_SPACE |  |  | 8.001 OBSERVATION SPACE | HQ/8F/8F.jpg |  |  | HQ
VAV0434 | VAV | Not Included | 8.001 OBSERVATION SPACE | entity:HQ_8.001_OBSERVATION_SPACE |  |  | 8.001 OBSERVATION SPACE | HQ/8F/8F.jpg |  |  | HQ
VAV0435 | VAV | Not Included | 8.001 OBSERVATION SPACE | entity:HQ_8.001_OBSERVATION_SPACE |  |  | 8.001 OBSERVATION SPACE | HQ/8F/8F.jpg |  |  | HQ
VAV0436 | VAV | Not Included | 8.001 OBSERVATION SPACE | entity:HQ_8.001_OBSERVATION_SPACE |  |  | 8.001 OBSERVATION SPACE | HQ/8F/8F.jpg |  |  | HQ
VAV0437 | VAV | Not Included | 8.001 OBSERVATION SPACE | entity:HQ_8.001_OBSERVATION_SPACE |  |  | 8.001 OBSERVATION SPACE | HQ/8F/8F.jpg |  |  | HQ
VAV0438 | VAV | Not Included | 8.002 VISITORS CENTER OFFICE | entity:HQ_8.002_VISITORS_CENTER_OFFICE |  |  | 8.002 VISITORS CENTER OFFICE | HQ/8F/8F.jpg |  |  | HQ
VAV0439 | VAV | Not Included | 8.602 VISITORS CENTER CORRIDOR | entity:HQ_8.602_VISITORS_CENTER_CORRIDOR |  | VISITORS CENTER CORRIDOR 08.201 | 8.602 VISITORS CENTER CORRIDOR | HQ/8F/8F.jpg |  |  | HQ
VAV0440 | VAV | Not Included | 8.602 VISITORS CENTER CORRIDOR | entity:HQ_8.602_VISITORS_CENTER_CORRIDOR |  |  | 8.602 VISITORS CENTER CORRIDOR | HQ/8F/8F.jpg |  |  | HQ
VAV0441 | VAV | Not Included | 8.602 VISITORS CENTER CORRIDOR | entity:HQ_8.602_VISITORS_CENTER_CORRIDOR |  |  | 8.602 VISITORS CENTER CORRIDOR | HQ/8F/8F.jpg |  |  | HQ
VAV0442 | VAV | Not Included | 8.602 VISITORS CENTER CORRIDOR | entity:HQ_8.602_VISITORS_CENTER_CORRIDOR |  |  | 8.602 VISITORS CENTER CORRIDOR | HQ/8F/8F.jpg |  |  | HQ
VAV0443 | VAV | Not Included | 8.602 VISITORS CENTER CORRIDOR | entity:HQ_8.602_VISITORS_CENTER_CORRIDOR |  |  | 8.602 VISITORS CENTER CORRIDOR | HQ/8F/8F.jpg |  |  | HQ
VAV0444 | VAV | Included | 9.011 BMO EXEC ASSIST | entity:HQ_9.011_BMO_EXECASSIST |  | BMO EXECASSIST 9.011 | 9.011 BMO EXEC. ASSIST. | HQ/9F/9F-1.jpg |  |  | HQ
VAV0445 | VAV | Included | 9.012 BMO EXEC ASSIST | entity:HQ_9.012_BMO_EXECASSIST |  | BMO EXECASSIST 9.012 | 9.012 BMO EXEC. ASSIST. | HQ/9F/9F-1.jpg |  |  | HQ
VAV0446 | VAV | Included | 9.013 BMO EXEC ASSIST | entity:HQ_9.013_BMO_EXECASSIST |  | BMO EXECASSIST 9.013 | 9.013 BMO EXEC. ASSIST. | HQ/9F/9F-1.jpg |  |  | HQ
VAV0447 | VAV | Included | 9.014 BMO EXEC ASSIST | entity:HQ_9.014_BMO_EXECASSIST |  | BMO EXECASSIST 9.014 | 9.014 BMO EXEC. ASSIST. | HQ/9F/9F-1.jpg |  |  | HQ
VAV0448 | VAV | Included | 9.015 BMO EXEC ASSIST | entity:HQ_9.015_BMO_EXECASSIST |  | BMO EXECASSIST 9.015 | 9.015 BMO EXEC. ASSIST. | HQ/9F/9F-1.jpg |  |  | HQ
VAV0449 | VAV | Included | 9.016 BMO EXEC ASSIST | entity:HQ_9.016_BMO_EXECASSIST |  | BMO EXECASSIST 9.016 | 9.016 BMO EXEC. ASSIST. | HQ/9F/9F-1.jpg |  |  | HQ
VAV0450 | VAV | Included | 9.017 BMO EXEC ASSIST | entity:HQ_9.017_BMO_EXECASSIST |  | BMO EXECASSIST 9.017 | 9.017 BMO EXEC. ASSIST. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0451 | VAV | Included | 9.018 BMO EXECSECRET | entity:HQ_9.018_BMO_EXECSECRET |  | BMO EXECSECRET 9.018 | 9.018 BMO EXEC. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0452 | VAV | Included | 9.019 BMO EXECSECRET | entity:HQ_9.019_BMO_EXECSECRET |  | BMO EXECSECRET 9.019 | 9.019 BMO EXEC. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0453 | VAV | Included | 9.020 BMO EXECSECRET | entity:HQ_9.02_BMO_EXECSECRET |  | BMO EXECSECRET 9.020 | 9.020 BMO EXEC. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0454 | VAV | Not Included | 9.021 BMO OPER DIR ENSUIT | entity:HQ_9.021_BMO_OPERDIRENSUIT |  | BMO OPERDIRENSUIT 9.021 | 9.021 BMO OPER. DIR. ENSUIT | HQ/9F/9F-2.jpg |  |  | HQ
VAV0455 | VAV | Included | 9.022 BMO EXEC ASSIST | entity:HQ_9.022_BMO_EXECASSIST |  | BMO EXECASSIST 9.022 | 9.022 BMO EXEC. ASSIST. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0456 | VAV | Included | 9.023 BMO EXECSECRET | entity:HQ_9.023_BMO_EXECSECRET |  | BMO EXECSECRET 9.023 | 9.023 BMO EXEC. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0457 | VAV | Included | 9.024 BMO EXECSECRET | entity:HQ_9.024_BMO_EXECSECRET |  | BMO EXECSECRET 9.024 | 9.024 BMO EXEC. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0458 | VAV | Included | 9.025 BMO EXECSECRET | entity:HQ_9.025_BMO_EXECSECRET |  | BMO EXECSECRET 9.025 | 9.025 BMO EXEC. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0459 | VAV | Included | 9.025 BMO EXECSECRET | entity:HQ_9.025_BMO_EXECSECRET |  |  | 9.025 BMO EXEC. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0460 | VAV | Included | 9.026 BMO SUPPSECRET | entity:HQ_9.026_BMO_SUPPSECRET |  | BMO SUPPSECRET 9.026 | 9.026 BMO SUPP. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0461 | VAV | Included | 9.027 BMO SUPPSECRET | entity:HQ_9.027_BMO_SUPPSECRET |  | BMO SUPPSECRET 9.027 | 9.027 BMO SUPP. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0462 | VAV | Included | 9.028 BMO SUPPSECRET | entity:HQ_9.028_BMO_SUPPSECRET |  | BMO SUPPSECRET 9.028 | 9.028 BMO SUPP. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0463 | VAV | Included | 9.029 BMO SUPPSECRET | entity:HQ_9.029_BMO_SUPPSECRET |  | BMO SUPPSECRET 9.029 | 9.029 BMO SUPP. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0464 | VAV | Included | 9.030 BMO SUPPSECRET | entity:HQ_9.03_BMO_SUPPSECRET |  | BMO SUPPSECRET 9.030 | 9.030 BMO SUPP. SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0465 | VAV | Included | 9.031 BMO PRINT COPY | entity:HQ_9.031_BMO_PRINT_COPY |  |  | 9.031 BMO PRINT COPY | HQ/9F/9F-2.jpg |  |  | HQ
VAV0466 | VAV | Included | 9.032 BMO STORAGE | entity:HQ_9.032_BMO_STORAGE |  | BMO PRINT STORAGE 9.032 | 9.032 BMO STORAGE | HQ/9F/9F-2.jpg |  |  | HQ
VAV0467 | VAV | Included | 9.033 HR EDUADVADVISOR ENSUIT | entity:HQ_9.033_HR_EDUADVADVISOR_ENSUIT |  | HR EDUADVADVENSUIT 9.033 | 9.033 HR EDU. ADV. ENSUIT | HQ/9F/9F-2.jpg |  |  | HQ
VAV0468 | VAV | Included | 9.034 HR EDUADVADVISOR ENSUIT | entity:HQ_9.034_HR_EDUADVADVISOR_ENSUIT |  | HR EDUADVADVENSUIT 9.034 | 9.034 HR EDU. ADV. ENSUIT | HQ/9F/9F-2.jpg |  |  | HQ
VAV0469 | VAV | Included | 9.035 HR EDUADVADVISOR ENSUIT | entity:HQ_9.035_HR_EDUADVADVISOR_ENSUIT |  | HR EDUADVADVENSUIT 9.035 | 9.035 HR EDU. ADV. ENSUIT | HQ/9F/9F-2.jpg |  |  | HQ
VAV0470 | VAV | Not Included | 9.036 BOD EXECUTIVE | entity:HQ_9.036_BOD_EXECUTIVE |  |  | 9.036 BOD EXECUTIVE | HQ/9F/9F-2.jpg |  |  | HQ
VAV0471 | VAV | Included | 9.037 BOD SECRETARY | entity:HQ_9.037_BOD_SECRETARY |  | BOD SECRETARY 9.037 | 9.037 BOD SEC. | HQ/9F/9F-2.jpg |  |  | HQ
VAV0472 | VAV | Not Included | 9.038 BOD EXECUTIVE | entity:HQ_9.038_BOD_EXECUTIVE |  | BOD SECRETARY 9.038 | 9.038 BOD EXECUTIVE | HQ/9F/9F-1.jpg |  |  | HQ
VAV0473 | VAV | Not Included | 9.601 HH WING CORRIDOR | entity:HQ_9.601_HH-WING_CORRIDOR |  | CORRIDOR SE | SOUTH WEST CORRIDOR | HQ/9F/9F-1.jpg |  |  | HQ
VAV0474 | VAV | Not Included | 9.601 HH WING CORRIDOR | entity:HQ_9.601_HH-WING_CORRIDOR |  | HH-WING CORRIDOR SW | HH-WING CORRIDOR 9.601 | HQ/9F/9F-1.jpg |  |  | HQ
VAV0475 | VAV | Included | 9.039 MEETING ROOM | entity:HQ_9.039_MEETING_ROOM |  |  | 9.039 MEETING ROOM | HQ/9F/9F-1.jpg |  |  | HQ
VAV0476 | VAV | Included | 9.040 BMO SAFE ROOM | entity:HQ_9.04_BMO_SAFE_ROOM |  | BMO SAFE ROOM 9.040 | 9.040 BMO SAFE | HQ/9F/9F-1.jpg |  |  | HQ
VAV0477 | VAV | Included | 9.041 BMO ARCHIVE ROOM | entity:HQ_9.041_BMO_ARCHIVE_ROOM |  |  | 9.041 BMO ARCHIVE ROOM | HQ/9F/9F-1.jpg |  |  | HQ
VAV0478 | VAV | Not Included | 9.601 HH WING CORRIDOR | entity:HQ_9.601_HH-WING_CORRIDOR |  | CORRIDOR SW | SOUTH WEST CORRIDOR | HQ/9F/9F-1.jpg |  |  | HQ
VAV0479 | VAV | Included | 9.001 LEGAL ARCHIVE | entity:HQ_9.001_LEGAL_ARCHIVE |  |  | 9.001 LEGAL ARCHIVE | HQ/9F/9F-1.jpg |  |  | HQ
VAV0480 | VAV | Included | 9.002 LEGAL CONSULE | entity:HQ_9.002_LEGAL_CONSULE |  |  | 9.002 LEGAL CONSULE | HQ/9F/9F-1.jpg |  |  | HQ
VAV0481 | VAV | Included | 9.003 LEGAL LEGAL CONSULE | entity:HQ_9.003_LEGAL_LEGAL_CONSULE |  |  | 9.003 LEGAL CONSULE | HQ/9F/9F-1.jpg |  |  | HQ
VAV0482 | VAV | Included | 9.004 LEGAL LEGAL CONSULE | entity:HQ_9.004_LEGAL_LEGAL_CONSULE |  |  | 9.004 LEGAL CONSULE | HQ/9F/9F-1.jpg |  |  | HQ
VAV0483 | VAV | Included | 9.005 LEGAL LEGAL CONSULE | entity:HQ_9.005_LEGAL_LEGAL_CONSULE |  |  | 9.005 LEGAL CONSULE | HQ/9F/9F-1.jpg |  |  | HQ
VAV0484 | VAV | Included | 9.006 LEGAL LEGAL CONSULE | entity:HQ_9.006_LEGAL_LEGAL_CONSULE |  |  | 9.006 LEGAL CONSULE | HQ/9F/9F-1.jpg |  |  | HQ
VAV0485 | VAV | Included | 9.007 LEGAL LEGAL CONSULE | entity:HQ_9.007_LEGAL_LEGAL_CONSULE |  |  | 9.007 LEGAL CONSULE | HQ/9F/9F-1.jpg |  |  | HQ
VAV0486 | VAV | Included | 9.008 LEGAL LEGSUPSEC | entity:HQ_9.008_LEGAL_LEGSUPSEC |  |  | 9.008 LEGAL SUP. SEC. | HQ/9F/9F-1.jpg |  |  | HQ
VAV0487 | VAV | Included | 9.009 LEGAL LEGSUPSEC | entity:HQ_9.009_LEGAL_LEGSUPSEC |  |  | 9.009 LEGAL SUP. SEC. | HQ/9F/9F-1.jpg |  |  | HQ
VAV0488 | VAV | Included | 9.010 LEGAL LEGADVENSUIT | entity:HQ_9.01_LEGAL_LEGADVENSUIT |  |  | 9.010 LEGAL ADV. ENSUIT | HQ/9F/9F-1.jpg |  |  | HQ
VAV0489 | VAV | Not Included | 9.105 LOUNGE | entity:HQ_9.105_LOUNGE |  | LOUNGE NW | 9.105 LOUNGE | HQ/9F/9F-1.jpg |  |  | HQ
VAV0490 | VAV | Not Included | 9.104 BMO WAITING AREA | entity:HQ_9.104_BMO_WAITING_AREA |  |  | 9.104 BMO WAITING AREA | HQ/9F/9F-1.jpg |  |  | HQ
VAV0491 | VAV | Included | 9.104 BMO WAITING AREA | entity:HQ_9.403_MALE_TOILET |  |  | 9.104 BMO WAITING AREA | HQ/9F/9F-1.jpg |  |  | HQ
VAV0492 | VAV | Not Included | 9.601 HH WING CORRIDOR | entity:HQ_9.601_HH-WING_CORRIDOR |  | CORRIDOR NE | NORTH EAST CORRIDOR | HQ/9F/9F-2.jpg |  |  | HQ
VAV0493 | VAV | Not Included | 9.110 SHEIKA WING DINING AREA | entity:HQ_9.11_SHEIKA_WING_DINING_AREA |  | OUTSIDE SHEIKA WING DINING AREA 9.110 | 9.110 SHEIKA WING DINING AREA | HQ/9F/9F-2.jpg |  |  | HQ
VAV0494 | VAV | Not Included | 9.110 SHEIKA WING DINING AREA | entity:HQ_9.11_SHEIKA_WING_DINING_AREA |  | SHEIKA WING DINING AREA SE | 9.110 SHEIKA WING DINING AREA | HQ/9F/9F-2.jpg |  |  | HQ
VAV0495 | VAV | Not Included | 9.110 SHEIKA WING DINING AREA | entity:HQ_9.11_SHEIKA_WING_DINING_AREA |  | OUTSIDE SHEIKA WING DINING AREA 9.11 | SOUTH EAST CORRIDOR | HQ/9F/9F-2.jpg |  |  | HQ
VAV0496 | VAV | Included | 9.108 SUPPORT SPACE PREP KITCHEN | entity:HQ_9.108_SUPPORT_SPACE_PREPKITCHEN |  |  | 9.108 KITCHEN | HQ/9F/9F-2.jpg |  |  | HQ
VAV0497 | VAV | Not Included | 9.110 SHEIKA WING DINING AREA | entity:HQ_9.11_SHEIKA_WING_DINING_AREA |  |  |  | HQ/9F/9F-2.jpg |  |  | HQ
VAV0498 | VAV | Included | 10.005 SHEIKHA WING ARCHIVE | entity:HQ_10.005_SHEIKHA_WING_ARCHIVE |  | SHEIKA WING ARCHIVE 10.005 | 10.005 ARCHIVE | HQ/10F/10F-1.jpg |  |  | HQ
VAV0499 | VAV | Not Included | 10.006 EXEC DIR ARCH COORD | entity:HQ_10.006_EXECDIRARCHCOORD |  | EXECDIRARCH COORD 10.006 | 10.006 EXEC. DIR. ARCH. COORD | HQ/10F/10F-1.jpg |  |  | HQ
VAV0500 | VAV | Included | 10.007 EXEC DIR PROT ASSIS | entity:HQ_10.007_EXECDIR_PROTASSIST |  | EXECDIRARCH COORD 10.007 | 10.007 EXEC. DIR. PROT. ASSIS. | HQ/10F/10F-1.jpg |  |  | HQ
VAV0501 | VAV | Included | 10.008 PROTOCOL DIR SCHED OFFICER | entity:HQ_10.008_PROTOCOL_DIR_SCHED_OFFICER |  | PROTOCOL DIRSCHEDOFF 10.008 | 10.008 SCHED OFFICER | HQ/10F/10F-1.jpg |  |  | HQ
VAV0502 | VAV | Included | 10.009 PROTOCOL DIR CEREMOFF | entity:HQ_10.009_PROTOCOL_DIR_CEREMOFF |  | PROTOCOL DIRCEREMOFF 10.009 | 10.009 CEREM. OFFICER | HQ/10F/10F-1.jpg |  |  | HQ
VAV0503 | VAV | Included | 10.010 PROTOCOL DIR CEREMOFF | entity:HQ_10.01_PROTOCOL_DIR_CEREMOFF |  | PROTOCOL DIRCEREMOFF 10.010 | 10.010 CEREM. OFFICER | HQ/10F/10F-1.jpg |  |  | HQ
VAV0504 | VAV | Included | 10.011 PROTOCOL DIR CEREMOFF | entity:HQ_10.011_PROTOCOL_DIR_CEREMOFF |  | PROTOCOL DIRCEREMOFF 10.011 | 10.011 CEREM. OFFICER | HQ/10F/10F-1.jpg |  |  | HQ
VAV0505 | VAV | Included | 10.012 PROTOCOL DIR TR AND VIS OFF | entity:HQ_10.012_PROTOCOL_DIR_TR_&_VIS_OFF |  | PROTOCOL DIRTR/VISOFF 10.012 | 10.012 TR. & VIS. OFFICER | HQ/10F/10F-1.jpg |  |  | HQ
VAV0506 | VAV | Included | 10.013 PROTOCOL DIR TR AND VIS OFF | entity:HQ_10.013_PROTOCOL_DIR_TR_&_VIS_OFF |  | PROTOCOL DIRTR/VISOFF 10.013 | 10.013 TR. & VIS. OFFICER | HQ/10F/10F-1.jpg |  |  | HQ
VAV0507 | VAV | Included | 10.015 PROTOCOL DIR SCHED OFFICER | entity:HQ_10.015_PROTOCOL_DIRSCHED_OFFICER |  | PROTOCOL DIRSCHEDOFF 10.015 | 10.015 SCHED OFFICER | HQ/10F/10F-2.jpg |  |  | HQ
VAV0508 | VAV | Included | 10.016 PLANNING DIR PLANNING ANALYST | entity:HQ_10.016_PLANNING_DIRPLANNING_ANALYST |  | PLANDIRPLANNING ANAL 10.016 | 10.016 PLANNING ANALYST | HQ/10F/10F-2.jpg |  |  | HQ
VAV0509 | VAV | Included | 10.017 PLANNING DIR STRAT PLANNER | entity:HQ_10.017_PLANNING_DIRSTRATPLANNER |  | PLANDIRSTRATPLNER 10.017 | 10.017 STRAT. PLANNER | HQ/10F/10F-2.jpg |  |  | HQ
VAV0510 | VAV | Not Included | 10.018 PLANNING DIR EXT COORD | entity:HQ_10.018_PLANNING_DIR_EXTCOORD |  | PLANNINGDIREXTCOORD 10.018 | 10.018 PLANNING DIR. EXT. COORD | HQ/10F/10F-2.jpg |  |  | HQ
VAV0511 | VAV | Included | 10.019 POLICY DIRSENPOLANALYST | entity:HQ_10.019_POLICY_DIRSENPOLANALYST |  | POLICY DIRSEN POLANA 10.019 | 10.019 SEN. POLICY ANALYST | HQ/10F/10F-2.jpg |  |  | HQ
VAV0512 | VAV | Included | 10.020 POLICY DIR SEN RESEARCH ANALYST | entity:HQ_10.02_POLICY_DIR_SENRESEARCH_ANALYST |  | POLICY DIRSEN RES ANA 10.020 | 10.020 RESEARCH ANALYST | HQ/10F/10F-2.jpg |  |  | HQ
VAV0513 | VAV | Included | 10.021 POLICY DIRRESANALYST | entity:HQ_10.021_POLICY_DIRRESANALYST |  | POLICY DIR RESEARCH ANA 10.021 | 10.021 RESEARCH ANALYST | HQ/10F/10F-2.jpg |  |  | HQ
VAV0514 | VAV | Included | 10.022 POLICY DIRRESANALYST | entity:HQ_10.022_POLICY_DIRRESANALYST |  | POLICY DIR RESEARCH ANA 10.022 | 10.022 RESEARCH ANALYST | HQ/10F/10F-2.jpg |  |  | HQ
VAV0515 | VAV | Included | 10.023 SHSERVDIR HR OFFICER | entity:HQ_10.023_SHSERVDIR_HR_OFFICER |  | SHSERVDIRHR OFFICER 10.023 | 10.023 HR OFFICER | HQ/10F/10F-2.jpg |  |  | HQ
VAV0516 | VAV | Included | 10.024 SHSERVDIR HR ASSISTANT | entity:HQ_10.024_SHSERVDIRHR_ASSISTANT |  | SHSERVDIRHR ASSISTANT 10.024 | 10.024 HR ASSISTANT | HQ/10F/10F-2.jpg |  |  | HQ
VAV0517 | VAV | Included | 10.025 SHSERVDIR PROCUR REPRESENT | entity:HQ_10.025_SHSERVDIRPROCURREPRESENT |  | SHSERVDIRPROC REPRE 10.025 | 10.025 PROCUR. REPRESENT | HQ/10F/10F-2.jpg |  |  | HQ
VAV0518 | VAV | Included | 10.026 SHSERVDIR SERVICE COORD | entity:HQ_10.026_SHSERVDIRSERVICE_COORD |  | SHSERVDIRSRVCE COORD 10.026 | 10.026 SERVICE COORD | HQ/10F/10F-2.jpg |  |  | HQ
VAV0519 | VAV | Included | 10.027 SHSERVDIRGENSERVSUPERV | entity:HQ_10.027_SHSERVDIRGENSERVSUPERV |  | SHSERVDIRGENSERVSUPERV 10.027 | 10.027 SERV. SUPERVISOR | HQ/10F/10F-2.jpg |  |  | HQ
VAV0520 | VAV | Not Included | 10.028 SHSERVDIR FINANCE CONTROL | entity:HQ_10.028_SHSERVDIRFINANCCONTROL |  | SHSERVDIRFINANCE CONTROL 10.028 | 10.028 FINANCE CONTROL | HQ/10F/10F-2.jpg |  |  | HQ
VAV0521 | VAV | Not Included | 10.029 SERV DIR TR AND GU SERV | entity:HQ_10.029_SHSERVDIRTR&_GUSERV |  | SHSERVDIRTR&GUSERV 10.029 | 10.029 SERV. DIR. TR. & GU. SERV. | HQ/10F/10F-2.jpg |  |  | HQ
VAV0522 | VAV | Not Included | 10.601 HH WING CORRIDOR | entity:HQ_10.601_HH-WING_CORRIDOR |  |  | HH-WING CORRIDOR 10.601 | HQ/10F/10F-1.jpg |  |  | HQ
VAV0523 | VAV | Not Included | 10.031 COMMUNICDIRCOMM DESIGR | entity:HQ_10.031_COMMUNICDIRCOMMDESIGNER |  | COMMUNICDIRCOMM DESIGR 10.031 | 10.031 COMM. DIR. DESIG. | HQ/10F/10F-2.jpg |  |  | HQ
VAV0524 | VAV | Not Included | 10.032 COMMUNICDIRSPEECH EDITOR | entity:HQ_10.032_COMMUNICDIRSPEECH_EDITOR |  | COMMUNICDIRSPEECH EDITR 10.032 | 10.032 COMM. DIR. EDITOR | HQ/10F/10F-2.jpg |  |  | HQ
VAV0525 | VAV | Not Included | 10.033 COMMUNICDIR TRANSLATOR | entity:HQ_10.033_COMMUNICDIR_TRANSLATOR |  | COMMUNICDIR TRANSLATOR 10.033 | 10.033 COMM. DIR. TRANSLTOR | HQ/10F/10F-1.jpg |  |  | HQ
VAV0526 | VAV | Not Included | 10.034 COMMUNICDIRPUBCOMMCOORD | entity:HQ_10.034_COMMUNICDIRPUBCOMMCOORD |  | COMMUNICDIRPUBCOMMCOORD 10.034 | 10.034 COMM. DIR. COORD | HQ/10F/10F-1.jpg |  |  | HQ
VAV0527 | VAV | Included | 10.035 SHSERVDIR IT SUPPORT OFFICER | entity:HQ_10.035_SHSERVDIR_IT_SUPPORT_OFFICER |  | SHSERVDIRIT SUPPOFCR 10.035 | 10.035 SUPP. OFFICER | HQ/10F/10F-1.jpg |  |  | HQ
VAV0528 | VAV | Not Included | 10.036 SH SERV DIR ACCOUNUT | entity:HQ_10.036_SHSERVDIR_ACCOUNT |  | SHSERVDIRACCOUNT 10.036 | 10.036 SH. SERV. DIR. ACCOUNT. | HQ/10F/10F-1.jpg |  |  | HQ
VAV0529 | VAV | Not Included | 10.037 SHSERVDIRSENACCOUNTANT | entity:HQ_10.037_SHSERVDIRSENACCOUNTANT |  | SHSERVDIRSENACCOUNT 10.037 | 10.037 SH. SERV. DIR. SR. ACCOUNT. | HQ/10F/10F-1.jpg |  |  | HQ
VAV0530 | VAV | Not Included | 10.001 SHEIKHA WING STORAGE | entity:HQ_10.001_SHEIKHA_WING_STORAGE |  |  | 10.001 SHEIKHA WING STORAGE | HQ/10F/10F-1.jpg |  |  | HQ
VAV0531 | VAV | Not Included | 10.001 SHEIKHA WING STORAGE | entity:HQ_10.001_SHEIKHA_WING_STORAGE |  |  | 10.001 SHEIKHA WING STORAGE | HQ/10F/10F-1.jpg |  |  | HQ
VAV0532 | VAV | Not Included | 10.001 SHEIKHA WING STORAGE | entity:HQ_10.001_SHEIKHA_WING_STORAGE |  |  | 10.001 SHEIKHA WING STORAGE | HQ/10F/10F-1.jpg |  |  | HQ
VAV0533 | VAV | Not Included | 10.003 BOARD ROOM WAITING AREA | entity:HQ_10.003_BOARD_ROOM_WAITING_AREA |  | BOARD RMWAITING AREA 10.003 | 10.003 BOARD ROOM WAITING | HQ/10F/10F-1.jpg |  |  | HQ
VAV0534 | VAV | Not Included | 10.003 BOARD ROOM WAITING AREA | entity:HQ_10.003_BOARD_ROOM_WAITING_AREA |  |  | 10.003 BOARD ROOM WAITING | HQ/10F/10F-1.jpg |  |  | HQ
VAV0535 | VAV | Included | 10.004 EXECDIRARCH COORD | entity:HQ_10.004_EXECDIRARCHCOORD |  | EXECDIRARCH COORD 10.004 | 10.004 ARCHIVE COORD | HQ/10F/10F-1.jpg |  |  | HQ
VAV0536 | VAV | Not Included | 10.106 LOUNGE | entity:HQ_10.106_LOUNGE |  |  | 10.106 LOUNGE | HQ/10F/10F-1.jpg |  |  | HQ
VAV0537 | VAV | Not Included | 10.106 LOUNGE | entity:HQ_10.106_LOUNGE |  |  | 10.106 NW LOUNGE | HQ/10F/10F-1.jpg |  |  | HQ
VAV0538 | VAV | Not Included | 10.109 BOARD PREP ROOM | entity:HQ_10.109_BOARD_PREPROOM |  | BOARD PREPROOM 10.109 | 10.109 BOARD PREP. ROOM | HQ/10F/10F-1.jpg |  |  | HQ
VAV0539 | VAV | Included | 10.101 CONSULTANT SPACE | entity:HQ_10.101_CONSULTANTS_SPACE |  |  | 10.101 CONSULTANT SPACE | HQ/10F/10F-2.jpg |  |  | HQ
VAV0540 | VAV | Included | 10.101 CONSULTANT SPACE | entity:HQ_10.101_CONSULTANTS_SPACE |  |  | 10.101 CONSULTANT SPACE | HQ/10F/10F-2.jpg |  |  | HQ
VAV0541 | VAV | Not Included | 10.112 TRANSLATOR ROOM | entity:HQ_10.112_TRANSLATOR_ROOM |  | TRANSLATER ROOM 10.112 | 10.112 AV ROOM | HQ/10F/10F-2.jpg |  |  | HQ
VAV0542 | VAV | Not Included | 10.601 HH WING CORRIDOR | entity:HQ_10.601_HH-WING_CORRIDOR |  | CORRIDOR 10.601 | NORTH EAST CORRIDOR | HQ/10F/10F-2.jpg |  |  | HQ
VAV0543 | VAV | Not Included | 10.601 HH WING CORRIDOR | entity:HQ_10.601_HH-WING_CORRIDOR |  | CORRIDOR 10.601 | HH-WING CORRIDOR 10.601 | HQ/10F/10F-1.jpg |  |  | HQ
VAV0544 | VAV | Not Included | 10.601 HH WING CORRIDOR | entity:HQ_10.601_HH-WING_CORRIDOR |  | CORRIDOR 10.601 | HH-WING CORRIDOR 10.601 | HQ/10F/10F-1.jpg |  |  | HQ
VAV0545 | VAV | Not Included | 10.601 HH WING CORRIDOR | entity:HQ_10.601_HH-WING_CORRIDOR |  | CORRIDOR 10.601 | NORTH EAST CORRIDOR | HQ/10F/10F-2.jpg |  |  | HQ
VAV0546 | VAV | Not Included | 10.601 HH WING CORRIDOR | entity:HQ_10.601_HH-WING_CORRIDOR |  | CORRIDOR 10.601 | HH-WING CORRIDOR 10.601 | HQ/10F/10F-1.jpg |  |  | HQ
VAV0547 | VAV | Not Included | 10.102 SHEIKHA WING MULTI PURPOSE ROOM | entity:HQ_10.102_SHEIKHA_WING_MULTIPURPOSE_ROOM |  | CORRIDO 10.102 | 10.002 SHEIKHA WING MULTI PURPOSE ROOM | HQ/10F/10F-1.jpg |  |  | HQ
VAV0548 | VAV | Included | 10.002E OFFICE SPACE | entity:HQ_10.002E_OFFICE_SPACE |  | SHELL SPACE E 10.002E | 10.002E OFFICE SPACE | HQ/10F/10F-1.jpg |  |  | HQ
VAV0549 | VAV | Included | 10.002D OFFICE SPACE | entity:HQ_10.002D_OFFICE_SPACE |  | SHELL SPACE C 10.002D | 10.002C OFFICE SPACE | HQ/10F/10F-1.jpg |  |  | HQ
VAV0550 | VAV | Included | 10.002C OFFICE SPACE | entity:HQ_10.002C_OFFICE_SPACE |  | SHELL SPACE B 10.002C | 10.002B OFFICE SPACE | HQ/10F/10F-1.jpg |  |  | HQ
VAV0551 | VAV | Included | 10.002A OFFICE SPACE | entity:HQ_10.002A_OFFICE_SPACE |  | SHELL SPACE A 10.002A | 10.002A OFFICE SPACE | HQ/10F/10F-1.jpg |  |  | HQ
VAV0552 | VAV | Not Included | 11.012 PLANNING DIR DIR PLANNING | entity:HQ_11.012_PLANNING_DIRDIRPLANNING |  | PLANNING DIR DIR PLANNING 11.012 | 11.012 PLANNING DIR. | HQ/11F/11F-1.jpg |  |  | HQ
VAV0553 | VAV | Not Included | 11.013 EXECDIRCORRF UP | entity:HQ_11.013_EXECDIRCORRF-UP |  | EXECDIRCORRF -UP 11.013 | 11.013 EXEC. DIR. CORR. | HQ/11F/11F-1.jpg |  |  | HQ
VAV0554 | VAV | Not Included | 11.014 EXEC DIR CORR MANAGER | entity:HQ_11.014_EXECDIRCORRMANAGER |  | EXECDIRCORRMANAGER 11.014 | 11.014 EXEC. DIR. CORR. MANAGER | HQ/11F/11F-1.jpg |  |  | HQ
VAV0555 | VAV | Not Included | 11.015 EXECDIRCORRF UP | entity:HQ_11.015_EXECDIRCORRF-UP |  | EXECDIRCORRF-UP 11.015 | 11.015 EXEC. DIR. CORR. | HQ/11F/11F-1.jpg |  |  | HQ
VAV0556 | VAV | Included | 11.016 EXECDIR LEGAL ASSIST | entity:HQ_11.016_EXECDIRLEGAL_ASSIST |  | EXECDIRLEGAL ASSIST 11.016 | 11.016 LEGAL ASSIST. | HQ/11F/11F-1.jpg |  |  | HQ
VAV0557 | VAV | Included | 11.017 EXECDIR LEGAL ADVISOR | entity:HQ_11.017_EXECDIRLEGAL_ADVISOR |  | EXECDIRLEGAL ADVISOR 11.017 | 11.017 LEGAL ADVISOR | HQ/11F/11F-1.jpg |  |  | HQ
VAV0558 | VAV | [9 empty] | HQ
VAV0559 | VAV | Included | 11.018 EXECDIREXECASSIST | entity:HQ_11.018_EXECDIREXECASSIST |  | EXECDIREXECASSIST 11.018 | 11.018 LEGAL ADVISOR | HQ/11F/11F-2.jpg |  |  | HQ
VAV0560 | VAV | Not Included | 11.019 EXECDIR DEP EXEC DIRECTOR | entity:HQ_11.019_EXECDIR_DEPEXECDIRECTOR |  | EXECDIRDEPEXECDIRECTOR 11.019 | 11.019 DEP. EXEC. DIRECTOR | HQ/11F/11F-2.jpg |  |  | HQ
VAV0561 | VAV | Not Included | 11.020 EXECDIREXECASSIST | entity:HQ_11.02_EXECDIREXECASSIST |  | EXECDIREXECASSIST 11.020 | 11.020 EXEC. ASSI. | HQ/11F/11F-2.jpg |  |  | HQ
VAV0562 | VAV | Not Included | 11.021 EXECDIR EXEC DIRECTOR | entity:HQ_11.021_EXECDIREXECDIRECTOR |  | EXECDIREXECDIRECTOR 11.021 | 11.021 EXEC. DIRECTOR | HQ/11F/11F-2.jpg |  |  | HQ
VAV0564 | VAV | Not Included | 11.022 SHEIKHA WING WAITING ROOM | entity:HQ_11.022_SHEIKHA_WING_WAITING_ROOM |  | SHEIKA WING WAITING ROOM 11.022 | 11.022 SHEIKHA WING WAITING ROOM | HQ/11F/11F-2.jpg |  |  | HQ
VAV0565 | VAV | Not Included | 11.022 SHEIKHA WING WAITING ROOM | entity:HQ_11.022_SHEIKHA_WING_WAITING_ROOM |  |  | 11.022 SHEIKHA WING WAITING ROOM | HQ/11F/11F-2.jpg |  |  | HQ
VAV0567 | VAV | Not Included | 11.023 SHEIKHA WING SECURITY ROOM | entity:HQ_11.023_SHEIKHA_WING_SECURITY_ROOM |  | SHEIKA WING SECURITY ROOM 11.023 | 11.023 SECURITY ROOM | HQ/11F/11F-2.jpg |  |  | HQ
VAV0568 | VAV | Not Included | 11.001 COMMUNICDIR COMMUNICATION DIRECTOR | entity:HQ_11.001_COMMUNICDIR_COMMUNICATION_DIRECTOR |  | COMMUNICATION DIRECTOR 11.001 | 11.001 COMMUNICATION DIR. | HQ/11F/11F-1.jpg |  |  | HQ
VAV0570 | VAV | Included | 11.002 COMMUNICDIR MED REL OFFICER | entity:HQ_11.002_COMMUNICDIRMEDRELOFFICER |  | COMMUDIRMEDRELOFFICER 11.002 | 11.002 MED. REL. OFFICER | HQ/11F/11F-1.jpg |  |  | HQ
VAV0571 | VAV | Not Included | 11.003 SHSERVDIR DIR SHARED SERVICES | entity:HQ_11.003_SHSERVDIR_DIRSHARED_SERVICES |  | SHSERV DIR SHARED SERV 11.003 | 11.003 DIR. SHARED SERVICES | HQ/11F/11F-1.jpg |  |  | HQ
VAV0573 | VAV | Included | 11.004 EXECDIRECTOR ADMASSIST | entity:HQ_11.004_EXECDIRECTOR_ADMASSIST |  | EXECDIRECTOR ADMASSIST 11.004 | 11.004 ADM. ASSI. | HQ/11F/11F-1.jpg |  |  | HQ
VAV0574 | VAV | Not Included | 11.005 PROTOCOL DIRPROTOCOL DIRECTOR | entity:HQ_11.005_PROTOCOL_DIRPROTOCOL_DIRECTOR |  | PROTOCOL DIRPROTCL DIR 11.005 | 11.005 PROTOCOL DIR. | HQ/11F/11F-1.jpg |  |  | HQ
VAV0575 | VAV | Not Included | 11.006 PROTOCOL DIRGIFTS DIRECTOR | entity:HQ_11.006_PROTOCOL_DIRGIFTS_DIRECTOR |  | PROTOCOL DIRGIFTS DIR 11.006 | 11.006 GIFT DIR. | HQ/11F/11F-1.jpg |  |  | HQ
VAV0576 | VAV | Included | 11.008 EXEC DIR CONSULTANT | entity:HQ_11.008_EXECDIRCONSULTANT |  | EXECDIRCONSULTANT 11.008 | 11.008 EXEC. DIR. CONSULTANT | HQ/11F/11F-1.jpg |  |  | HQ
VAV0577 | VAV | Included | 11.009 SECRETARY | entity:HQ_11.009_SECRETARY |  | SECRETARY 11.009 | 11.009 SEC. | HQ/11F/11F-1.jpg |  |  | HQ
VAV0578 | VAV | Not Included | 11.010 POLICY DIR OF POL AND RES | entity:HQ_11.01_POLICY_DIRDIROF_POL&_RES |  | POLICY DIROF POL & RES 11.010 | 11.010 DIR. OF POL. & RES. | HQ/11F/11F-1.jpg |  |  | HQ
VAV0579 | VAV | Included | 11.011 SECRETARY | entity:HQ_11.011_SECRETARY |  |  | 11.011 SECRETARY | HQ/11F/11F-1.jpg |  |  | HQ
VAV0580 | VAV | Not Included | 11.103 SHEIKHA WING BUSINESS LOUNGE | entity:HQ_11.103_SHEIKHA_WING_BUSINESS_LOUNGE |  | SHEIKA WING WAITING AREA NW | SHEIKHA WING BUSINESS LOUNGE | HQ/11F/11F-1.jpg |  |  | HQ
VAV0581 | VAV | Not Included | 11.103 SHEIKHA WING BUSINESS LOUNGE | entity:HQ_11.103_SHEIKHA_WING_BUSINESS_LOUNGE |  | SHEIKA WING WAITING AREA 11.103 | SHEIKHA WING BUSINESS LOUNGE | HQ/11F/11F-1.jpg |  |  | HQ
VAV0582 | VAV | Not Included | 11.201 SHEIKHA WING LOBBY | entity:HQ_11.201_SHEIKHA_WING_LOBBY |  | SHEIKA WING LOBBY 11.201 | 11.201 SHEIKHA WING LOBBY | HQ/11F/11F-2.jpg |  |  | HQ
VAV0583 | VAV | Not Included | 11.201 SHEIKHA WING LOBBY | entity:HQ_11.201_SHEIKHA_WING_LOBBY |  |  | 11.201 SHEIKHA WING LOBBY | HQ/11F/11F-2.jpg |  |  | HQ
VAV0584 | VAV | Not Included | 11.208 SHEIKHA WING SHEIKHA ENSUIT | entity:HQ_11.202_SHEIKHA_WING_SHEIKHA_ENSUIT |  | SHEIKHA WING SHEIKHA EN 11.208 | 11.208 SHEIKHA WING SHEIKHA ENSUIT | HQ/11F/11F-2.jpg |  |  | HQ
VAV0585 | VAV | Not Included | 11.208 SHEIKHA WING SHEIKHA ENSUIT | entity:HQ_11.202_SHEIKHA_WING_SHEIKHA_ENSUIT |  |  | 11.208 SHEIKHA WING SHEIKHA ENSUIT | HQ/11F/11F-2.jpg |  |  | HQ
VAV0586 | VAV | Not Included | 11.208 SHEIKHA WING SHEIKHA ENSUIT | entity:HQ_11.202_SHEIKHA_WING_SHEIKHA_ENSUIT |  |  | 11.208 SHEIKHA WING SHEIKHA ENSUIT | HQ/11F/11F-2.jpg |  |  | HQ
VAV0587 | VAV | Not Included | 11.208 SHEIKHA WING SHEIKHA ENSUIT | entity:HQ_11.202_SHEIKHA_WING_SHEIKHA_ENSUIT |  |  | 11.208 SHEIKHA WING SHEIKHA ENSUIT | HQ/11F/11F-2.jpg |  |  | HQ
VAV0588 | VAV | Not Included | 11.203 SHEIKHA WING RELAX AREA | entity:HQ_11.203_SHEIKHA_WING_RELAX_AREA |  |  | 11.203 SHEIKHA WING RELAX AREA | HQ/11F/11F-2.jpg |  |  | HQ
VAV0589 | VAV | Not Included | 11.203 SHEIKHA WING RELAX AREA | entity:HQ_11.203_SHEIKHA_WING_RELAX_AREA |  |  | 11.203 SHEIKHA WING RELAX AREA | HQ/11F/11F-2.jpg |  |  | HQ
VAV0590 | VAV | Not Included | 11.204 SHEIKHA WING MEETING ROOM | entity:HQ_11.204_SHEIKHA_WING_MEETING_ROOM |  |  | 11.204 SHEIKHA WING MEETING ROOM | HQ/11F/11F-2.jpg |  |  | HQ
VAV0591 | VAV | Not Included | 11.204 SHEIKHA WING MEETING ROOM | entity:HQ_11.204_SHEIKHA_WING_MEETING_ROOM |  |  | 11.204 SHEIKHA WING MEETING ROOM | HQ/11F/11F-2.jpg |  |  | HQ
VAV0592 | VAV | Not Included | 8.400 VISITORS CENTER | entity:HQ_8.400_VISITORS_CENTER |  | LEVEL / VISITOR CENTER 09 | VISITORS CENTER | HQ/8F/8F.jpg |  |  | HQ
VAV0593 | VAV | Not Included | 8.400 VISITORS CENTER | entity:HQ_8.400_VISITORS_CENTER |  |  | VISITORS CENTER | HQ/8F/8F.jpg |  |  | HQ
VAV0594 | VAV | Not Included | 8.400 VISITORS CENTER | entity:HQ_8.400_VISITORS_CENTER |  |  | VISITORS CENTER | HQ/8F/8F.jpg |  |  | HQ
VAV0595 | VAV | Included | B1.116 SHEIKHA LOBBY | entity:HQ_B1.109_ROOM |  | FEMALE BREAK ROOM B.109 | B.116 LOBBY | HQ/Basment Floor/BF-2.jpg |  |  | HQ
VAV0596 | VAV | Included | 4.015B OFFICE SPACE | entity:HQ_4.015B_OFFICE_SPACE |  | SHELL SPACE B 04.015B | 4.015B OFFICE SPACE | HQ/4F/4F-2.jpg |  |  | HQ
VAV0597 | VAV | Included | 4.001A OFFICE SPACE | entity:HQ_4.001A_OFFICE_SPACE |  | SHELL SPACE A 04.001A | 4.001A OFFICE SPACE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0598 | VAV | Included | 4.001E OFFICE SPACE | entity:HQ_4.001E_OFFICE_SPACE |  | SHELL SPACE E 04.001E | 4.001E OFFICE SPACE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0599 | VAV | Included | 4.001C OFFICE SPACE | entity:HQ_4.001C_OFFICE_SPACE |  | SHELL SPACE C 04.001C | 4.001C OFFICE SPACE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0600 | VAV | Included | 4.001H OFFICE SPACE | entity:HQ_4.001H_OFFICE_SPACE |  | SHELL SPACE H 04.001H | 4.001H OFFICE SPACE | HQ/4F/4F-1.jpg |  |  | HQ
VAV0601 | VAV | Included | 10.002B OFFICE SPACE | entity:HQ_10.002B_OFFICE_SPACE |  | SHELL SPACE D 10.002B | 10.002D OFFICE SPACE | HQ/10F/10F-1.jpg |  |  | HQ
VAV0602 | VAV | Included | 11.007 EXEC DIR CONSULTANT | entity:HQ_11.007_EXECDIRCONSULTANT |  | EXECDIRCONSULTANT 11.007 | 11.007 EXEC. DIR. CONSULTANT | HQ/11F/11F-1.jpg |  |  | HQ
VAV0603 | VAV | Not Included | 11.601 SHEIKA WING CORRIDOR NE | entity:HQ_11.601_SHEIKHA_WING_CORRIDOR |  | SHEIKA WING CORRIDOR NE | SHEIKHA WING CORRIDOR 11.601 | HQ/11F/11F-2.jpg |  |  | HQ
VAV0604 | VAV | Not Included | 11.601 SHEIKA WING CORRIDOR NE | entity:HQ_11.601_SHEIKHA_WING_CORRIDOR |  | CORRIDOR SW | SOUTH WEST CORRIDOR | HQ/11F/11F-1.jpg |  |  | HQ
VAV0605 | VAV | Not Included | 11.102 HH WING BUSINESS LOUNGE | entity:HQ_11.102_HH_WING_BUSINESS_LOUNGE |  |  | HH WING BUSINESS LOUNGE | HQ/11F/11F-1.jpg |  |  | HQ
VAV0606 | VAV | Not Included | 11.102 HH WING BUSINESS LOUNGE | entity:HQ_11.102_HH_WING_BUSINESS_LOUNGE |  |  | HH WING BUSINESS LOUNGE | HQ/11F/11F-1.jpg |  |  | HQ
VAV0607 | VAV | Included | G.013 PR AND MARKET STAFF | entity:HQ_G.013_PR_&_MARKET_STAFF |  |  | G.013 PR & MARKET STAFF | HQ/Ground Floor/GF-1.jpg |  |  | HQ
VAV0608 | VAV | Not Included | G.405 TOILET | entity:HQ_G.405_TOILET | [6 empty] | HQ
AHUB001 | AHU | Not Included | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 | [6 empty] | QNL
AHUB002 | AHU | Not Included | B.063 PLANT ROOM 01 | entity:QNL_B_063_PLANT_ROOM_01 | [6 empty] | QNL
AHUB003 | AHU | Not Included | B.070 PLANT ROOM 02 | entity:QNL_B_070_PLANT_ROOM_02 |  |  | Plant Rm 2 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
AHUB004 | AHU | Not Included | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 | [6 empty] | QNL
AHUB005 | AHU | Not Included | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 |  |  | Plant Rm 4 | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
AHUB006 | AHU | Not Included | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 |  |  | Plant Rm 4 | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
AHUB007 | AHU | Not Included | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 |  |  | Plant Rm 4 | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
AHUB008 | AHU | Not Included | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 |  |  | Plant Rm 4 | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
AHUB009 | AHU | Not Included | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 | [6 empty] | QNL
AHUB010 | AHU | Not Included | B.070 PLANT ROOM 02 | entity:QNL_B_070_PLANT_ROOM_02 |  |  | Plant Rm 2 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
AHUB011 | AHU | Not Included | B.063 PLANT ROOM 01 | entity:QNL_B_063_PLANT_ROOM_01 |  |  | Plant Rm 1 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
AHUB012 | AHU | Not Included | B.063 PLANT ROOM 01 | entity:QNL_B_063_PLANT_ROOM_01 |  |  | Plant Rm 1 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
AHUB013 | AHU | Not Included | B.070 PLANT ROOM 02 | entity:QNL_B_070_PLANT_ROOM_02 | [6 empty] | QNL
AHUB014 | AHU | Not Included | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 | [6 empty] | QNL
AHUB015 | AHU | Not Included | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 | [6 empty] | QNL
FCU_1F_001 | FCU | Not Included | T1.323 IDF ROOM | entity:QNL_T1_323_IDF_ROOM | [6 empty] | QNL
FCU_1F_002 | FCU | Included | L1.030 ICT ROOM 02 | entity:QNL_L1_030_ICT_ROOM_02 | [6 empty] | QNL
FCU_1F_003 | FCU | Not Included | L1.099 IDF ROOM 02 | entity:QNL_L1_099_IDF_ROOM_02 |  |  | IDF Rm | QNL/FF-2.jpg | SAME - screen and column D name the same room |  | QNL
FCU_1F_004 | FCU | Included | BR6 BRIDGE CEILING VOID | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_005 | FCU | Included | BR6 BRIDGE CEILING VOID | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_006 | FCU | Included | BR6 BRIDGE CEILING VOID | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_007 | FCU | Included | BR6 BRIDGE CEILING VOID | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_008 | FCU | Included | BR6 BRIDGE CEILING VOID | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_009 | FCU | Included | BR5 BRIDGE CEILING VOID | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_010 | FCU | Included | BR5 BRIDGE CEILING VOID | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_011 | FCU | Included | BR5 BRIDGE CEILING VOID | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_012 | FCU | Included | BR5 BRIDGE CEILING VOID | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_013 | FCU | Included | BR6 BRIDGE CEILING VOID | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_014 | FCU | Included | BR4 BRIDGE CEILING VOID | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_015 | FCU | Included | BR6 BRIDGE CEILING VOID | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_016 | FCU | Included | BC1 BRIDGE CEILING | entity:QNL_L1_BC1_BRIDGE_CEILING | [6 empty] | QNL
FCU_1F_017 | FCU | Included | BR4 BRIDGE CEILING VOID | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_018 | FCU | Included | BR4 BRIDGE CEILING VOID | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_019 | FCU | Included | BR5 BRIDGE CEILING VOID | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_020 | FCU | Included | BR3 BRIDGE CEILING VOID | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_021 | FCU | Included | BR5 BRIDGE CEILING VOID | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_022 | FCU | Included | BR3 BRIDGE CEILING VOID | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_023 | FCU | Included | BR3 BRIDGE CEILING VOID | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_024 | FCU | Included | BR3 BRIDGE CEILING VOID | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_025 | FCU | Included | BR2 BRIDGE CEILING VOID | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_026 | FCU | Included | BR4 BRIDGE CEILING VOID | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_027 | FCU | Included | BR2 BRIDGE CEILING VOID | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_028 | FCU | Included | BR4 BRIDGE CEILING VOID | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_029 | FCU | Included | BR2 BRIDGE CEILING VOID | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_030 | FCU | Included | BR2 BRIDGE CEILING VOID | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_031 | FCU | Included | BR1 BRIDGE CEILING VOID | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_032 | FCU | Included | BR1 BRIDGE CEILING VOID | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_033 | FCU | Included | BR1 BRIDGE CEILING VOID | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_034 | FCU | Included | BR1 BRIDGE CEILING VOID | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_035 | FCU | Included | BR2 BRIDGE CEILING VOID | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_036 | FCU | Included | BR2 BRIDGE CEILING VOID | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_037 | FCU | Included | BR3 BRIDGE CEILING VOID | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_038 | FCU | Included | BR3 BRIDGE CEILING VOID | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_039 | FCU | Included | BR4 BRIDGE CEILING VOID | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_040 | FCU | Included | BR4 BRIDGE CEILING VOID | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_041 | FCU | Included | BC2 BRIDGE CEILING | entity:QNL_L1_BC2_BRIDGE_CEILING | [6 empty] | QNL
FCU_1F_042 | FCU | Included | BR5 BRIDGE CEILING VOID | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_043 | FCU | Included | BR6 BRIDGE CEILING VOID | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_044 | FCU | Included | BR6 BRIDGE CEILING VOID | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_045 | FCU | Included | BR6 BRIDGE CEILING VOID | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_046 | FCU | Included | BR6 BRIDGE CEILING VOID | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_047 | FCU | Included | BR1 BRIDGE CEILING VOID | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_048 | FCU | Included | BR1 BRIDGE CEILING VOID | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_049 | FCU | Included | BR2 BRIDGE CEILING VOID | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_050 | FCU | Included | BR2 BRIDGE CEILING VOID | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_051 | FCU | Included | BR4 BRIDGE CEILING VOID | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_052 | FCU | Included | BR4 BRIDGE CEILING VOID | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_053 | FCU | Included | BR5 BRIDGE CEILING VOID | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_054 | FCU | Included | BR5 BRIDGE CEILING VOID | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID | [6 empty] | QNL
FCU_1F_055 | FCU | Included | L1.990 VESTIBULE | entity:QNL_L1_990_VESTIBULE | [6 empty] | QNL
FCU_1F_056 | FCU | Included | L1.991 EXTERNAL BOOK DROP | entity:QNL_L1_991_EXTERNAL_BOOK_DROP | [6 empty] | QNL
FCU_1F_057 | FCU | Included | L1.144 ILL DIRECTOR | entity:QNL_L1_144_ILL_DIRECTOR | [6 empty] | QNL
FCU_1F_058 | FCU | Included | L1.145 ILL DIRECTOR | entity:QNL_L1_144_ILL_DIRECTOR | [6 empty] | QNL
FCU_1F_059 | FCU | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT | [6 empty] | QNL
FCU_1F_060 | FCU | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT |  |  | Restaurant / Front Kitchen (open plan) | QNL/FF-2.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - by the Front Kitchen label | QNL
FCU_1F_061 | FCU | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT |  |  | Restaurant / Front Kitchen (open plan) | QNL/FF-2.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
FCU_1F_062 | FCU | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT | [6 empty] | QNL
FCU_1F_063 | FCU | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT | [6 empty] | QNL
FCU_1F_064 | FCU | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT |  |  | Restaurant / Front Kitchen (open plan) | QNL/FF-2.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
FCU_1F_065 | FCU | Not Included | BI BRIDGE IDF | entity:QNL_L1_BI_BRIDGE_IDF | [6 empty] | QNL
FCU_2F_001 | FCU | Not Included | T1.275 IDF ROOM | entity:QNL_T1_275_IDF_ROOM | [6 empty] | QNL
FCU_2F_002 | FCU | Not Included | T1.276 IDF ROOM | entity:QNL_T1_276_IDF_ROOM | [6 empty] | QNL
FCU_2F_003 | FCU | Not Included | T1.171 IDF ROOM | entity:QNL_T1_171_IDF_ROOM | [6 empty] | QNL
FCU_2F_004 | FCU | Not Included | T1.1714 IDF ROOM | entity:QNL_T1_1714_IDF_ROOM | [6 empty] | QNL
FCU_2F_005 | FCU | Not Included | L2.009 KDF ROOM | entity:QNL_L2_009_KDF_ROOM | [6 empty] | QNL
FCU_2F_034 | FCU | Included | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID |  |  | Auditorium | QNL/SF-6.jpg | SAME - screen and column D name the same room |  | QNL
FCU_2F_035 | FCU | Included | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID |  |  | Auditorium | QNL/SF-6.jpg | SAME - screen and column D name the same room |  | QNL
FCU_2F_036 | FCU | Included | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID |  |  | Auditorium | QNL/SF-6.jpg | SAME - screen and column D name the same room |  | QNL
FCU_2F_037 | FCU | Included | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID | [6 empty] | QNL
FCU_2F_038 | FCU | Included | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID | [6 empty] | QNL
FCU_2F_039 | FCU | Included | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID | [6 empty] | QNL
FCU_2F_040 | FCU | Included | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID | [6 empty] | QNL
FCU_2F_041 | FCU | Included | L2.088 BRIDGE RAISED FLOOR | entity:QNL_L2_088_BRIDGE_RAISED_FLOOR | [6 empty] | QNL
FCU_2F_042 | FCU | Included | L2.088 BRIDGE RAISED FLOOR | entity:QNL_L2_088_BRIDGE_RAISED_FLOOR | [6 empty] | QNL
FCU_2F_043 | FCU | Included | L2.088 BRIDGE RAISED FLOOR | entity:QNL_L2_088_BRIDGE_RAISED_FLOOR | [6 empty] | QNL
FCU_2F_044 | FCU | Included | L2.088 BRIDGE RAISED FLOOR | entity:QNL_L2_088_BRIDGE_RAISED_FLOOR | [6 empty] | QNL
FCU_2F_045 | FCU | Included | L2.081 GROUP STUDY ROOM | entity:QNL_L2_081_GROUP_STUDY_ROOM |  |  | Group Study Rm | QNL/SF-6.jpg | SAME - screen and column D name the same room | west side of the study block | QNL
FCU_2F_046 | FCU | Included | L2.076 GROUP STUDY ROOM | entity:QNL_L2_076_GROUP_STUDY_ROOM |  |  | Group Study Rm | QNL/SF-6.jpg | SAME - screen and column D name the same room | west side of the study block | QNL
FCU_2F_047 | FCU | Included | L2.076 GROUP STUDY ROOM | entity:QNL_L2_076_GROUP_STUDY_ROOM |  |  | Group Study Rm | QNL/SF-6.jpg | SAME - screen and column D name the same room | west side of the study block | QNL
FCU_2F_048 | FCU | Included | L2.070 INDIVISTUDY ROOM | entity:QNL_L2_070_INDIVISTUDY_ROOM | [6 empty] | QNL
FCU_2F_049 | FCU | Included | L2.070 INDIVISTUDY ROOM | entity:QNL_L2_070_INDIVISTUDY_ROOM |  |  | Indv. Study Rm | QNL/SF-6.jpg | SAME - screen and column D name the same room | east side of the study block | QNL
FCU_2F_050 | FCU | Included | L2.070 INDIVISTUDY ROOM | entity:QNL_L2_070_INDIVISTUDY_ROOM |  |  | Indv. Study Rm | QNL/SF-6.jpg | SAME - screen and column D name the same room | east side of the study block | QNL
FCU_2F_051 | FCU | Included | L2.073 INDIVISTUDY ROOM | entity:QNL_L2_073_INDIVISTUDY_ROOM |  |  | Indv. Study Rm | QNL/SF-6.jpg | SAME - screen and column D name the same room | east side of the study block | QNL
FCU_2F_052 | FCU | Included | L2.073 INDIVISTUDY ROOM | entity:QNL_L2_073_INDIVISTUDY_ROOM |  |  | Indv. Study Rm | QNL/SF-6.jpg | SAME - screen and column D name the same room | east side of the study block | QNL
FCU_2F_053 | FCU | Included | L2.073 INDIVISTUDY ROOM | entity:QNL_L2_073_INDIVISTUDY_ROOM | [6 empty] | QNL
FCU_2F_054 | FCU | Included | L2.088 LOUNGE AREA | entity:QNL_L2_088_BRIDGE_RAISED_FLOOR |  |  | Lounge area | QNL/SF-6.jpg | CHECK - read, but with a caveat; see the reason | the dot sits beside the Lounge area label on the open plate; column D says Bridge Raised Floor L2.088 | QNL
FCU_2F_055 | FCU | Included | L2.088 LOUNGE AREA | entity:QNL_L2_088_BRIDGE_RAISED_FLOOR |  |  | Lounge area | QNL/SF-6.jpg | CHECK - read, but with a caveat; see the reason | the dot sits beside the Lounge area label on the open plate; column D says Bridge Raised Floor L2.088 | QNL
FCU_2F_056 | FCU | Included | T1.021 OPEN STUDY TERRACE | entity:QNL_T1_021_OPEN_STUDY_TERRACE | [6 empty] | QNL
FCU_2F_057 | FCU | Included | T1.021 OPEN STUDY TERRACE | entity:QNL_T1_021_OPEN_STUDY_TERRACE | [6 empty] | QNL
FCU_2F_058 | FCU | Included | T1.021 OPEN STUDY TERRACE | entity:QNL_T1_021_OPEN_STUDY_TERRACE | [6 empty] | QNL
FCU_2F_059 | FCU | Included | T1.021 OPEN STUDY TERRACE | entity:QNL_T1_021_OPEN_STUDY_TERRACE | [6 empty] | QNL
FCU_2F_060 | FCU | Included | T1.020 OPEN LOUNGE TERRACE | entity:QNL_T1_020_OPEN_LOUNGE_TERRACE | [6 empty] | QNL
FCU_2F_061 | FCU | Included | T1.020 OPEN LOUNGE TERRACE | entity:QNL_T1_020_OPEN_LOUNGE_TERRACE | [6 empty] | QNL
FCU_2F_062 | FCU | Included | T1.020 OPEN LOUNGE TERRACE | entity:QNL_T1_020_OPEN_LOUNGE_TERRACE | [6 empty] | QNL
FCU_B_001 | FCU | Not Included | B.155 FACULTY CARRELS | entity:QNL_B_155_FACULTY_CARRELS |  |  | IDF Rm | QNL/BF-8.jpg | SAME - screen and column D name the same room | the dot is in the first of the small cells along the north-west wall; the IDF Rm label sits over the second | QNL
FCU_B_002 | FCU | Included | B.085 FUMIGATION ROOM | entity:QNL_B_085_FUMIGATION_ROOM | [6 empty] | QNL
FCU_B_003 | FCU | Not Included | B.062 IDF CORRIDOR | entity:QNL_B_062_IDF_CORRIDOR |  |  | IDF | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_004 | FCU | Not Included | B.215 IDF FM STORAGE | entity:QNL_B_215_IDF_FM_STORAGE |  |  | FM Storage | QNL/BF-10.jpg | SAME - screen and column D name the same room | the dot is at the west wall in the band that carries the FM Storage and Storage labels | QNL
FCU_B_005 | FCU | Not Included | B.140 HL PLANT ROOM | entity:QNL_B_140_HL_PLANT_ROOM | [6 empty] | QNL
FCU_B_006 | FCU | Not Included | B.071 FIRE COMMAND ROOM | entity:QNL_B_071_FIRE_COMMAND_ROOM | [6 empty] | QNL
FCU_B_007 | FCU | Not Included | B.072 SPRIMKLERS PUMPS AND ZONES VALVES | entity:QNL_B_072_SPRIMKLERS_PUMPS_&_ZONES_VALVES | [6 empty] | QNL
FCU_B_008 | FCU | Not Included | B.087 GAS SUPPRESSION ROOM | entity:QNL_B_087_GAS_SUPPRESSION_ROOM |  |  | Cell between Gas Suppression and Server Rm | QNL/BF-3.jpg | DIFF - the screen puts this unit somewhere column D does not | the dot is in the middle cell, one wall east of the cell the Gas Suppression label points into; column D says GAS SUPPRESSION ROOM B.087 | QNL
FCU_B_009 | FCU | Included | B.088 PEOPLE MOVER PLANT | entity:QNL_B_088_PEOPLE_MOVER_PLANT | [6 empty] | QNL
FCU_B_010 | FCU | Not Included | B.105 SECURITY CONTOL ROOM | entity:QNL_B_105_SECURITY_CONTOL_ROOM | [6 empty] | QNL
FCU_B_011 | FCU | Not Included | B.063 PLANT ROOM 01 | entity:QNL_B_063_PLANT_ROOM_01 |  |  | Plant Rm 1 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_012 | FCU | Not Included | B.063 PLANT ROOM 01 | entity:QNL_B_063_PLANT_ROOM_01 |  |  | Plant Rm 1 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_013 | FCU | Not Included | B.070 PLANT ROOM 02 | entity:QNL_B_070_PLANT_ROOM_02 |  |  | Plant Rm 2 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_014 | FCU | Not Included | B.070 PLANT ROOM 02 | entity:QNL_B_070_PLANT_ROOM_02 |  |  | Plant Rm 2 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_015 | FCU | Not Included | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 |  |  | Plant Rm 3 / Corridor 5 (open plan) | QNL/BF-6.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - Plant Rm 3 end | QNL
FCU_B_016 | FCU | Not Included | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 |  |  | Plant Rm 3 / Corridor 5 (open plan) | QNL/BF-6.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - Plant Rm 3 end | QNL
FCU_B_017 | FCU | Not Included | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 |  |  | Plant Rm 3 / Corridor 5 (open plan) | QNL/BF-6.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - Plant Rm 3 end | QNL
FCU_B_018 | FCU | Not Included | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 |  |  | Plant Rm 4 | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_019 | FCU | Not Included | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 |  |  | Plant Rm 4 | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_020 | FCU | Not Included | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 |  |  | Plant Rm 4 | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_021 | FCU | Not Included | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 |  |  | Plant Rm 4 | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_022 | FCU | Included | B.210 FM STORAGE | entity:QNL_B_210_FM_STORAGE |  |  | FM Storage | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_023 | FCU | Included | B.210 FM STORAGE | entity:QNL_B_210_FM_STORAGE |  |  | FM Storage | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_024 | FCU | Not Included | B.211 PH PLANT ROOM | entity:QNL_B_211_PH_PLANT_ROOM |  |  | PH Plant | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_025 | FCU | Not Included | B.212 MISTING PUMP ROOM | entity:QNL_B_212_MISTING_PUMP_ROOM | [6 empty] | QNL
FCU_B_026 | FCU | Not Included | B.212 MISTING PUMP ROOM | entity:QNL_B_212_MISTING_PUMP_ROOM |  |  | Misting System | QNL/BF-10.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_027 | FCU | Included | B.121 SORTING SHELVING ROOM | entity:QNL_B_121_SORTING_SHELVING_ROOM | [6 empty] | QNL
FCU_B_028 | FCU | Included | B.121 SORTING SHELVING ROOM | entity:QNL_B_121_SORTING_SHELVING_ROOM |  |  | Sorting Shelving Rm | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_029 | FCU | Included | B.145 LOBY AND CSECURITY | entity:QNL_B_145_LOBY_&_CSECURITY | [6 empty] | QNL
FCU_B_030 | FCU | Included | B.226 PUMP RM 4 | entity:QNL_B_226_PUMP_ROOM |  |  | Pump Rm 4 | QNL/BF-10.jpg | DIFF - the screen puts this unit somewhere column D does not | the dot is inside the Pump Rm 4 box; column D says WATER FEATURE ROOM B.226 | QNL
FCU_B_031 | FCU | Not Included | B.215A IDF | entity:QNL_B_215A_IDF | [6 empty] | QNL
FCU_B_032 | FCU | Included | B.132 SHELL SPACE SPECIAL COLLECTION | entity:QNL_B_132_SHELL_SPACE-SPECIAL_COLLECTION |  |  | Shell Space-Special Collection | QNL/BF-3.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_033 | FCU | Included | B.132 SHELL SPACE SPECIAL COLLECTION | entity:QNL_B_132_SHELL_SPACE-SPECIAL_COLLECTION |  |  | Shell Space-Special Collection | QNL/BF-3.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_034 | FCU | Included | B.132 SHELL SPACE SPECIAL COLLECTION | entity:QNL_B_132_SHELL_SPACE-SPECIAL_COLLECTION |  |  | Shell Space-Special Collection | QNL/BF-3.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_035 | FCU | Included | B.132 SHELL SPACE SPECIAL COLLECTION | entity:QNL_B_132_SHELL_SPACE-SPECIAL_COLLECTION |  |  | Shell Space-Special Collection | QNL/BF-3.jpg | SAME - screen and column D name the same room |  | QNL
FCU_B_036 | FCU | Included | B.122 IT OFFICE | entity:QNL_B_122_IT_OFFICE | [6 empty] | QNL
FCU_B_037 | FCU | Not Included | B.215A IDF | entity:QNL_B_215A_IDF | [6 empty] | QNL
FCU_B_038 | FCU | Not Included | B.145 LOBY AND CSECURITY | entity:QNL_B_145_LOBY_&_CSECURITY | [6 empty] | QNL
VAV0001 | VAV | [9 empty] | QNL
VAV_1F_S11_001 | VAV | Included | L1.026 GROUP STUDY ROOM1 | entity:QNL_L1_026_GROUP_STUDY_ROOM1 | [6 empty] | QNL
VAV_1F_S11_002 | VAV | Included | L1.027 GROUP STUDY ROOM2 | entity:QNL_L1_027_GROUP_STUDY_ROOM2 |  |  | Study Rm2 | QNL/FF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_1F_S11_003 | VAV | Included | L1.028 GROUP STUDY ROOM3 | entity:QNL_L1_028_GROUP_STUDY_ROOM3 |  |  | Cell between Study Rm2 and Study Rm 4 | QNL/FF.jpg | SAME - screen and column D name the same room | the cell carries no label; Study Rm3 labels the large room to the east | QNL
VAV_1F_S11_004 | VAV | Included | L1.020 INFO LITERACY INSTR1 | entity:QNL_L1_020_INFO_LITERACY_INSTR1 | [6 empty] | QNL
VAV_1F_S11_005 | VAV | Included | L1.020 INFO LITERACY INSTR1 | entity:QNL_L1_020_INFO_LITERACY_INSTR1 |  |  | Info. Literacy Instr.1 | QNL/FF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_1F_S11_006 | VAV | Included | L1.021 INFOR LTERACY INSTR 2 | entity:QNL_L1_021_INFO_LITERACY_INSTR2 | [6 empty] | QNL
VAV_1F_S11_007 | VAV | Included | L1.021 INFOR LTERACY INSTR 2 | entity:QNL_L1_021_INFO_LITERACY_INSTR2 | [6 empty] | QNL
VAV_1F_S11_008 | VAV | Included | L1.021 INFOR LTERACY INSTR 2 | entity:QNL_L1_021_INFO_LITERACY_INSTR2 | [6 empty] | QNL
VAV_1F_S11_009 | VAV | Included | L1.021 INFOR LTERACY INSTR 2 | entity:QNL_L1_021_INFO_LITERACY_INSTR2 | [6 empty] | QNL
VAV_1F_S11_010 | VAV | Included | L1.021 INFOR LTERACY INSTR 2 | entity:QNL_L1_021_INFO_LITERACY_INSTR2 |  |  | Info. Literacy Instr.2 / Writing Head (open plan) | QNL/FF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
VAV_1F_S11_011 | VAV | Included | L1.021 INFOR LTERACY INSTR 2 | entity:QNL_L1_021_INFO_LITERACY_INSTR2 | [6 empty] | QNL
VAV_1F_S11_012 | VAV | Included | L1.021 INFOR LTERACY INSTR 2 | entity:QNL_L1_021_INFO_LITERACY_INSTR2 | [6 empty] | QNL
VAV_1F_S11_013 | VAV | Included | L1.021 INFOR LTERACY INSTR 2 | entity:QNL_L1_021_INFO_LITERACY_INSTR2 | [6 empty] | QNL
VAV_1F_S11_014 | VAV | Included | L1.022 COMPUTER CLASS RM | entity:QNL_L1_022_COMPUTER_CLASSROOM | [6 empty] | QNL
VAV_1F_S11_015 | VAV | Included | L1.022 COMPUTER CLASS RM | entity:QNL_L1_022_COMPUTER_CLASSROOM |  |  | Computer Class Rm | QNL/FF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_1F_S11_016 | VAV | Included | L1.022 COMPUTER CLASS RM | entity:QNL_L1_022_COMPUTER_CLASSROOM |  |  | Computer Class Rm | QNL/FF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_1F_S11_017 | VAV | Included | L1.022 COMPUTER CLASS RM | entity:QNL_L1_022_COMPUTER_CLASSROOM | [6 empty] | QNL
VAV_1F_S11_018 | VAV | Included | L1.022 COMPUTER CLASS RM | entity:QNL_L1_022_COMPUTER_CLASSROOM | [6 empty] | QNL
VAV_1F_S11_019 | VAV | Included | L1.022 COMPUTER CLASS RM | entity:QNL_L1_022_COMPUTER_CLASSROOM |  |  | Info. Literacy Instr.2 / Writing Head (open plan) | QNL/FF.jpg | DIFF - the screen puts this unit somewhere column D does not | the dot is in the Info. Literacy Instr.2 / Writing Head cell, two walls west of the Computer Class Rm where column D puts it | QNL
VAV_1F_S11_020 | VAV | Included | L1.022 COMPUTER CLASS RM | entity:QNL_L1_022_COMPUTER_CLASSROOM |  |  | Computer Class Rm | QNL/FF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_1F_S11_021 | VAV | Included | L1.022 COMPUTER CLASS RM | entity:QNL_L1_022_COMPUTER_CLASSROOM | [6 empty] | QNL
VAV_1F_S11_022 | VAV | Included | L1.029 GROUP STUDY ROOM 4 | entity:QNL_L1_029_GROUP_STUDY_ROOM4 |  |  | Study Rm 4 | QNL/FF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_1F_S11_087 | VAV | Included | L1.023 CORRIDOR | entity:QNL_L1023_2_CORRIDOR |  |  | Yellow band at the north-west corner | QNL/FF-3.jpg | CHECK - read, but with a caveat; see the reason | the band carries no label; column D says CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 | QNL
VAV_1F_S11_088 | VAV | Included | L1.023 CORRIDOR | entity:QNL_L1023_2_CORRIDOR |  |  | Study Rm3 | QNL/FF.jpg | DIFF - the screen puts this unit somewhere column D does not | the dot is inside the Study Rm3 room; column D says CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 | QNL
VAV_1F_S11_089 | VAV | Included | L1.023 CORRIDOR | entity:QNL_L1023_2_CORRIDOR | [6 empty] | QNL
VAV_1F_S11_090 | VAV | Included | L1.023 CORRIDOR | entity:QNL_L1023_2_CORRIDOR | [6 empty] | QNL
VAV_1F_S15_001 | VAV | Included | L1.063 MEDIA STUDIO 1 | entity:QNL_L1_063_MEDIA_STUDIO_1 | [6 empty] | QNL
VAV_1F_S15_002 | VAV | Included | L1.063 MEDIA STUDIO 1 | entity:QNL_L1_063_MEDIA_STUDIO_1 | [6 empty] | QNL
VAV_1F_S15_003 | VAV | Included | L1.065 MEDIA STUDIO 1 | entity:QNL_L1_065_MEDIA_STUDIO_1 |  |  | Media Studio1 / Storage / Media Studio2 (open plan) | QNL/FF-3.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - under the Storage label | QNL
VAV_1F_S15_004 | VAV | Included | L1.065 MEDIA STUDIO 1 | entity:QNL_L1_065_MEDIA_STUDIO_1 |  |  | Media Studio1 / Storage / Media Studio2 (open plan) | QNL/FF-3.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - under the Storage label | QNL
VAV_1F_S15_005 | VAV | Not Included | L1.040 HEAD LIBRARIAN OFFICE | entity:QNL_L1_040_HEAD_LIBRARIAN_OFFICE | [6 empty] | QNL
VAV_1F_S15_006 | VAV | Included | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING |  |  | Children Library | QNL/FF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_1F_S15_007 | VAV | Included | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING |  |  | Children Library | QNL/FF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_1F_S15_008 | VAV | Included | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING |  |  | Children Library | QNL/FF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_1F_S15_009 | VAV | Included | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING |  |  | Unlabelled purple strip west of the Restaurant | QNL/FF-2.jpg | CHECK - read, but with a caveat; see the reason | the strip carries no label; column D says CHILDRENS LIBRARY-PRE SCHOOL COLLECTION L1.047, which is on the Zone 1 screen | QNL
VAV_1F_S15_010 | VAV | Included | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING |  |  | Unlabelled purple strip west of the Restaurant | QNL/FF-2.jpg | CHECK - read, but with a caveat; see the reason | the strip carries no label; column D says CHILDRENS LIBRARY-PRE SCHOOL COLLECTION L1.047, which is on the Zone 1 screen | QNL
VAV_1F_S15_011 | VAV | Included | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING | [6 empty] | QNL
VAV_1F_S15_012 | VAV | Included | L1.048 STAFF OFFICE | entity:QNL_L1_048_STAFF_OFFICE |  |  | Yellow cell south of Staff Office | QNL/FF.jpg | SAME - screen and column D name the same room | the cell carries no label of its own; the Staff Office cell is the one above it | QNL
VAV_1F_S15_021 | VAV | Included | L1.104 PRAYER ROOM FEMALE | entity:QNL_L1_104_PRAYER_ROOM_FEMALE | [6 empty] | QNL
VAV_1F_S15_022 | VAV | Included | L1.104 PRAYER ROOM FEMALE | entity:QNL_L1_104_PRAYER_ROOM_FEMALE |  |  | Prayer Rm (Female) | QNL/FF-3.jpg | SAME - screen and column D name the same room | the upper half of the purple block, which is where the Prayer Rm (Female) pointer lands | QNL
VAV_1F_S15_023 | VAV | Included | L1.104 PRAYER ROOM FEMALE | entity:QNL_L1_104_PRAYER_ROOM_FEMALE | [6 empty] | QNL
VAV_1F_S15_024 | VAV | Included | L1.104 PRAYER ROOM FEMALE | entity:QNL_L1_104_PRAYER_ROOM_FEMALE | [6 empty] | QNL
VAV_1F_S15_025 | VAV | Included | L1.106 ABLUTION WOMEN | entity:QNL_L1_106_ABLUTIONWOMEN | [6 empty] | QNL
VAV_1F_S15_038 | VAV | Included | L1.105 ABLUTION MEN | entity:QNL_L1_105_ABLUTIONMEN | [6 empty] | QNL
VAV_1F_S15_039 | VAV | Included | L1.002A GREEM ROOM | entity:QNL_L1_002A_GREEM_ROOM | [6 empty] | QNL
VAV_1F_S15_039S | VAV | Included | L1.048 STAFF OFFICE | entity:QNL_L1_048_STAFF_OFFICE |  |  | Head Librarian Office | QNL/FF.jpg | DIFF - the screen puts this unit somewhere column D does not | the dot is in the Head Librarian Office cell, one wall north of the Staff Office cell where column D puts it | QNL
VAV_1F_S15_040 | VAV | Included | L1.002A GREEM ROOM | entity:QNL_L1_002A_GREEM_ROOM | [6 empty] | QNL
VAV_1F_S15_096 | VAV | Included | L1.041 MULTIPURPOSE ROOM | entity:QNL_L1_041_MULTPURPOSE_ROOM |  |  | Multipurpose Rm | QNL/FF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_1F_S15_097 | VAV | Included | L1.041 MULTIPURPOSE ROOM | entity:QNL_L1_041_MULTPURPOSE_ROOM |  |  | Multipurpose Rm | QNL/FF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_1F_S15_098 | VAV | Included | L1.041 MULTIPURPOSE ROOM | entity:QNL_L1_041_MULTPURPOSE_ROOM |  |  | Multipurpose Rm | QNL/FF-2.jpg | SAME - screen and column D name the same room |  | QNL
VAV_2F_S10_001 | VAV | Included | L2.992 GULF MATERIAL | entity:QNL_L2_992_GULF_MATERIAL |  |  | Libr.Com.Rel. Spo. & Event Spc / Ad.Admin &Planning (yellow zone) | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | column D says GULF MATERIAL L2 | QNL
VAV_2F_S10_002 | VAV | Included | L2.992 GULF MATERIAL | entity:QNL_L2_992_GULF_MATERIAL |  |  | Libr.Com.Rel. Spo. & Event Spc / Ad.Admin &Planning (yellow zone) | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | column D says GULF MATERIAL L2 | QNL
VAV_2F_S10_003 | VAV | Included | L2.992 GULF MATERIAL | entity:QNL_L2_992_GULF_MATERIAL |  |  | Libr.Com.Rel. Spo. & Event Spc / Ad.Admin &Planning (yellow zone) | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | column D says GULF MATERIAL L2 | QNL
VAV_2F_S10_004 | VAV | Included | L2.992 GULF MATERIAL | entity:QNL_L2_992_GULF_MATERIAL |  |  | Libr.Com.Rel. Spo. & Event Spc / Ad.Admin &Planning (yellow zone) | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | south half of the yellow zone, which carries no label of its own; column D says GULF MATERIAL L2 | QNL
VAV_2F_S10_005 | VAV | Included | L2.992 GULF MATERIAL | entity:QNL_L2_992_GULF_MATERIAL |  |  | Libr.Com.Rel. Spo. & Event Spc / Ad.Admin &Planning (yellow zone) | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | south half of the yellow zone, which carries no label of its own; column D says GULF MATERIAL L2 | QNL
VAV_2F_S10_006 | VAV | Included | L2.992 GULF MATERIAL | entity:QNL_L2_992_GULF_MATERIAL | [6 empty] | QNL
VAV_2F_S12_001 | VAV | Included | L1.001 OPEN READING AREA | entity:QNL_L1_001_OPEN_READING_AREA | [6 empty] | QNL
VAV_2F_S12_002 | VAV | Included | L1.001 OPEN READING AREA | entity:QNL_L1_001_OPEN_READING_AREA | [6 empty] | QNL
VAV_2F_S12_003 | VAV | Included | L1.001 OPEN READING AREA | entity:QNL_L1_001_OPEN_READING_AREA |  |  | Unlabelled open area, west half of Zone 1 | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the west half of this Zone 1 plan carries no room label at all; column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S12_004 | VAV | Included | L1.001 OPEN READING AREA | entity:QNL_L1_001_OPEN_READING_AREA | [6 empty] | QNL
VAV_2F_S12_005 | VAV | Included | L1.001 OPEN READING AREA | entity:QNL_L1_001_OPEN_READING_AREA | [6 empty] | QNL
VAV_2F_S12_006 | VAV | Included | L1.001 OPEN READING AREA | entity:QNL_L1_001_OPEN_READING_AREA |  |  | Unlabelled open area, west half of Zone 1 | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the west half of this Zone 1 plan carries no room label at all; column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S12_007 | VAV | Included | L1.001 OPEN READING AREA | entity:QNL_L1_001_OPEN_READING_AREA |  |  | Unlabelled open area, west half of Zone 1 | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the west half of this Zone 1 plan carries no room label at all; column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S12_008 | VAV | Included | L1.001 OPEN READING AREA | entity:QNL_L1_001_OPEN_READING_AREA |  |  | Unlabelled open area, west half of Zone 1 | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the west half of this Zone 1 plan carries no room label at all; column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S12_009 | VAV | Included | L1.001 OPEN READING AREA | entity:QNL_L1_001_OPEN_READING_AREA |  |  | Unlabelled open area, west half of Zone 1 | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the west half of this Zone 1 plan carries no room label at all; column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S12_010 | VAV | Included | L1.002 BRAILLE READER | entity:QNL_L1_002_BRAILLE_READER |  |  | Unlabelled open area, west half of Zone 1 | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the west half of this Zone 1 plan carries no room label at all; column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S12_011 | VAV | Included | L1.002 BRAILLE READER | entity:QNL_L1_002_BRAILLE_READER |  |  | Unlabelled open area, west half of Zone 1 | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the west half of this Zone 1 plan carries no room label at all; column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S12_012 | VAV | Included | L1.003 TUTORING HEAD | entity:QNL_L1_003_TUTORING_HEAD |  |  | Unlabelled open area, west half of Zone 1 | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the west half of this Zone 1 plan carries no room label at all; column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S12_013 | VAV | Included | L1.004 WRITING ROOM 1 | entity:QNL_L1_004_WRITING_ROOM1 |  |  | Unlabelled open area, west half of Zone 1 | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the west half of this Zone 1 plan carries no room label at all; column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S12_014 | VAV | Included | L1.005 WRITING ROOM 2 | entity:QNL_L1_005_WRITING_ROOM2 |  |  | Unlabelled open area, west half of Zone 1 | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the west half of this Zone 1 plan carries no room label at all; column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S12_015 | VAV | Included | L1.005 WRITING ROOM 2 | entity:QNL_L1_005_WRITING_ROOM2 | [6 empty] | QNL
VAV_2F_S12_016 | VAV | Included | L1.007 STUDENT CARRELS | entity:QNL_L1_007_STUDENT_CARRLES |  |  | Unlabelled open area, west half of Zone 1 | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the west half of this Zone 1 plan carries no room label at all; column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S12_017 | VAV | Included | L1.007 STUDENT CARRELS | entity:QNL_L1_007_STUDENT_CARRLES | [6 empty] | QNL
VAV_2F_S12_018 | VAV | Included | L1.007 STUDENT CARRELS | entity:QNL_L1_007_STUDENT_CARRLES | [6 empty] | QNL
VAV_2F_S12_019 | VAV | Included | L1.007 STUDENT CARRELS | entity:QNL_L1_007_STUDENT_CARRLES | [6 empty] | QNL
VAV_2F_S12_020 | VAV | Included | L1.007 STUDENT CARRELS | entity:QNL_L1_007_STUDENT_CARRLES | [6 empty] | QNL
VAV_2F_S12_021 | VAV | Included | L2.010 BREAKOUT SPACE | entity:QNL_L2_010_BREAKOUT_SPACE |  |  | Circulation Office / Breakout space (open plan) | QNL/SF-1.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
VAV_2F_S12_022 | VAV | Included | L2.011 CIRCULATION OFFICE | entity:QNL_L2_011_CTRCULATION_OFFICE |  |  | Circulation Office / Breakout space (open plan) | QNL/SF-1.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
VAV_2F_S12_023 | VAV | Included | L2.012 OFFICE SPEC COL | entity:QNL_L2_012_OFFICE_SPEC_COL | [6 empty] | QNL
VAV_2F_S12_024 | VAV | Included | L2.013 OFFICE SPEC COL | entity:QNL_L2_013_OFFICE_SPEC_COL | [6 empty] | QNL
VAV_2F_S12_025 | VAV | Included | L2.993 CORRIDOR | entity:QNL_L2_993_CORRIDOR | [6 empty] | QNL
VAV_2F_S12_026 | VAV | Included | L2.011 CIRCULATION OFFICE | entity:QNL_L2_015_40_GROUP_STUDY_ROOM_5 |  |  | Circulation Office / Breakout space (open plan) | QNL/SF-1.jpg | DIFF - the screen puts this unit somewhere column D does not | the dot is in the open Circulation Office / Breakout space band; Group Study Room 5, which column D names, is a cell south of it | QNL
VAV_2F_S12_027 | VAV | Included | L2.017 40 GROUP STUDY ROOM 7 | entity:QNL_L2_017_40_GROUP_STUDY_ROOM_7 | [6 empty] | QNL
VAV_2F_S12_028 | VAV | Included | L2.018 GROUP STUDY ROOM 8 | entity:QNL_L2_018_GROUP_STUDY_ROOM_8 | [6 empty] | QNL
VAV_2F_S12_029 | VAV | Included | L2.017 40 GROUP STUDY ROOM 7 | entity:QNL_L2_016_40_GROUP_STUDY_ROOM_6 |  |  | Group Study Rm 7 | QNL/SF-1.jpg | DIFF - the screen puts this unit somewhere column D does not | the dot is inside the Group Study Rm 7 cell; column D says Group Study Room 6 L2.016, the cell one wall west | QNL
VAV_2F_S12_097 | VAV | Included | L2.018 GROUP STUDY ROOM 8 | entity:QNL_L2_018_GROUP_STUDY_ROOM_8 | [6 empty] | QNL
VAV_2F_S13_001 | VAV | Not Included | L2.044 LIB DIRECTOR S ROOM | entity:QNL_L2_044_LIBDIRECTORS_ROOM |  |  | Lib. Director's Rm | QNL/SF-3.jpg | SAME - screen and column D name the same room |  | QNL
VAV_2F_S13_002 | VAV | Not Included | L2.044 LIB DIRECTOR S ROOM | entity:QNL_L2_044_LIBDIRECTORS_ROOM | [6 empty] | QNL
VAV_2F_S13_003 | VAV | Included | L2.043 SERVICE AND LOUNGE | entity:QNL_L2_043_SERVICE_&_LOUNGE |  |  | Service & Lounge | QNL/SF-3.jpg | SAME - screen and column D name the same room |  | QNL
VAV_2F_S13_004 | VAV | Included | L2.014 TRANS SPC AND SPACE ED | entity:QNL_L2_025_OPEN_OFFICE |  |  | Academic Pers. Libraria | QNL/SF-1.jpg | DIFF - the screen puts this unit somewhere column D does not | the dot is inside the Academic Pers. Libraria cell; column D says OPEN OFFICE L2.025, which is the cell at the west end of the same zone | QNL
VAV_2F_S13_005 | VAV | Included | L2.021 LIBR COM REL SPC AND EVENTS SPC | entity:QNL_L2_022_ACADEMIC_PERS_LIBRARIA |  |  | Transl.Spc& Space ED (strip along the south of the cyan zone) | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the strip runs the width of the cyan zone below the cells; column D says ACADEMIC PERS. LIBRARIA L2.022, which is one of those cells | QNL
VAV_2F_S13_006 | VAV | Included | L2.022 ACADEMIC PERS LIBRARIA | entity:QNL_L2_022_ACADEMIC_PERS_LIBRARIA |  |  | Transl.Spc& Space ED (strip along the south of the cyan zone) | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the strip runs the width of the cyan zone below the cells; column D says ACD PERS LIBRARIAN L2.022, which is one of those cells | QNL
VAV_2F_S13_007 | VAV | Included | L2.023 AD ADMIN AND PLANNING | entity:QNL_L2_023_AD_ADMIN_&_PLANNING |  |  | Cell east of Academic Pers. Libraria | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | the cell carries no label; column D says AD ADMIN & PLANNING L2.023, which is in the yellow zone to the south | QNL
VAV_2F_S13_008 | VAV | Included | L2.024 OFFICE COORD | entity:QNL_L2_024_OFFICE_COORD |  |  | Office Coord | QNL/SF-3.jpg | SAME - screen and column D name the same room |  | QNL
VAV_2F_S13_009 | VAV | Included | L2.025 OPEN OFFICE | entity:QNL_L2_025_OPEN_OFFICE | [6 empty] | QNL
VAV_2F_S13_010 | VAV | Included | L2.993 CORRIDOR | entity:QNL_L2_993_CORRIDOR | [6 empty] | QNL
VAV_2F_S13_011 | VAV | Included | L2.993 CORRIDOR | entity:QNL_L2_993_CORRIDOR | [6 empty] | QNL
VAV_2F_S13_012 | VAV | Included | L2.993 CORRIDOR | entity:QNL_L2_993_CORRIDOR |  |  | Transl.Spc& Space ED (strip along the south of the cyan zone) | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | column D says CORRIDOR L2; the strip may be that corridor, it is not labelled as one | QNL
VAV_2F_S13_013 | VAV | Included | L2.993 CORRIDOR | entity:QNL_L2_993_CORRIDOR |  |  | Transl.Spc& Space ED (strip along the south of the cyan zone) | QNL/SF-1.jpg | CHECK - read, but with a caveat; see the reason | column D says CORRIDOR L2; the strip may be that corridor, it is not labelled as one | QNL
VAV_2F_S13_014 | VAV | Included | L2.993 CORRIDOR | entity:QNL_L2_993_CORRIDOR | [6 empty] | QNL
VAV_2F_S13_015 | VAV | Included | L2.993 CORRIDOR | entity:QNL_L2_993_CORRIDOR | [6 empty] | QNL
VAV_2F_S13_016 | VAV | Not Included | L2.048 VIP WATING | entity:QNL_L2_048_VIP_WATING | [6 empty] | QNL
VAV_2F_S14_001 | VAV | Included | L1.080 PUBLIC SERVICES | entity:QNL_L1_080_PUBLIC_SERVICE | [6 empty] | QNL
VAV_2F_S14_002 | VAV | Included | L1.080 PUBLIC SERVICES | entity:QNL_L1_080_PUBLIC_SERVICE | [6 empty] | QNL
VAV_2F_S14_003 | VAV | Included | L1.080 PUBLIC SERVICES | entity:QNL_L1_080_PUBLIC_SERVICE | [6 empty] | QNL
VAV_2F_S14_004 | VAV | Included | L1.080 PUBLIC SERVICES | entity:QNL_L1_080_PUBLIC_SERVICE | [6 empty] | QNL
VAV_2F_S14_005 | VAV | Included | L1.081 BIBLIOGRAPHER 1 | entity:QNL_L1_081_BIBLIOGRANHER1 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_006 | VAV | Included | L1.082 BIBLIOGRAPHER 2 | entity:QNL_L1_082_BIBLIOGRAPHER2 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_007 | VAV | Included | L1.083 SPEC COLL AND ARCH | entity:QNL_L1_083_SPEC_COLL&ARCH |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_008 | VAV | Included | L1.084 R AND L SERVICES | entity:QNL_L1_084_R&L_SERVICES |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_009 | VAV | Included | L1.085 AD PUBLIC SERVICE | entity:QNL_L1_085_ADPUBLIC_SERVICE |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_010 | VAV | Included | L1.086 REF LIBRARIAN 1 | entity:QNL_L1_086_REF_LIBRARIAN_1 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_011 | VAV | Included | L1.087 REF LIBRARIAN 2 | entity:QNL_L1_087_REF_LIBRARIAN_2 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_012 | VAV | Included | L1.088 REF LIBRARIAN 3 | entity:QNL_L1_088_REF_LIBRARIAN_3 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_013 | VAV | Included | L1.089 REF LIBRARIAN 4 | entity:QNL_L1_089_REF_LIBRARIAN_4 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_014 | VAV | Included | L1.090 REF LIBRARIAN 5 | entity:QNL_L1_090_REF_LIBRARIAN_5 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_015 | VAV | Included | L1.091 REF LIBRARIAN 6 | entity:QNL_L1_091_REF_LIBRARIAN_6 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_016 | VAV | Included | L1.092 REF LIBRARIAN 7 | entity:QNL_L1_092_REF_LIBRARIAN_7 | [6 empty] | QNL
VAV_2F_S14_017 | VAV | Included | L1.093 REF LIBRARIAN 8 | entity:QNL_L1_093_REF_LIBRARIAN_8 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_018 | VAV | Included | L1.094 REF LIBRARIAN 9 | entity:QNL_L1_094_REF_LIBRARIAN_9 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_019 | VAV | Included | L1.095 REF LIBRARIAN 10 | entity:QNL_L1_095_REF_LIBRARIAN_10 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_020 | VAV | Included | L1.096 REF LIBRARIAN 11 | entity:QNL_L1_096_REF_LIBRARIAN_11 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S14_021 | VAV | Included | L1.097 REF LIBRARIAN 12 | entity:QNL_L1_097_REF_LIBRARIAN_12 |  |  | VIP Waiting / VIP Meeting (open cyan zone) | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | column D gives this unit a first-floor room number (L1.xxx) although the tag and the screen are both second floor | QNL
VAV_2F_S15_001 | VAV | Not Included | L2.051 VIP ROOM | entity:QNL_L2_051_VIP_ROOM | [6 empty] | QNL
VAV_2F_S15_002 | VAV | Not Included | L2.051 VIP ROOM | entity:QNL_L2_051_VIP_ROOM |  |  | VIP Rm | QNL/SF-3.jpg | SAME - screen and column D name the same room |  | QNL
VAV_2F_S15_003 | VAV | Not Included | L2.051 VIP ROOM | entity:QNL_L2_051_VIP_ROOM | [6 empty] | QNL
VAV_2F_S15_004 | VAV | Not Included | L2.051 VIP ROOM | entity:QNL_L2_051_VIP_ROOM | [6 empty] | QNL
VAV_2F_S15_005 | VAV | Not Included | L2.046 VIP MEETING | entity:QNL_L2_046_VIP_MEETING |  |  | VIP Rm | QNL/SF-3.jpg | CHECK - read, but with a caveat; see the reason | the dot is in the pink VIP Rm; column D says MAJLIS-VIP Meeting L2.046, and VIP Meeting is printed in the cyan zone to the east | QNL
VAV_B_S10_001 | VAV | Included | B.200 DIGITIZATION | entity:QNL_B_200_DIGITIZATION | [6 empty] | QNL
VAV_B_S10_002 | VAV | Included | B.200 DIGITIZATION | entity:QNL_B_200_DIGITIZATION | [6 empty] | QNL
VAV_B_S10_003 | VAV | Included | B.200 DIGITIZATION | entity:QNL_B_200_DIGITIZATION | [6 empty] | QNL
VAV_B_S10_004 | VAV | Included | B.200 DIGITIZATION | entity:QNL_B_200_DIGITIZATION | [6 empty] | QNL
VAV_B_S10_005 | VAV | Included | B.200 DIGITIZATION | entity:QNL_B_200_DIGITIZATION | [6 empty] | QNL
VAV_B_S10_006 | VAV | Included | B.200 DIGITIZATION | entity:QNL_B_200_DIGITIZATION | [6 empty] | QNL
VAV_B_S10_007 | VAV | Included | B.200 DIGITIZATION | entity:QNL_B_200_DIGITIZATION | [6 empty] | QNL
VAV_B_S10_008 | VAV | Included | B.200 DIGITIZATION | entity:QNL_B_200_DIGITIZATION | [6 empty] | QNL
VAV_B_S10_009 | VAV | Included | B.203 TECHNICAL SERVICES | entity:QNL_B_204_TECHNICAL_SERVICES | [6 empty] | QNL
VAV_B_S10_010 | VAV | Included | B.204 TECHNICAL SERVICES | entity:QNL_B_204_TECHNICAL_SERVICES |  |  | Technical Services | QNL/BF-5.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S10_011 | VAV | Included | B.204 TECHNICAL SERVICES | entity:QNL_B_204_TECHNICAL_SERVICES |  |  | Technical Services | QNL/BF-5.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S10_012 | VAV | Included | B.209 CONSERVATION WORK AREA | entity:QNL_B_209_CONSERVATION_WORK_AREA | [6 empty] | QNL
VAV_B_S10_013 | VAV | Included | B.209 CONSERVATION WORK AREA | entity:QNL_B_209_CONSERVATION_WORK_AREA | [6 empty] | QNL
VAV_B_S10_014 | VAV | Included | B.209 CONSERVATION WORK AREA | entity:QNL_B_209_CONSERVATION_WORK_AREA | [6 empty] | QNL
VAV_B_S10_015 | VAV | Included | B.206 INSTRUCTION OUTREACH | entity:QNL_B_206_INSTRUCTION_OUTREACH | [6 empty] | QNL
VAV_B_S10_016 | VAV | Included | B.205 INSTRUCTION PRESENTATION | entity:QNL_B_205_INSTRUCTION_PRESENTATION |  |  | Instruction Presentation | QNL/BF-5.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S10_017 | VAV | Included | B.205 INSTRUCTION PRESENTATION | entity:QNL_B_205_INSTRUCTION_PRESENTATION |  |  | Instruction Presentation | QNL/BF-5.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S10_018 | VAV | Included | B.205 INSTRUCTION PRESENTATION | entity:QNL_B_205_INSTRUCTION_PRESENTATION | [6 empty] | QNL
VAV_B_S10_019 | VAV | Included | B.208 PROF LIBRARIAN | entity:QNL_B_208_PROF_LIBRARIAN | [6 empty] | QNL
VAV_B_S10_020 | VAV | Included | B.207 RESERCHERS READING AREA | entity:QNL_B_207_PRESEARCHERS_READING_AREA |  |  | Researchers Reading Area | QNL/BF-7.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S10_021 | VAV | Included | B.207 RESERCHERS READING AREA | entity:QNL_B_207_PRESEARCHERS_READING_AREA |  |  | Researchers Reading Area | QNL/BF-7.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S10_022 | VAV | Included | B.207 RESERCHERS READING AREA | entity:QNL_B_207_PRESEARCHERS_READING_AREA |  |  | Researchers Reading Area | QNL/BF-7.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S10_023 | VAV | Included | B.207 RESERCHERS READING AREA | entity:QNL_B_207_PRESEARCHERS_READING_AREA |  |  | Researchers Reading Area | QNL/BF-7.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S10_024 | VAV | Included | B.200 DIGITIZATION | entity:QNL_B_200_DIGITIZATION |  |  | Digitization / Instruction Outreach (open plan) | QNL/BF-5.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
VAV_B_S11_001 | VAV | Included | B.001A BREAK OUT AREA | entity:QNL_B_001A_BREAK_OUT_AREA |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - west end | QNL
VAV_B_S11_002 | VAV | Included | B.001A BREAK OUT AREA | entity:QNL_B_001A_BREAK_OUT_AREA |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - west end | QNL
VAV_B_S11_003 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - west end | QNL
VAV_B_S11_004 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
VAV_B_S11_005 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - east end | QNL
VAV_B_S11_006 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - east end | QNL
VAV_B_S11_007 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - east end | QNL
VAV_B_S11_008 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Tech.Services & Collection (open plan) | QNL/BF-1.jpg | OPEN - one space, two or more labels; the screen cannot split them |  | QNL
VAV_B_S11_009 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Tech.Services & Collection (open plan) | QNL/BF-1.jpg | OPEN - one space, two or more labels; the screen cannot split them |  | QNL
VAV_B_S11_010 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Tech.Services & Collection (open plan) | QNL/BF-1.jpg | OPEN - one space, two or more labels; the screen cannot split them |  | QNL
VAV_B_S11_011 | VAV | Included | B.001A BREAK OUT AREA | entity:QNL_B_001A_BREAK_OUT_AREA |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - west end | QNL
VAV_B_S11_012 | VAV | Included | B.001A BREAK OUT AREA | entity:QNL_B_001A_BREAK_OUT_AREA |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - west end | QNL
VAV_B_S11_013 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - west end | QNL
VAV_B_S11_014 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - west end | QNL
VAV_B_S11_015 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - east end | QNL
VAV_B_S11_016 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - east end | QNL
VAV_B_S11_017 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - east end | QNL
VAV_B_S11_018 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Tech.Services & Collection (open plan) | QNL/BF-1.jpg | OPEN - one space, two or more labels; the screen cannot split them |  | QNL
VAV_B_S11_019 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Tech.Services & Collection (open plan) | QNL/BF-1.jpg | OPEN - one space, two or more labels; the screen cannot split them |  | QNL
VAV_B_S11_020 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  |  | Tech.Services & Collection (open plan) | QNL/BF-1.jpg | OPEN - one space, two or more labels; the screen cannot split them |  | QNL
VAV_B_S11_021 | VAV | Included | B.001 TECH SERVICES AND COLLECTIONS OFFICE | entity:QNL_B_009_RECEPTION_&_LOUNGE |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | DIFF - the screen puts this unit somewhere column D does not | open plan - east end, inside the purple zone | QNL
VAV_B_S11_022 | VAV | Included | B.009 RECEPTION AND LOUNGE | entity:QNL_B_009_RECEPTION_&_LOUNGE |  |  | Corridor east of Receving Area | QNL/BF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S11_023 | VAV | Included | B.009 RECEPTION AND LOUNGE | entity:QNL_B_009_RECEPTION_&_LOUNGE |  |  | Unlabelled strip between Plant Rm 1 and Plant Rm 2 | QNL/BF-2.jpg | CHECK - read, but with a caveat; see the reason | the strip carries no label on this screen, so it cannot be matched against column D either way | QNL
VAV_B_S11_024 | VAV | Included | B.002 KITCHEN | entity:QNL_B_002_KITCHEN |  |  | Kitchen | QNL/BF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S11_025 | VAV | Included | B.028 STORAGE | entity:QNL_B_028_STORAGE |  |  | Storage | QNL/BF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S11_026 | VAV | Not Included | B.003 FINANCE COORDINATOR AND BUSINESS SUPPORT OFCR | entity:QNL_B_003_FINANCE_COORDINATOR_&_BUSINESS_SUPPORT_OFCR |  |  | Finance Cooridinator & Business Support officer | QNL/BF.jpg | DIFF - the screen puts this unit somewhere column D does not |  | QNL
VAV_B_S11_027 | VAV | Not Included | B.003 FINANCE COORDINATOR AND BUSINESS SUPPORT OFCR | entity:QNL_B_003_FINANCE_COORDINATOR_&_BUSINESS_SUPPORT_OFCR | [6 empty] | QNL
VAV_B_S11_028 | VAV | Included | B.004 ANALOGUE RESOURCES | entity:QNL_B_004_ANALOG_RESOURCES |  |  | Analog Resource | QNL/BF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S11_029 | VAV | Included | B.005 DIGITAL RESOURCES | entity:QNL_B_005_DIGITAL_RESOURCES | [6 empty] | QNL
VAV_B_S11_030 | VAV | Included | B.006 BUDGET AND PAYMENT 1 | entity:QNL_B_006_BUDGET_&_PAYMENT_1 |  |  | Budget & Payment | QNL/BF.jpg | SAME - screen and column D name the same room | lower band, west of the partition | QNL
VAV_B_S11_031 | VAV | Included | B.007 BUDGET AND PAYMENT 2 | entity:QNL_B_007_BUDGET_&_PAYMENT_2 |  |  | Budget & Payment | QNL/BF.jpg | SAME - screen and column D name the same room | lower band, west of the partition | QNL
VAV_B_S11_032 | VAV | Included | B.024 AD COLLECTION | entity:QNL_B_024_AD_COLLECTIONS |  |  | Ad Collection | QNL/BF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S11_033 | VAV | Included | B.024 AD COLLECTION | entity:QNL_B_024_AD_COLLECTIONS |  |  | Ad Collection | QNL/BF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S11_034 | VAV | Included | B.020 ENGINEERING | entity:QNL_B_020_ENGINEERING | [6 empty] | QNL
VAV_B_S11_035 | VAV | Included | B.021 ARABIC SUDIES | entity:QNL_B_021_ARABIC_STUDIES | [6 empty] | QNL
VAV_B_S11_036 | VAV | Included | B.022 LICENSING EXPERT | entity:QNL_B_022_LICENSING_EXPERT | [6 empty] | QNL
VAV_B_S11_037 | VAV | Included | B.023 ART AND HUMANITIES | entity:QNL_B_023_ARTS_&_HUMANITIES |  |  | Corridor 4 | QNL/BF-1.jpg | DIFF - the screen puts this unit somewhere column D does not | dot is in the Corridor 4 strip west of the MV Rm wall, the strip the Corridor 4 label points into; column D says Art & Humanities B.023 | QNL
VAV_B_S11_038 | VAV | Included | B.027 PROCUREMENT SPC PROCUREMENT OFCR | entity:QNL_B_027_PROCUREMENT_SPC_PROCUREMENT_OFCR |  |  | Procurement SPC | QNL/BF.jpg | DIFF - the screen puts this unit somewhere column D does not |  | QNL
VAV_B_S11_039 | VAV | Included | B.026 BUSINESS AND COMPUTING | entity:QNL_B_026_BUSINESS_&_COMPUTING | [6 empty] | QNL
VAV_B_S11_040 | VAV | Included | B.025 SOCIAL SCIENCES | entity:QNL_B_025_SOCIAL_SCIENCES | [6 empty] | QNL
VAV_B_S11_041 | VAV | Included | B.029 LITERATURE AND ANGUAGE | entity:QNL_B_029_LITERATURE_&_ANGUAGE | [6 empty] | QNL
VAV_B_S11_042 | VAV | Included | B.030 SNR P COORDINATOR AND P COORDINATOR | entity:QNL_B_030_SNR_P_COORDINATOR_&_P_COORDINATOR | [6 empty] | QNL
VAV_B_S11_043 | VAV | Included | B.008 RECEIVING AREA | entity:QNL_B_008_RECEIVING_AREA |  |  | Corridor east of Receving Area | QNL/BF.jpg | DIFF - the screen puts this unit somewhere column D does not | east of the Receving Area wall, in the corridor strip with S11-046 and S11-022; column D says Receiving Area B.008 | QNL
VAV_B_S11_044 | VAV | Included | B.008 RECEIVING AREA | entity:QNL_B_008_RECEIVING_AREA |  |  | Budget & Payment (lower band) | QNL/BF.jpg | CHECK - read, but with a caveat; see the reason | the dot is in the lower band with S11-030 and S11-031; the partition between the cells is only partial, so which cell is not certain. Column D says Receiving Area B.008 | QNL
VAV_B_S11_045 | VAV | Included | B.008 RECEIVING AREA | entity:QNL_B_008_RECEIVING_AREA |  |  | Receving Area | QNL/BF.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S11_046 | VAV | Included | B.008 RECEIVING AREA | entity:QNL_B_008_RECEIVING_AREA |  |  | Corridor east of Receving Area | QNL/BF.jpg | DIFF - the screen puts this unit somewhere column D does not | right of the Receving Area wall, in the corridor strip with S11-022; column D says Receiving Area B.008 | QNL
VAV_B_S13_001 | VAV | Included | B.034 MEETING ROOM | entity:QNL_B_034_MEETING_ROOM |  |  | Meeting Rm | QNL/BF-1.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S13_002 | VAV | Included | B.034 MEETING ROOM | entity:QNL_B_034_MEETING_ROOM |  |  | Meeting Rm | QNL/BF-1.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S13_003 | VAV | Included | B.103 PROCESSING ROOM | entity:QNL_B_103_PROCESSING_ROOM |  |  | Processing Rm | QNL/BF-5.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S13_004 | VAV | Included | B.103 PROCESSING ROOM | entity:QNL_B_103_PROCESSING_ROOM |  |  | Processing Rm | QNL/BF-5.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S13_005 | VAV | [9 empty] | QNL
VAV_B_S13_006 | VAV | Included | B.085 FUMIGATION ROOM | entity:QNL_B_085_FUMIGATION_ROOM | [6 empty] | QNL
VAV_B_S13_007 | VAV | Included | B.101 SHIPPING CLIRK | entity:QNL_B_101_SHIPPING_CLERK |  |  | Shipping Clerk | QNL/BF-5.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S13_008 | VAV | Not Included | B.105 SECURITY CONTOL ROOM | entity:QNL_B_105_SECURITY_CONTOL_ROOM |  |  | Security Store | QNL/BF-5.jpg | DIFF - the screen puts this unit somewhere column D does not | the dot is inside the Security Store cell; the screen has no room called Security Control Room, which is what column D says | QNL
VAV_B_S14_001 | VAV | Included | B.040 OFFICE | entity:QNL_B_040_OFFICE |  |  | Office | QNL/BF-4.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S14_002 | VAV | Included | B.056 OFFICE DIG INIT | entity:QNL_B_056_OFFICE_DIG_INIT | [6 empty] | QNL
VAV_B_S14_003 | VAV | Included | B.057 OFFICE AD FOR LIT | entity:QNL_B_057_OFFICE_AD_FOR_LIT |  |  | Loading Area (north-west grey band) | QNL/BF-4.jpg | DIFF - the screen puts this unit somewhere column D does not | the dot is in the grey Loading Area band, two walls west of the pink; column D says Office AD For LIT B.057 | QNL
VAV_B_S14_004 | VAV | Included | B.041 DIGITIZATION ROOM | entity:QNL_B_041_DIGITIZATION_ROOM | [6 empty] | QNL
VAV_B_S14_005 | VAV | Included | B.041 DIGITIZATION ROOM | entity:QNL_B_041_DIGITIZATION_ROOM | [6 empty] | QNL
VAV_B_S14_006 | VAV | Included | B.041 DIGITIZATION ROOM | entity:QNL_B_041_DIGITIZATION_ROOM | [6 empty] | QNL
VAV_B_S14_007 | VAV | Included | B.058 SHELL SPACE | entity:QNL_B_058_SHELL_SPACE | [6 empty] | QNL
VAV_B_S14_008 | VAV | Included | B.041 DIGITIZATION ROOM | entity:QNL_B_59_SHELL_SPACE |  |  | Office AD For LIT / Digitization Rm (open plan) | QNL/BF-4.jpg | DIFF - the screen puts this unit somewhere column D does not | the dot is in the Digitization Rm end of the open band; Shell Space is the next room east across a wall, which is what column D says | QNL
VAV_B_S14_009 | VAV | Included | B.057 OFFICE AD FOR LIT | entity:QNL_B_041_DIGITIZATION_ROOM |  |  | Office AD For LIT / Digitization Rm (open plan) | QNL/BF-4.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - Office AD For LIT end | QNL
VAV_B_S14_010 | VAV | Included | B.041 DIGITIZATION ROOM | entity:QNL_B_041_DIGITIZATION_ROOM | [6 empty] | QNL
VAV_B_S14_011 | VAV | Included | B.041 DIGITIZATION ROOM | entity:QNL_B_041_DIGITIZATION_ROOM |  |  | Office AD For LIT / Digitization Rm (open plan) | QNL/BF-4.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - Digitization Rm end | QNL
VAV_B_S14_012 | VAV | Included | B.041 DIGITIZATION ROOM | entity:QNL_B_041_DIGITIZATION_ROOM |  |  | Office AD For LIT / Digitization Rm (open plan) | QNL/BF-4.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - Digitization Rm end | QNL
VAV_B_S14_013 | VAV | Included | B.058 SHELL SPACE | entity:QNL_B_058_SHELL_SPACE | [6 empty] | QNL
VAV_B_S14_014 | VAV | Included | B.059 SHELL SPACE | entity:QNL_B_59_SHELL_SPACE | [6 empty] | QNL
VAV_B_S14_015 | VAV | Included | B.041 DIGITIZATION ROOM | entity:QNL_B_041_DIGITIZATION_ROOM | [6 empty] | QNL
VAV_B_S14_016 | VAV | Included | B.041 DIGITIZATION ROOM | entity:QNL_B_041_DIGITIZATION_ROOM | [6 empty] | QNL
VAV_B_S14_040 | VAV | Included | B.044 BOH KITCHEN | entity:QNL_B_044_BOH_KITCHEN | [6 empty] | QNL
VAV_B_S14_041 | VAV | Included | B.044 BOH KITCHEN | entity:QNL_B_044_BOH_KITCHEN | [6 empty] | QNL
VAV_B_S14_042 | VAV | Included | B.043 BINDING AND PRESERVATION SPACE | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE | [6 empty] | QNL
VAV_B_S14_043 | VAV | Included | B.043 BINDING AND PRESERVATION SPACE | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE | [6 empty] | QNL
VAV_B_S14_044 | VAV | Included | B.043 BINDING AND PRESERVATION SPACE | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE |  |  | Binding & Preservation Space | QNL/BF-4.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S14_045 | VAV | Included | B.043 BINDING AND PRESERVATION SPACE | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE |  |  | Binding & Preservation Space | QNL/BF-4.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S14_046 | VAV | Included | B.043 BINDING AND PRESERVATION SPACE | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE | [6 empty] | QNL
VAV_B_S14_047 | VAV | Included | B.044 BOH KITCHEN | entity:QNL_B_044_BOH_KITCHEN |  |  | Fine Binding / Q-Tel Rm | QNL/BF-4.jpg | SAME - screen and column D name the same room | one cell carrying both labels, west of Binding & Preservation Space | QNL
VAV_B_S14_048 | VAV | Included | B.043 BINDING AND PRESERVATION SPACE | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE | [6 empty] | QNL
VAV_B_S14_049 | VAV | Included | B.043 BINDING AND PRESERVATION SPACE | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE |  |  | Binding & Preservation Space | QNL/BF-4.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S14_050 | VAV | Included | B.043 BINDING AND PRESERVATION SPACE | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE |  |  | Binding & Preservation Space | QNL/BF-4.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S14_051 | VAV | Included | B.043 BINDING AND PRESERVATION SPACE | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE | [6 empty] | QNL
VAV_B_S15_001 | VAV | Included | B.153 PROF LIBRARIAN | entity:QNL_B_153_PROF_LIBRARIAN | [6 empty] | QNL
VAV_B_S15_002 | VAV | Not Included | B.145 LOBY AND CSECURITY | entity:QNL_B_145_LOBY_&_CSECURITY | [6 empty] | QNL
VAV_B_S15_003 | VAV | Not Included | B.145 LOBY AND CSECURITY | entity:QNL_B_145_LOBY_&_CSECURITY | [6 empty] | QNL
VAV_B_S15_004 | VAV | Not Included | B.145 LOBY AND CSECURITY | entity:QNL_B_145_LOBY_&_CSECURITY | [6 empty] | QNL
VAV_B_S15_005 | VAV | Included | B.153 PROF LIBRARIAN | entity:QNL_B_153_PROF_LIBRARIAN | [6 empty] | QNL
VAV_B_S15_006 | VAV | Included | B.153 PROF LIBRARIAN | entity:QNL_B_153_PROF_LIBRARIAN | [6 empty] | QNL
VAV_B_S15_007 | VAV | Not Included | B.152 HC SECURITY ROOM | entity:QNL_B_152_SECURITY_ROOM | [6 empty] | QNL
VAV_B_S15_008 | VAV | Included | B.151 RESEARCH AND DOC RECORD MGMT | entity:QNL_B_151_RESEARCH_&_DOC-RCRDS_MGMT | [6 empty] | QNL
VAV_B_S15_009 | VAV | Not Included | B.149 HC DIRECTOR HEAD | entity:QNL_B_149_DIRECTOR_HEAD | [6 empty] | QNL
VAV_B_S15_010 | VAV | Not Included | B.149 HC DIRECTOR HEAD | entity:QNL_B_149_DIRECTOR_HEAD |  |  | Cell north-east of VIP Majlis | QNL/BF-8.jpg | CHECK - read, but with a caveat; see the reason | the cell carries no label of its own | QNL
VAV_B_S15_011 | VAV | Not Included | B.149 HC DIRECTOR HEAD | entity:QNL_B_149_DIRECTOR_HEAD |  |  | VIP Majlis | QNL/BF-8.jpg | SAME - screen and column D name the same room |  | QNL
VAV_B_S15_012 | VAV | Not Included | B.149 HC DIRECTOR HEAD | entity:QNL_B_149_DIRECTOR_HEAD | [6 empty] | QNL
VAV_B_S15_013 | VAV | Included | B.151 RESEARCH AND DOC RECORD MGMT | entity:QNL_B_151_RESEARCH_&_DOC-RCRDS_MGMT | [6 empty] | QNL
CAV_1F_S11_001 | CAV | Included | L1.023 CORRIDOR | entity:QNL_L1_023_CORRIDOR | [6 empty] | QNL
CAV_1F_S11_002 | CAV | Included | L1.023 CORRIDOR | entity:QNL_L1_023_CORRIDOR |  |  | Grey area by L-1 and Rest Rm | QNL/FF.jpg | CHECK - read, but with a caveat; see the reason | unlabelled; may be the CORRIDOR L1.023 column D names | QNL
CAV_1F_S11_006 | CAV | Included | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING | [6 empty] | QNL
CAV_1F_S11_007 | CAV | Included | L1.023 CORRIDOR | entity:QNL_L1_023_CORRIDOR | [6 empty] | QNL
CAV_1F_S11_008 | CAV | Included | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING | [6 empty] | QNL
CAV_1F_S11_009 | CAV | Included | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING | [6 empty] | QNL
CAV_1F_S15_002 | CAV | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT |  |  | Restaurant / Front Kitchen (open plan) | QNL/FF-2.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
CAV_1F_S15_004 | CAV | Included | L1.100 AERIAL PLATFORM PARKING | entity:QNL_L1_100_AERIAL_PLATFORM_PARKING | [6 empty] | QNL
CAV_1F_S15_005 | CAV | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT |  |  | Restaurant / Front Kitchen (open plan) | QNL/FF-2.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
CAV_1F_S15_006 | CAV | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT | [6 empty] | QNL
CAV_1F_S15_010 | CAV | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT | [6 empty] | QNL
CAV_1F_S15_011 | CAV | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT |  |  | Restaurant / Front Kitchen (open plan) | QNL/FF-2.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
CAV_1F_S15_012 | CAV | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT |  |  | Restaurant / Front Kitchen (open plan) | QNL/FF-2.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - by the Front Kitchen label | QNL
CAV_1F_S15_013 | CAV | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT |  |  | Restaurant / Front Kitchen (open plan) | QNL/FF-2.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
CAV_1F_S15_014 | CAV | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT | [6 empty] | QNL
CAV_1F_S15_015 | CAV | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT |  |  | Restaurant / Front Kitchen (open plan) | QNL/FF-2.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
CAV_1F_S15_016 | CAV | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT |  |  | Restaurant / Front Kitchen (open plan) | QNL/FF-2.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
CAV_1F_S15_017 | CAV | Included | L1.150 RESTAURANT | entity:QNL_L1_150_RESTAURANT |  |  | Restaurant / Front Kitchen (open plan) | QNL/FF-2.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan | QNL
CAV_1F_S15_018 | CAV | Included | L1.100 AERIAL PLATFORM PARKING | entity:QNL_L1_100_AERIAL_PLATFORM_PARKING | [6 empty] | QNL
CAV_1F_S15_019 | CAV | Included | L1.153 FURNITURE STORE | entity:QNL_L1_153_FURNITURE_STORAGE |  |  | Band south of the Media Studios | QNL/FF-3.jpg | CHECK - read, but with a caveat; see the reason | the band carries no label; column D says FURNITURE STORE L1.153 | QNL
CAV_B_S12_001 | CAV | Included | B.063 PLANT ROOM 01 | entity:QNL_B_061_CORRIDOR |  |  | Plant Rm 1 | QNL/BF-2.jpg | DIFF - the screen puts this unit somewhere column D does not | both S12-001 and S12-002 land in Plant Rm 1; column D says CORRIDOR B.061 | QNL
CAV_B_S12_002 | CAV | Not Included | B.063 PLANT ROOM 01 | entity:QNL_B_063_PLANT_ROOM_01 |  |  | Plant Rm 1 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S12_003 | CAV | Not Included | B.063 PLANT ROOM 01 | entity:QNL_B_063_PLANT_ROOM_01 |  |  | Plant Rm 1 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S13_001 | CAV | Included | B.064 CORRIDOR 2 | entity:QNL_B_064_CORRIDOR_2 |  |  | Corridor south of Plant Rm 1 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S13_002 | CAV | Included | B.064 CORRIDOR 2 | entity:QNL_B_064_CORRIDOR_2 |  |  | Corridor south of Plant Rm 1 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S13_003 | CAV | Included | B.064 CORRIDOR 2 | entity:QNL_B_064_CORRIDOR_2 | [6 empty] | QNL
CAV_B_S13_004 | CAV | Included | B.064 CORRIDOR 2 | entity:QNL_B_064_CORRIDOR_2 |  |  | Corridor 2 | QNL/BF-5.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S13_005 | CAV | Included | B.064 CORRIDOR 2 | entity:QNL_B_064_CORRIDOR_2 |  |  | Corridor 2 | QNL/BF-5.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S13_006 | CAV | Included | B.035 CORRIDOR 4 | entity:QNL_B_035_CORRIDOR_4 |  |  | Plant Rm 2 - narrow band along its north wall | QNL/BF-2.jpg | CHECK - read, but with a caveat; see the reason | the band may be the Corridor 4 column D names; it carries no label here | QNL
CAV_B_S13_007 | CAV | Included | B.035 CORRIDOR 4 | entity:QNL_B_035_CORRIDOR_4 |  |  | Corridor 4 | QNL/BF-1.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S13_008 | CAV | Included | B.035 CORRIDOR 4 | entity:QNL_B_035_CORRIDOR_4 |  |  | Unlabelled strip north of Fire Cmd | QNL/BF-3.jpg | CHECK - read, but with a caveat; see the reason | the strip carries no label; column D says CORRIDOR 4 B.035 | QNL
CAV_B_S13_009 | CAV | Included | B.104 STORAGE | entity:QNL_B_104_STORAGE |  |  | Storage | QNL/BF-5.jpg | SAME - screen and column D name the same room | the dot sits on the Storage / Security Equip. boundary | QNL
CAV_B_S13_010 | CAV | Not Included | B.070 PLANT ROOM 02 | entity:QNL_B_070_PLANT_ROOM_02 |  |  | Plant Rm 2 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S13_011 | CAV | Not Included | B.070 PLANT ROOM 02 | entity:QNL_B_070_PLANT_ROOM_02 |  |  | Plant Rm 2 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S13_012 | CAV | Not Included | B.070 PLANT ROOM 02 | entity:QNL_B_071_FIRE_COMMAND_ROOM |  |  | Plant Rm 2 | QNL/BF-2.jpg | DIFF - the screen puts this unit somewhere column D does not | dot is inside Plant Rm 2 with S13-010 and S13-011; column D says Fire Command B.071 | QNL
CAV_B_S13_013 | CAV | Not Included | B.087 GAS SUPPRESSION ROOM | entity:QNL_B_087_GAS_SUPPRESSION_ROOM |  |  | Gas Suppression | QNL/BF-3.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S13_014 | CAV | Included | B.064 CORRIDOR 2 | entity:QNL_B_088_PEOPLE_MOVER_PLANT |  |  | Cell between Gas Suppression and Server Rm | QNL/BF-3.jpg | CHECK - read, but with a caveat; see the reason | the middle cell carries no label of its own | QNL
CAV_B_S13_015 | CAV | Not Included | B.089 SERVER ROOM | entity:QNL_B_089_SERVER_ROOM |  |  | Server Rm | QNL/BF-3.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S13_020 | CAV | Not Included | B.084 UPS BATTERY ROOM | entity:QNL_B_084_UPS_BATTERY_ROOM | [6 empty] | QNL
CAV_B_S13_021 | CAV | Not Included | B.072 SPRIMKLERS PUMPS AND ZONES VALVES | entity:QNL_B_072_SPRIMKLERS_PUMPS_&_ZONES_VALVES |  |  | Sprinkler Pump | QNL/BF-3.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S13_050 | CAV | Not Included | B.104A PLANT ROOM | entity:QNL_B_104A_PLANT_ROOM | [6 empty] | QNL
CAV_B_S14_001 | CAV | Included | B.040 OFFICE | entity:QNL_B_051_STORAGE | [6 empty] | QNL
CAV_B_S14_002 | CAV | Included | B.052 CORRIDOR 3 | entity:QNL_B_052_CORRIDOR_3 | [6 empty] | QNL
CAV_B_S14_003 | CAV | Not Included | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 | [6 empty] | QNL
CAV_B_S14_004 | CAV | Not Included | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 |  |  | Plant Rm 3 / Corridor 5 (open plan) | QNL/BF-6.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - level with the Corridor 5 label | QNL
CAV_B_S14_005 | CAV | Not Included | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 | [6 empty] | QNL
CAV_B_S14_006 | CAV | Included | B.044 BOH KITCHEN | entity:QNL_B_044_BOH_KITCHEN |  |  | Pink lobby west of Refrigerated Store | QNL/BF-4.jpg | SAME - screen and column D name the same room |  | QNL
CAV_B_S14_007 | CAV | Included | B.044 BOH KITCHEN | entity:QNL_B_044_BOH_KITCHEN | [6 empty] | QNL
CAV_B_S15_001 | CAV | Included | B.063 PLANT ROOM 01 | entity:QNL_B_063_PLANT_ROOM_01 | [6 empty] | QNL
CAV_B_S15_002 | CAV | Included | B.063 PLANT ROOM 01 | entity:QNL_B_063_PLANT_ROOM_01 | [6 empty] | QNL
CAV_B_S15_003 | CAV | Included | B.063 PLANT ROOM 01 | entity:QNL_B_063_PLANT_ROOM_01 | [6 empty] | QNL
DX_B01 | DX Unit |  | B.035 CORRIDOR 4 | entity:QNL_B_081_MV_ROOM |  |  | Corridor 4 | QNL/BF-1.jpg | CHECK - read, but with a caveat; see the reason | the dot is in the Corridor 4 strip, one wall west of MV Rm; column D says MV ROOM B.081 | QNL
DX_B02 | DX Unit |  | B.035 CORRIDOR 4 | entity:QNL_B_081_MV_ROOM | [6 empty] | QNL
DX_B03 | DX Unit |  | B.095 EMERGENCY LIGHTING BATTERY ROOM | entity:QNL_B_082_TRANSFORMER_ROOM |  |  | Emergency Lighting Battery Rm | QNL/BF-1.jpg | CHECK - read, but with a caveat; see the reason | column D says TRANSFORMER ROOM B.082, which is the room north of it | QNL
DX_B04 | DX Unit |  | B.082 TRANSFORMER ROOM | entity:QNL_B_082_TRANSFORMER_ROOM | [6 empty] | QNL
DX_B05 | DX Unit |  | B.083 HV ROOM | entity:QNL_B_083_HV_ROOM | [6 empty] | QNL
DX_B06 | DX Unit |  | B.083 HV ROOM | entity:QNL_B_083_HV_ROOM |  |  | Loading Area (pink, south-west) | QNL/BF-4.jpg | CHECK - read, but with a caveat; see the reason | the dot is in the pink Loading Area, which is where the condenser sits; column D names HV ROOM B.083, a room drawn on BF-1 | QNL
DX_B07 | DX Unit |  | B.095 EMERGENCY LIGHTING BATTERY ROOM | entity:QNL_B_095_EMERGENCY_LIGHTING_BATTERY_ROOM | [6 empty] | QNL
DX_B08 | DX Unit |  | B.095 EMERGENCY LIGHTING BATTERY ROOM | entity:QNL_B_084_UPS_BATTERY_ROOM | [6 empty] | QNL
DX_B09 | DX Unit |  | B.084 UPS BATTERY ROOM | entity:QNL_B_084_UPS_BATTERY_ROOM | [6 empty] | QNL
DX_B10 | DX Unit |  | B.103 PROCESSING ROOM | entity:QNL_B_102_SECURITY_&_BMS |  |  | Processing Rm | QNL/BF-5.jpg | CHECK - read, but with a caveat; see the reason | column D says SECURITY & BMS B.102 | QNL
DX_B11 | DX Unit |  | B.107 SECURITY EQUIPMENT ROOM | entity:QNL_B046_ITT_ITTIGATION_CONTROL_ROOM |  |  | Security Equip. | QNL/BF-5.jpg | CHECK - read, but with a caveat; see the reason | column D says ITTIGATION CONTROL ROOM B.046_ITT | QNL
DX_B12 | DX Unit |  | B.107 SECURITY EQUIPMENT ROOM | entity:QNL_B_107_SECURITY_EQUIPMENT_ROOM | [6 empty] | QNL
DX_B13 | DX Unit |  | B.093 TRANSH CHAMBER | entity:QNL_B_093_TRANSH_CHAMBER | [6 empty] | QNL
DX_B14 | DX Unit |  | B.095 EMERGENCY LIGHTING BATTERY ROOM | entity:QNL_B_082_TRANSFORMER_ROOM |  |  | Emergency Lighting Battery Rm | QNL/BF-1.jpg | CHECK - read, but with a caveat; see the reason | column D says TRANSFORMER ROOM B.082, which is the room north of it | QNL
DX_B15 | DX Unit |  | B.093 TRANSH CHAMBER | entity:QNL_B_093_TRANSH_CHAMBER | [6 empty] | QNL
DX_B16 | DX Unit |  | B.095 EMERGENCY LIGHTING BATTERY ROOM | entity:QNL_B_095_EMERGENCY_LIGHTING_BATTERY_ROOM | [6 empty] | QNL
DX_B17 | DX Unit |  | B.045A REFRIGERATE STORE | entity:QNL_B_045A_REFRIGERATE_STORE | [6 empty] | QNL
DX_B18 | DX Unit |  | B.045A REFRIGERATE STORE | entity:QNL_B_045A_REFRIGERATE_STORE | [6 empty] | QNL
DX_B19 | DX Unit |  | B.045A REFRIGERATE STORE | entity:QNL_B_045A_REFRIGERATE_STORE | [6 empty] | QNL
DX_B20 | DX Unit |  | B.092 STORAGE | entity:QNL_B_092_STORAGE | [6 empty] | QNL
DX_B21 | DX Unit |  | P.004 PLANT ZONE | entity:QNL_P_004_PLANT_ZONE | [6 empty] | QNL
DX_B22 | DX Unit |  | B.106 REST ROOM SECURITY | entity:QNL_B106_RES_REST_ROOM_SECURITY | [6 empty] | QNL
DX_B23 | DX Unit |  | B.107 SECURITY EQUIPMENT ROOM | entity:QNL_B_107_SECURITY_EQUIPMENT_ROOM | [6 empty] | QNL
DX_B24 | DX Unit |  | P.004 PLANT ZONE | entity:QNL_P_004_PLANT_ZONE | [6 empty] | QNL
HEX01 | HEX |  | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 | [6 empty] | QNL
HEX02 | HEX |  | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 | [6 empty] | QNL
HEX03 | HEX |  | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 | [6 empty] | QNL
HEX04 | HEX |  | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 | [6 empty] | QNL
HEX05 | HEX |  | B.211 PH PLANT ROOM | entity:QNL_B_211_PH_PLANT_ROOM | [6 empty] | QNL
EF_201 | EF |  | L-3 L 3 | entity:QNL_L1-L-3_L-3 | [6 empty] | QNL
EF_B05 | EF |  | B.085 FUMIGATION ROOM | entity:QNL_B_085_FUMIGATION_ROOM | [6 empty] | QNL
EF_B06 | EF |  | B.055 DIGITIZATION CENTER | entity:QNL_B_055_DIGITIZATION_CENTER | [6 empty] | QNL
EF_B07 | EF |  | B.109 LOADING AREA | entity:QNL_B_109_LOADING_AREA |  |  | Loading Area (north-west grey band) | QNL/BF-4.jpg | SAME - screen and column D name the same room |  | QNL
EF_B08 | EF |  | B.109 LOADING AREA | entity:QNL_B_109_LOADING_AREA | [6 empty] | QNL
EF_B09 | EF |  | B.080 GENERATOR | entity:QNL_B_080_GENERATOR | [6 empty] | QNL
EF_B10 | EF |  | B.093 TRANSH CHAMBER | entity:QNL_B_093_TRANSH_CHAMBER | [6 empty] | QNL
EF_B11 | EF |  | B.091 FUEL ROOM | entity:QNL_B_091_FUEL_ROOM | [6 empty] | QNL
EF_B12 | EF |  | B.214 IDF ROOM | entity:QNL_B_214_IDF_ROOM | [6 empty] | QNL
EF_B13 | EF |  | B.072 SPRIMKLERS PUMPS AND ZONES VALVES | entity:QNL_B_072_SPRIMKLERS_PUMPS_&_ZONES_VALVES |  |  | Plant Rm 2 | QNL/BF-2.jpg | CHECK - read, but with a caveat; see the reason | the dot is inside Plant Rm 2 with the AHUs, which is where the fan sits; column D names Sprinklers Pumps B.072, a room drawn on BF-3, so the two are answering different questions | QNL
EF_B14 | EF |  | B.064 CORRIDOR 2 | entity:QNL_B_071_FIRE_COMMAND_ROOM |  |  | Plant Rm 2 | QNL/BF-2.jpg | CHECK - read, but with a caveat; see the reason | the dot is inside Plant Rm 2 with the AHUs, which is where the fan sits; column D names Fire Command B.071, a room drawn on BF-3 | QNL
EF_B15 | EF |  | B.109 LOADING AREA | entity:QNL_B_109_LOADING_AREA | [6 empty] | QNL
EF_B16 | EF |  | B.109 LOADING AREA | entity:QNL_B_109_LOADING_AREA | [6 empty] | QNL
EF_BBV01 | EF |  | B.070 PLANT ROOM 02 | entity:QNL_B_070_PLANT_ROOM_02 | [6 empty] | QNL
EF_BBV02 | EF |  | B.070 PLANT ROOM 02 | entity:QNL_B_070_PLANT_ROOM_02 |  |  | Plant Rm 2 | QNL/BF-2.jpg | SAME - screen and column D name the same room |  | QNL
EF_RP01 | EF |  | P.002 PLANT ZONE | entity:QNL_P_002_PLANT_ZONE | [6 empty] | QNL
EF_RP02 | EF |  | P.004 PLANT ZONE | entity:QNL_P_004_PLANT_ZONE | [6 empty] | QNL
EF_RP03 | EF |  | P.007 PLANT ZONE | entity:QNL_P_007_PLANT_ZONE |  |  | Plant Zone | QNL/RF-3.jpg | SAME - screen and column D name the same room | the screen prints Plant Zone with no P-number, so which plant zone it is cannot be checked from it | QNL
KEF_101 | KEF |  | L1.067 RESTAURANT | entity:QNL_L1_067_RESTAURANT | [6 empty] | QNL
KEF_B019 | KEF |  | B.049 MEP KITCHEN | entity:QNL_B_049_MEP_KITCHEN | [6 empty] | QNL
KEF_B020 | KEF |  | B.052 CORRIDOR 3 | entity:QNL_B_052_CORRIDOR_3 | [6 empty] | QNL
KEF_B04 | KEF |  | B.001A BREAK OUT AREA | entity:QNL_B_001A_BREAK_OUT_AREA |  |  | Break Out Area / Tech.Services & Collections Office (open plan) | QNL/BF.jpg | OPEN - one space, two or more labels; the screen cannot split them | open plan - west end | QNL
SEF_RP04 | SEF |  | P.002 PLANT ZONE | entity:QNL_P_002_PLANT_ZONE | [6 empty] | QNL
SEF_RP05 | SEF |  | P.002 PLANT ZONE | entity:QNL_P_002_PLANT_ZONE | [6 empty] | QNL
SEF_RP06 | SEF |  | P.002 PLANT ZONE | entity:QNL_P_002_PLANT_ZONE | [6 empty] | QNL
SEF_RP07 | SEF |  | P.004 PLANT ZONE | entity:QNL_P_004_PLANT_ZONE | [6 empty] | QNL
SEF_RP08 | SEF |  | P.004 PLANT ZONE | entity:QNL_P_004_PLANT_ZONE | [6 empty] | QNL
SEF_RP09 | SEF |  | P.004 PLANT ZONE | entity:QNL_P_004_PLANT_ZONE | [6 empty] | QNL
SEF_RP10 | SEF |  | P.007 PLANT ZONE | entity:QNL_P_007_PLANT_ZONE |  |  | Plant Zone | QNL/RF-3.jpg | SAME - screen and column D name the same room | the screen prints Plant Zone with no P-number, so which plant zone it is cannot be checked from it | QNL
SEF_RP11 | SEF |  | P.006 PLANT ZONE | entity:QNL_P_006_PLANT_ZONE |  |  | Plant Zone | QNL/RF-3.jpg | SAME - screen and column D name the same room | the screen prints Plant Zone with no P-number, so which plant zone it is cannot be checked from it | QNL
SEF_RP12 | SEF |  | P.006 PLANT ZONE | entity:QNL_P_006_PLANT_ZONE |  |  | Plant Zone | QNL/RF-3.jpg | SAME - screen and column D name the same room | the screen prints Plant Zone with no P-number, so which plant zone it is cannot be checked from it | QNL
SEF_ZoneA | SEF |  | P.002 PLANT ZONE | entity:QNL_P_002_PLANT_ZONE | [6 empty] | QNL
SEF_ZoneB | SEF |  | P.004 PLANT ZONE | entity:QNL_P_004_PLANT_ZONE | [6 empty] | QNL
SEF_ZoneC | SEF |  | P.007 PLANT ZONE | entity:QNL_P_007_PLANT_ZONE | [6 empty] | QNL
TEF_101C | TEF |  | E2 SHAFT | entity:QNL_L1-E2_ELEC_SHAFT | [6 empty] | QNL
TEF_102C | TEF |  | E1 SHAFT | entity:QNL_L1-E1_ELEC_SHAFT | [6 empty] | QNL
TEF_B01A | TEF |  | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 | [6 empty] | QNL
TEF_B01B | TEF |  | B.110 PLANT ROOM 03 | entity:QNL_B_110_PLANT_ROOM_03 | [6 empty] | QNL
TEF_B02A | TEF |  | B.070 PLANT ROOM 02 | entity:QNL_B_070_PLANT_ROOM_02 | [6 empty] | QNL
TEF_B02B | TEF |  | B.070 PLANT ROOM 02 | entity:QNL_B_070_PLANT_ROOM_02 | [6 empty] | QNL
TEF_B03A | TEF |  | B.120 COMPACT SHELVING MAIN COLLECTION | entity:QNL_B_120_COMPACT_SHELVING_-MAIN_COLLECTION | [6 empty] | QNL
TEF_B03B | TEF |  | B.120 COMPACT SHELVING MAIN COLLECTION | entity:QNL_B_120_COMPACT_SHELVING_-MAIN_COLLECTION | [6 empty] | QNL
CCU_B01 | CCU |  | B.048 QTEL ROOM | entity:QNL_B_048_QTEL_ROOM | [6 empty] | QNL
CCU_B02 | CCU |  | B.048 QTEL ROOM | entity:QNL_B_048_QTEL_ROOM | [6 empty] | QNL
CCU_B03 | CCU |  | B.050 TELECOM ROOM | entity:QNL_B_050_TELECOM_ROOM | [6 empty] | QNL
CCU_B04 | CCU |  | B.050 TELECOM ROOM | entity:QNL_B_050_TELECOM_ROOM | [6 empty] | QNL
CCU_B05 | CCU |  | B.089 SERVER ROOM | entity:QNL_B_089_SERVER_ROOM | [6 empty] | QNL
CCU_B06 | CCU |  | B.089 SERVER ROOM | entity:QNL_B_089_SERVER_ROOM | [6 empty] | QNL
CCU_B07 | CCU |  | B.089 SERVER ROOM | entity:QNL_B_089_SERVER_ROOM | [6 empty] | QNL
CCU_B08 | CCU |  | B.141 VAULT | entity:QNL_B141_VAU_VAULT | [6 empty] | QNL
CCU_B09 | CCU |  | B.141 VAULT | entity:QNL_B141_VAU_VAULT | [6 empty] | QNL
CCU_B10 | CCU |  | B.222 IDF | entity:QNL_B_222_IDF | [6 empty] | QNL
CCU_B11 | CCU |  | B.222 IDF | entity:QNL_B_222_IDF | [6 empty] | QNL
CCU_8081 | CCU | [9 empty] | QNL
CCU_8082 | CCU | [9 empty] | QNL
CCU_8083 | CCU | [9 empty] | QNL
CCU_8084 | CCU | [9 empty] | QNL
CCU_8085 | CCU | [9 empty] | QNL
CCU_8086 | CCU | [9 empty] | QNL
CCU_MDFRm | CCU | [9 empty] | QNL
CCU_Qtel | CCU | [9 empty] | QNL
CCU_Server_Rm | CCU | [9 empty] | QNL
CCU_AVServer_Rm | CCU | [9 empty] | QNL
CCU_HeritageVault | CCU | [9 empty] | QNL
CHW_P01 | CHW Pump |  | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 | [6 empty] | QNL
CHW_P02 | CHW Pump |  | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 | [6 empty] | QNL
CHW_P03 | CHW Pump |  | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 | [6 empty] | QNL
CHW_P04 | CHW Pump |  | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 | [6 empty] | QNL
CHWPU_P01 | CHW Pump |  | B.220 PLANT ROOM 04 | entity:QNL_B_220_PLANT_ROOM_04 | [6 empty] | QNL
CHWPU_P02 | CHW Pump | [9 empty] | QNL
ELEC_Gen | Generator |  | B.080 GENERATOR | entity:QNL_B_080_GENERATOR | [6 empty] | QNL
AHUB_0001 | AHU | Not Included | B.013 CHILLED WATER | entity:SSC_B1_013_CHILLED_WATER |  |  | B.013 CHILLED WATER | SSC/BF-part1.jpg |  |  | SSC
AHUB_0002 | AHU | Not Included | B.014 VENT PLANT | entity:SSC_B1_014_VENT_PLANT |  |  | B.014 VENT PLANT | SSC/BF-part1.jpg |  |  | SSC
AHUB_0003 | AHU | Not Included | B.014 VENT PLANT | entity:SSC_B1_014_VENT_PLANT |  |  | B.014 VENT PLANT | SSC/BF-part1.jpg |  |  | SSC
AHUB_0004 | AHU | Not Included | B.008 VENT PLANT | entity:SSC_B1_008_VENT_PLANT |  |  | B.008 VENT PLANT | SSC/BF-part2.jpg |  |  | SSC
AHUB_0005 | AHU | Not Included | B.014 VENT PLANT | entity:SSC_B1_013_CHILLED_WATER |  |  | B.014 VENT PLANT | SSC/BF-part1.jpg |  |  | SSC
FCU0001 | FCU | Not Included | B.016 SPRINKLER AND WATER | entity:SSC_B1_016_SPRINKLER_&_WATER |  | SPRINKLER & WATER RM B.016 | B.016 SPRINKLER AND WATER | SSC/BF-part1.jpg |  |  | SSC
FCU0002 | FCU | Not Included | B.025 MAIN SEC CONTROL ROOM | entity:SSC_B1_025_MAIN_SEC._CONTROL_ROOM |  |  | B.025 MAIN SEC CONTROL ROOM | SSC/BF-part1.jpg |  |  | SSC
FCU0003 | FCU | Not Included | B.030 CORRIDOR | entity:SSC_B1_039_BMS |  | BMS B.039 | B.030 CORRIDOR | SSC/BF-part1.jpg |  |  | SSC
FCU0004 | FCU | Not Included | 1.008 AV ROOM | entity:SSC_01_008_AV_ROOM |  | A/V ROOM 1.008 |  |  |  |  | SSC
FCU0005 | FCU | Not Included | 1.027 IDF 1 | entity:SSC_01_027_IDF_1 |  |  | 01.027 IDF-1 | SSC/FF-part2.jpg |  |  | SSC
FCU0006 | FCU | Not Included | 1.027 IDF 1 | entity:SSC_01_027_IDF_1 | [6 empty] | SSC
FCU0007 | FCU | Not Included | 1.039 IDF 2 | entity:SSC_01_039_IDF_2 |  |  | 01.039 IDF-2 | SSC/FF-part2.jpg |  |  | SSC
FCU0008 | FCU | Not Included | 1.039 IDF 2 | entity:SSC_01_039_IDF_2 | [6 empty] | SSC
FCU0009 | FCU | Included | 1.029 SHELL SPACE | entity:SSC_01_028_CORRIDOR |  | AIR LOCK 1.034 |  |  |  |  | SSC
FCU0010 | FCU | Included | 1.013 CORRIDOR | entity:SSC_01_010_CORRIDOR |  | AIR LOCK 1.011 | 01.013 CORRIDOR | SSC/FF-part1.jpg |  |  | SSC
FCU0011 | FCU | Included | 3.033 PRINTING | entity:SSC_03_033_PRINTING |  | PRINTING ROOM 2 03.033 |  |  |  |  | SSC
VAV0001 | VAV | Included | B.015 ENTRANCE | entity:SSC_B1_015_ENTRANCE |  |  | B.015 ENTRANCE | SSC/BF-part1.jpg |  |  | SSC
VAV0002 | VAV | Included | 1.014 SHELL SPACE | entity:SSC_01_014_SHELL_SPACE |  | SHELL SPACE NW 01.014 | 01.014 SHELL SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0003 | VAV | Included | 1.014 SHELL SPACE | entity:SSC_01_014_SHELL_SPACE |  |  | 01.014 SHELL SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0004 | VAV | Included | 1.014 SHELL SPACE | entity:SSC_01_014_SHELL_SPACE |  |  | 01.014 SHELL SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0005 | VAV | Included | 1.015 SHELL SPACE | entity:SSC_01_015_SHELL_SPACE |  | SHELL SPACE SW 01.015 | 01.015 SHELL SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0006 | VAV | Included | 1.015 SHELL SPACE | entity:SSC_01_015_SHELL_SPACE |  |  | 01.015 SHELL SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0007 | VAV | Included | 1.015 SHELL SPACE | entity:SSC_01_015_SHELL_SPACE |  |  | 01.015 SHELL SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0008 | VAV | Included | 1.024 CORRIDOR | entity:SSC_01_024_CORRIDOR |  | CORRIDORS SE 01.024 | 01.024 CORRIDOR | SSC/FF-part2.jpg |  |  | SSC
VAV0009 | VAV | Included | 1.001 CORRIDOR | entity:SSC_01_019_PRAYER_ROOM |  |  | 01.002 SHELL SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0010 | VAV | Included | 1.019 PRAYER ROOM | entity:SSC_01_019_PRAYER_ROOM |  |  | 01.019 PRAYER ROOM | SSC/FF-part1.jpg |  |  | SSC
VAV0011 | VAV | Included | 1.019 PRAYER ROOM | entity:SSC_01_019_PRAYER_ROOM | [6 empty] | SSC
VAV0012 | VAV | Included | 1.019 PRAYER ROOM | entity:SSC_01_019_PRAYER_ROOM |  |  | 01.019 PRAYER ROOM | SSC/FF-part1.jpg |  |  | SSC
VAV0013 | VAV | Included | 1.019 PRAYER ROOM | entity:SSC_01_019_PRAYER_ROOM |  |  | 01.019 PRAYER ROOM | SSC/FF-part2.jpg |  |  | SSC
VAV0014 | VAV | Included | 1.019 PRAYER ROOM | entity:SSC_01_019_PRAYER_ROOM |  |  | 01.019 PRAYER ROOM | SSC/FF-part2.jpg |  |  | SSC
VAV0015 | VAV | Included | 1.029 ROOM NO 42 | entity:SSC_01_029_ROOM_NO_42 |  | SHELL SPACE E 01.029 | 01.029 SHELL SPACE | SSC/FF-part2.jpg |  |  | SSC
VAV0016 | VAV | Included | 1.029 ROOM NO 43 | entity:SSC_01_029_ROOM_NO_43 |  |  | 01.029 SHELL SPACE | SSC/FF-part2.jpg |  |  | SSC
VAV0017 | VAV | Included | 1.029 ROOM NO 44 | entity:SSC_01_029_ROOM_NO_44 |  |  | 01.029 SHELL SPACE | SSC/FF-part2.jpg |  |  | SSC
VAV0018 | VAV | Included | 1.029 SHELL SPACE | entity:SSC_01_029_SHELL_SPACE |  |  | 01.029 SHELL SPACE | SSC/FF-part2.jpg |  |  | SSC
VAV0019 | VAV | Included | 1.029 SHELL SPACE | entity:SSC_01_029_SHELL_SPACE |  |  | 01.029 SHELL SPACE | SSC/FF-part2.jpg |  |  | SSC
VAV0020 | VAV | Included | 1.029 SHELL SPACE | entity:SSC_01_029_SHELL_SPACE | [6 empty] | SSC
VAV0021 | VAV | Included | 1.013 CORRIDOR | entity:SSC_01_013_CORRIDOR |  | CORRIDORS W 01.013 | 01.013 CORRIDOR | SSC/FF-part1.jpg |  |  | SSC
VAV0022 | VAV | Included | 1.003 OPEN SPACE | entity:SSC_01_003_OPEN_SPACE |  | OPEN OFFICE BELOW SKYLIGHT 01.003 |  |  |  |  | SSC
VAV0023 | VAV | Included | 1.003 OPEN SPACE | entity:SSC_01_003_OPEN_SPACE | [6 empty] | SSC
VAV0024 | VAV | Included | 1.003 OPEN SPACE | entity:SSC_01_001_CORRIDOR |  | CORRIDORS S 01.001 | 01.003 OPEN SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0025 | VAV | Included | 1.002 SHELL SPACE | entity:SSC_01_002_SHELL_SPACE |  |  | 01.002 SHELL SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0026 | VAV | Included | 1.002 SHELL SPACE | entity:SSC_01_002_SHELL_SPACE |  | SHELL SPACE S 01.002 |  |  |  |  | SSC
VAV0027 | VAV | Included | 1.002 SHELL SPACE | entity:SSC_01_002_SHELL_SPACE |  |  | 01.002 SHELL SPACE | SSC/FF-part2.jpg |  |  | SSC
VAV0028 | VAV | Included | 1.002 SHELL SPACE | entity:SSC_01_002_SHELL_SPACE |  | OPEN OFFICE BELOW SKYLIGHT 01.003 | 01.002 SHELL SPACE | SSC/FF-part2.jpg |  |  | SSC
VAV0029 | VAV | Included | 1.003 OPEN SPACE | entity:SSC_01_001_CORRIDOR |  |  | 01.003 OPEN SPACE | SSC/FF-part2.jpg |  |  | SSC
VAV0030 | VAV | Included | 1.016 SHELL SPACE | entity:SSC_01_016_SHELL_SPACE |  | PRINTING ROOM SHELL SPACE 01.016 | 01.016 SHELL SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0031 | VAV | Included | 1.003 OPEN SPACE | entity:SSC_01_001_CORRIDOR |  |  | 01.003 OPEN SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0032 | VAV | Included | 1.018 CORRIDOR | entity:SSC_01_018_CORRIDOR |  | CORRIDORS SW 01.018 | 01.018 CORRIDOR | SSC/FF-part1.jpg |  |  | SSC
VAV0033 | VAV | Included | 1.039 IDF 2 | entity:SSC_01_028_CORRIDOR |  | IDF 01.027 & 39 | 01.025 MALE TOILET | SSC/FF-part2.jpg |  |  | SSC
VAV0034 | VAV | Included | 1.003 OPEN SPACE | entity:SSC_01_003_OPEN_SPACE |  | CORRIDOR CENTRAL 01.004 | 01.003 OPEN SPACE | SSC/FF-part1.jpg |  |  | SSC
VAV0035 | VAV | Included | 1.028 CORRIDOR | entity:SSC_01_010_CORRIDOR |  | CORRIDORS E 01.028 | 01.028 CORRIDOR | SSC/FF-part2.jpg |  |  | SSC
VAV0036 | VAV | Included | 1.019 PRAYER ROOM | entity:SSC_01_022_ABLUTION_ROOM |  | ABLUTION ROOMS 01.020 & 23 | 01.019 PRAYER ROOM | SSC/FF-part2.jpg |  |  | SSC
VAV0037 | VAV | Not Included | 1.008 AV ROOM | entity:SSC_01_008_AV_ROOM |  | A/V RM 1.008 |  |  |  |  | SSC
VAV0038 | VAV | Included | ST-4 STAIR 4 | entity:SSC_01_ST-4_STAIR_4 |  | CORRIDOR AUDITORIUM W 01.010 |  |  |  |  | SSC
VAV0039 | VAV | Included | 1.003 OPEN SPACE | entity:SSC_01_003_OPEN_SPACE |  | CORRIDOR AUDITORIUM E 01.035 | 01.028 CORRIDOR | SSC/FF-part2.jpg |  |  | SSC
VAV0040 | VAV | Included | 2.006 CONFERENCE ROOM | entity:SSC_02_006_CONFERENCE_ROOM |  |  | 02.006 CONFERENCE ROOM | SSC/Second Floor.jpg |  |  | SSC
VAV0041 | VAV | Not Included | 2.005 EXECUTIVE CONFERENCE ROOM | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM |  |  | 02.005 EXECUTIVE CONFERENCE ROOM | SSC/Second Floor.jpg |  |  | SSC
VAV0042 | VAV | Not Included | 2.005 EXECUTIVE CONFERENCE ROOM | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM |  |  | 02.005 EXECUTIVE CONFERENCE ROOM | SSC/Second Floor.jpg |  |  | SSC
VAV0043 | VAV | Included | 2.004 CORRIDOR | entity:SSC_02_004_CORRIDOR | [6 empty] | SSC
VAV0044 | VAV | Included | 2.001 FOYER | entity:SSC_02_001_FOYER | [6 empty] | SSC
VAV0045 | VAV | Included | 2.001 FOYER | entity:SSC_02_001_FOYER | [6 empty] | SSC
VAV0046 | VAV | Included | 2.002 LOBBY | entity:SSC_02_002_LOBBY |  |  | 02.002 LOBBY | SSC/Second Floor.jpg |  |  | SSC
VAV0047 | VAV | Included | 2.002 LOBBY | entity:SSC_02_002_LOBBY |  |  | 02.002 LOBBY | SSC/Second Floor.jpg |  |  | SSC
VAV0048 | VAV | Included | 2.002 LOBBY | entity:SSC_02_002_LOBBY |  |  | 02.002 LOBBY | SSC/Second Floor.jpg |  |  | SSC
VAV0049 | VAV | Included | 2.003 CORRIDOR | entity:SSC_02_002_LOBBY |  |  | 02.003 CORRIDOR | SSC/Second Floor.jpg |  |  | SSC
VAV0050 | VAV | Included | 2.002 LOBBY | entity:SSC_02_003_CORRIDOR |  |  | 02.002 LOBBY | SSC/Second Floor.jpg |  |  | SSC
VAV0051 | VAV | Not Included | 2.005 EXECUTIVE CONFERENCE ROOM | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM |  |  | 02.005 EXECUTIVE CONFERENCE ROOM | SSC/Second Floor.jpg |  |  | SSC
VAV0052 | VAV | Included | 2.006 CONFERENCE ROOM | entity:SSC_02_006_CONFERENCE_ROOM |  |  | 02.006 CONFERENCE ROOM | SSC/Second Floor.jpg |  |  | SSC
VAV0053 | VAV | Included | 3.015 RESEARCHER OFFICE | entity:SSC_03_015_RESEARCHERS_OFFICE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.015 RESEARCHER OFFICE | SSC/TF-part1.jpg |  |  | SSC
VAV0054 | VAV | Included | 3.014 VISITOR S CUBICLE | entity:SSC_03_014_VISITORS_CUBICLE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.014 VISITORS CUBIDE | SSC/TF-part1.jpg |  |  | SSC
VAV0055 | VAV | Included | 3.013 RESEARCHER OFFICE | entity:SSC_03_013_RESEARCHERS_OFFICE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.013 RESEARCHER OFFICE | SSC/TF-part1.jpg |  |  | SSC
VAV0056 | VAV | Included | 3.012 RESEARCHER OFFICE | entity:SSC_03_012_RESEARCHERS_OFFICE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.012 RESEARCHER OFFICE | SSC/TF-part1.jpg |  |  | SSC
VAV0057 | VAV | Included | 3.011 VISITOR S CUBICLE | entity:SSC_03_011_VISITORS_CUBICLE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.011 VISITORS CUBIDE | SSC/TF-part1.jpg |  |  | SSC
VAV0058 | VAV | Included | 3.010 RESEARCHER OFFICE | entity:SSC_03_010_RESEARCHERS_OFFICE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.010 RESEARCHER OFFICE | SSC/TF-part1.jpg |  |  | SSC
VAV0059 | VAV | Included | 3.009 RESEARCHER OFFICE | entity:SSC_03_009_RESEARCHERS_OFFICE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.009 RESEARCHER OFFICE | SSC/TF-part1.jpg |  |  | SSC
VAV0060 | VAV | Included | 3.008 VISITOR S CUBICLE | entity:SSC_03_008_VISITORS_CUBICLE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.008 VISITORS CUBIDE | SSC/TF-part1.jpg |  |  | SSC
VAV0061 | VAV | Included | 3.007 OPERATIONS MANAGERS | entity:SSC_03_007_OPERATIONS_MANAGER | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.007 OPERATIONS MANAGERS | SSC/TF-part1.jpg |  |  | SSC
VAV0062 | VAV | Included | 3.006A ROOM | entity:SSC_03_006_MEETING_ROOM | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.006A ROOM | SSC/TF-part2.jpg |  |  | SSC
VAV0063 | VAV |  | (NOT FOUND ON DRAWING LEVEL 3) | #N/A | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS | [5 empty] | SSC
VAV0064 | VAV | Included | 3.006B ROOM | entity:SSC_03_006_MEETING_ROOM | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS | [5 empty] | SSC
VAV0065 | VAV | Included | 3.005 RESEARCHER OFFICE | entity:SSC_03_005_RESEARCHERS_OFFICE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS | [5 empty] | SSC
VAV0066 | VAV | Included | 3.004 VISITOR S CUBICLE | entity:SSC_03_004_VISITORS_CUBICLE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS | [5 empty] | SSC
VAV0067 | VAV | Included | 3.003 RESEARCHER OFFICE | entity:SSC_03_003_RESEARCHERS_OFFICE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS | [5 empty] | SSC
VAV0068 | VAV | Not Included | 3.002 DIRECTOR MEETING ROOM | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS | [5 empty] | SSC
VAV0069 | VAV | Not Included | 3.002 DIRECTOR MEETING ROOM | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS | [5 empty] | SSC
VAV0070 | VAV | Not Included | 3.001 DIRECTOR S OFFICE | entity:SSC_03_001_DIRECTORS_OFFICE | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS | [5 empty] | SSC
VAV0071 | VAV | Included | 3.032 GENERAL OFFICE AREA | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.032 GENERAL OFFICE AREA | SSC/TF-part2.jpg |  |  | SSC
VAV0072 | VAV | Included | 3.032 GENERAL OFFICE AREA | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.032 GENERAL OFFICE AREA | SSC/TF-part2.jpg |  |  | SSC
VAV0073 | VAV | Included | 3.032 GENERAL OFFICE AREA | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS | [5 empty] | SSC
VAV0074 | VAV | Included | 3.032 GENERAL OFFICE AREA | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS | [5 empty] | SSC
VAV0075 | VAV | Included | 3.032 GENERAL OFFICE AREA | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.032 GENERAL OFFICE AREA | SSC/TF-part2.jpg |  |  | SSC
VAV0076 | VAV | Included | 3.031 ASSOC DIRECTORS OFFICE | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS | [5 empty] | SSC
VAV0077 | VAV | Included | 3.032 GENERAL OFFICE AREA | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | FOUND ON THE MECH DRAWINGS BUT MISSED ON THE BMS DRAWINGS |  | 03.032 GENERAL OFFICE AREA | SSC/TF-part2.jpg |  |  | SSC
VAV0078 | VAV | Included | 3.031 ASSOC DIRECTORS OFFICE | entity:SSC_03_031_ASSOC._DIRECTORS_OFFICE |  |  | 03.031 ASSOC.DIR OFFICE | SSC/TF-part2.jpg |  |  | SSC
VAV0079 | VAV | Not Included | 3.030 ASSOC DIRECTORS MEETING ROOM | entity:SSC_03_030_ASSOC._DIRECTORS_MEETING_ROOM | [6 empty] | SSC
VAV0080 | VAV | Not Included | 3.030 ASSOC DIRECTORS MEETING ROOM | entity:SSC_03_030_ASSOC._DIRECTORS_MEETING_ROOM |  |  | 03.030 ASSOC.DIR MEETING ROOM | SSC/TF-part2.jpg |  |  | SSC
VAV0081 | VAV | Included | 3.029 RESEARCHER OFFICE | entity:SSC_03_029_RESEARCHERS_OFFICE |  |  | 03.029 RESEARCHER OFFICE | SSC/TF-part2.jpg |  |  | SSC
VAV0082 | VAV | Included | 3.028 VISITOR S CUBICLE | entity:SSC_03_028_VISITORS_CUBICLE |  |  | 03.028 VISITORS CUBIDE | SSC/TF-part2.jpg |  |  | SSC
VAV0083 | VAV | Included | 3.027 RESEARCHER OFFICE | entity:SSC_03_027_RESEARCHERS_OFFICE |  |  | 03.027 RESEARCHER OFFICE | SSC/TF-part2.jpg |  |  | SSC
VAV0084 | VAV | Included | 3.026 MEETING ROOM | entity:SSC_03_026_MEETING_ROOM | [6 empty] | SSC
VAV0085 | VAV | Included | 3.026 MEETING ROOM | entity:SSC_03_026_MEETING_ROOM |  |  | 03.026 MEETING ROOM | SSC/TF-part2.jpg |  |  | SSC
VAV0086 | VAV | Included | 3.026 MEETING ROOM | entity:SSC_03_026_MEETING_ROOM |  |  | 03.026 MEETING ROOM | SSC/TF-part2.jpg |  |  | SSC
VAV0087 | VAV | Included | 3.025 SECRETARIAL AREA | entity:SSC_03_025_SECRETARIAL_AREA |  |  | 03.025 SECRETARIAL AREA | SSC/TF-part1.jpg |  |  | SSC
VAV0088 | VAV | Included | 3.024 VISITOR S CUBICLE | entity:SSC_03_024_VISITORS_CUBICLE |  |  | 03.024 VISITORS CUBIDE | SSC/TF-part1.jpg |  |  | SSC
VAV0089 | VAV | Included | 3.023 RESEARCHER OFFICE | entity:SSC_03_023_RESEARCHERS_OFFICE |  |  | 03.023 RESEARCHER OFFICE | SSC/TF-part1.jpg |  |  | SSC
VAV0090 | VAV | Included | 3.022 RESEARCHER OFFICE | entity:SSC_03_022_RESEARCHERS_OFFICE |  |  | 03.022 RESEARCHER OFFICE | SSC/TF-part1.jpg |  |  | SSC
VAV0091 | VAV | Included | 3.021 VISITOR S CUBICLE | entity:SSC_03_021_VISITORS_CUBICLE |  |  | 03.021 VISITORS CUBIDE | SSC/TF-part1.jpg |  |  | SSC
VAV0092 | VAV | Included | 3.020 RESEARCHER OFFICE | entity:SSC_03_020_RESEARCHERS_OFFICE |  |  | 03.020 RESEARCHER OFFICE | SSC/TF-part1.jpg |  |  | SSC
VAV0093 | VAV | Included | 3.019 IT MANAGERS OFFICE | entity:SSC_03_019_IT_MANAGERS_OFFICE |  |  | 03.019 IT MANAGERS OFFICE | SSC/TF-part1.jpg |  |  | SSC
VAV0094 | VAV | Included | 3.018 VISITOR S CUBICLE | entity:SSC_03_018_VISITORS_CUBICLE |  |  | 03.018 VISITORS CUBIDE | SSC/TF-part1.jpg |  |  | SSC
VAV0095 | VAV | Included | 3.017 RESEARCHER OFFICE | entity:SSC_03_017_RESEARCHERS_OFFICE |  |  | 03.017 RESEARCHER OFFICE | SSC/TF-part1.jpg |  |  | SSC
VAV0096 | VAV | Included | 3.016 LOUNGE | entity:SSC_03_016_LOUNGE | [6 empty] | SSC
VAV0097 | VAV | Included | 3.016 LOUNGE | entity:SSC_03_016_LOUNGE | [6 empty] | SSC
VAV0098 | VAV | Included | 3.016 LOUNGE | entity:SSC_03_049_IT_OFFICE | [6 empty] | SSC
VAV0099 | VAV | Included | 3.034 CORRIDOR | entity:SSC_03_042_CORRIDOR | [6 empty] | SSC
VAV0100 | VAV | Included | 3.041 CORRIDOR | entity:SSC_03_041_CORRIDOR | [6 empty] | SSC
VAV0101 | VAV | Included | 3.042 CORRIDOR | entity:SSC_03_044_CORRIDOR | [6 empty] | SSC
VAV0102 | VAV | Included | 3.041 CORRIDOR | entity:SSC_03_034_CORRIDOR |  | STUDY LIBRARY AREA UNDER SKYLIGHT AND CORRIDORS N 03.034 | 03.041 | SSC/TF-part1.jpg |  |  | SSC
VAV0103 | VAV | Included | 3.034 CORRIDOR | entity:SSC_03_034_CORRIDOR | [6 empty] | SSC
VAV0104 | VAV | Included | 3.034 CORRIDOR | entity:SSC_03_034_CORRIDOR | [6 empty] | SSC
VAV0105 | VAV | Included | 3.034 CORRIDOR | entity:SSC_03_034_CORRIDOR | [6 empty] | SSC
VAV0106 | VAV | Included | 3.042 CORRIDOR | entity:SSC_03_042_CORRIDOR | [6 empty] | SSC
VAV0107 | VAV | Included | 3.032 GENERAL OFFICE AREA | entity:SSC_03_002_DIRECTORS_MEETING_ROOM |  | GENERAL OFFICE AREA 03.032 | 03.032 GENERAL OFFICE AREA | SSC/TF-part2.jpg |  |  | SSC
VAV0108 | VAV | Included | 3.032 GENERAL OFFICE AREA | entity:SSC_03_002_DIRECTORS_MEETING_ROOM |  | GENERAL OFFICE AREA 03.032 | 03.032 GENERAL OFFICE AREA | SSC/TF-part2.jpg |  |  | SSC
RDC_NB_AHU8511 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | [7 empty] | RDC
RDC_NB_AHU8512 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | [7 empty] | RDC
RDC_NB_2F_2F_AHU8513 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | [7 empty] | RDC
RDC_NB_2F_AHU8514 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | [7 empty] | RDC
RDC_NB_2F_AHU8515 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | [7 empty] | RDC
RDC_NB_2F_AHU8516 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | [7 empty] | RDC
RDC_NB_2F_AHU8517 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | [7 empty] | RDC
RDC_NB_2F_AHU8518 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | [7 empty] | RDC
RDC_NB_2F_AHU8519 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | [7 empty] | RDC
RDC_NB_2F_AHU8520 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | [7 empty] | RDC
RDC_NB_2F_AHU8521 | AHU | Not Included | NORTH BUILDING PENT HOUSE N-2101 | [7 empty] | RDC
RDC_SB_2F_AHU8011 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | [7 empty] | RDC
RDC_SB_2F_AHU8012 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | [7 empty] | RDC
RDC_SB_2F_AHU8021 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | [7 empty] | RDC
RDC_SB_2F_AHU8022 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | [7 empty] | RDC
RDC_SB_2F_AHU8023 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | [7 empty] | RDC
RDC_SB_2F_AHU8024 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | [7 empty] | RDC
RDC_SB_2F_AHU8025 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | [7 empty] | RDC
RDC_SB_2F_AHU8026 | AHU | Not Included | SOUTH BUILDING PENTHOUSE S-2101 | [7 empty] | RDC
RDC_SB_GF_AHU8031 | AHU | Not Included | Mech S-0136 | [7 empty] | RDC
RDC_SB_GF_AHU8032 | AHU | Not Included | Mech S-0136 | [7 empty] | RDC
RDC_SB_GF_AHU8033 | AHU | Not Included | Mech S-0136 | [7 empty] | RDC
RDC_SB_GF_AHU8034 | AHU | Not Included | Mech S-0136 | [7 empty] | RDC
RDC_SB_GF_AHU8035 | AHU | Not Included | MECH S-0136 | [7 empty] | RDC
RDC_SB_GF_AHU8036 | AHU | Not Included | COMPUTER RESEARCH LAB S-1112 | [7 empty] | RDC
RDC_SB_GF_AHU8037 | AHU | Not Included | Cyber Server S-0138 | [7 empty] | RDC
RDC_SB_GF_AHU8041 | AHU | Not Included | UPS ROOM S-0145 | [7 empty] | RDC
RDC_SB_GF_AHU8042 | AHU | Not Included | Corridor S-0143 | [7 empty] | RDC
RDC_UB_AHU8601 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_AHU8602 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_AHU8603 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_AHU8604 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_AHU8605 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_AHU8606 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_AHU8607 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_AHU8608 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_AHU8609 | AHU | Not Included | UTILITY BUILDING MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_NB_GF_VAV4001 | VAV | Included | Store N-0201 | [7 empty] | RDC
RDC_NB_GF_VAV4005_EV4006 | EV | Not Included | Electrical N-0202 | [7 empty] | RDC
RDC_NB_GF_VAV4040 | VAV | Not Included | Air Quality High Bay N-0215A | [7 empty] | RDC
RDC_NB_GF_VAV4050_VEV4051 | VEV | Not Included | CSP High Bay N-0215B | [7 empty] | RDC
RDC_NB_GF_VAV4060_VEV4061 | VEV | Not Included | Machine Shop N-0215C | [7 empty] | RDC
RDC_NB_GF_VAV4070A_VEV4073A | VAV | Not Included | Open High Bay Lab N-0215D | [7 empty] | RDC
RDC_NB_GF_VAV4070B_VEV4073B | VAV | Not Included | Open High Bay Lab N-0215D | [7 empty] | RDC
RDC_NB_GF_VAV4071A_VEV4074A | VAV | Not Included | Open High Bay Lab N-0215D | [7 empty] | RDC
RDC_NB_GF_VAV4071B_VEV4074B | VAV | Not Included | Open High Bay Lab N-0215D | [7 empty] | RDC
RDC_NB_GF_VAV4072A_VEV4075A | VAV | Not Included | Open High Bay Lab N-0215D | [7 empty] | RDC
RDC_NB_GF_VAV4072B_VEV4075B | VAV | Not Included | Open High Bay Lab N-0215D | [7 empty] | RDC
RDC_NB_GF_VAV4080A_VEV4082A | VAV | Not Included | Desal High Bay Lab N-0215E | [7 empty] | RDC
RDC_NB_GF_VAV4080B_VEV4082B | VAV | Not Included | Desal High Bay Lab N-0215E | [7 empty] | RDC
RDC_NB_GF_VAV4081A_VEV4083A | VAV | Not Included | Desal High Bay Lab N-0215E | [7 empty] | RDC
RDC_NB_GF_VAV4081B_VEV4083B | VAV | Not Included | Desal High Bay Lab N-0215E | [7 empty] | RDC
RDC_NB_GF_VAV4090_VEV4091 | VEV | Not Included | Support Lab N-0215F | [7 empty] | RDC
RDC_NB_GF_VAV4100_EV4101 | EV | Not Included | Emergency Elec. Room N-0225 | [7 empty] | RDC
RDC_NB_GF_VAV4105_EV4106 | EV | Not Included | Normal Electrical Room N-0225 | [7 empty] | RDC
RDC_NB_GF_VAV4110_EV4111 | EV | Included | Conference Room N-0227 | [7 empty] | RDC
RDC_NB_GF_VAV4115_EV4116 | EV | Included | Office N-0228 | [7 empty] | RDC
RDC_NB_GF_VAV4120_EV4121 | EV | Included | Office N-0229 | [7 empty] | RDC
RDC_NB_GF_VAV4125_EV4126 | EV | Included | Office N-0230 | [7 empty] | RDC
RDC_NB_GF_VAV4130_EV4131 | EV | Included | Office N-0231 | [7 empty] | RDC
RDC_NB_GF_VAV4135_EV4136 | EV | Included | Office N-0232 | [7 empty] | RDC
RDC_NB_GF_VAV4140_EV4141 | EV | Included | Conference Room N-0233 | [7 empty] | RDC
RDC_NB_GF_VAV4145_EV4146 | EV | Included | Office N-0234 | [7 empty] | RDC
RDC_NB_GF_VAV4165_EV4166 | EV | Included | Office N-0236 | [7 empty] | RDC
RDC_NB_GF_VAV4180_VEV4181 | VEV | Not Included | Test Room N-0240A | [7 empty] | RDC
RDC_NB_GF_VAV4190_VEV4192 | VEV | Not Included | CSP Lab N-0240B | [7 empty] | RDC
RDC_NB_GF_VAV4191 | VAV | Not Included | CSP Lab N-0240B | [7 empty] | RDC
RDC_NB_GF_VAV4200_VEV4201 | VEV | Not Included | Test Room 1 N-0240C | [7 empty] | RDC
RDC_NB_GF_VAV4210 | VAV | Not Included | Desalination Lab N-0240D | [7 empty] | RDC
RDC_NB_GF_VAV4211 | VAV | Not Included | Desalination Lab N-0240D | [7 empty] | RDC
RDC_NB_GF_VAV4212 | VAV | Not Included | Desalination Lab N-0240D | [7 empty] | RDC
RDC_NB_GF_VAV4225 | VAV | Included | Office N-0247 | [7 empty] | RDC
RDC_NB_GF_VAV4230 | VAV | Included | Office N-0248 | [7 empty] | RDC
RDC_NB_GF_VAV4235 | VAV | Included | Office 05 -8WS- N-0250 | [7 empty] | RDC
RDC_NB_GF_VAV4240 | VAV | Included | Office 04 N-0251 | [7 empty] | RDC
RDC_NB_GF_VAV4245 | VAV | Included | Office N-0252 | [7 empty] | RDC
RDC_NB_GF_VAV4250 | VAV | Included | Office N-0253 | [7 empty] | RDC
RDC_NB_GF_VAV4255 | VAV | Included | Office N-0254 | [7 empty] | RDC
RDC_NB_GF_VAV4260 | VAV | Included | Office 05 -8WS- N-0255 | [7 empty] | RDC
RDC_NB_GF_VAV4265 | VAV | Included | Office N-0256 | [7 empty] | RDC
RDC_NB_GF_VAV4270 | VAV | Included | Office N-0257 | [7 empty] | RDC
RDC_NB_GF_VAV4275 | VAV | Included | Office N-0258 | [7 empty] | RDC
RDC_NB_GF_VAV4280 | VAV | Included | Office N-0259 | [7 empty] | RDC
RDC_NB_GF_VAV4285 | VAV | Included | Workstation N-0260 | [7 empty] | RDC
RDC_NB_GF_VAV4290 | VAV | Included | Office 04 N-0261 | [7 empty] | RDC
RDC_NB_GF_VAV4295 | VAV | Included | Office N-0262 | [7 empty] | RDC
RDC_NB_GF_VAV4300 | VAV | Included | Office N-0263 | [7 empty] | RDC
RDC_NB_GF_VAV4305 | VAV | Included | Office N-0264 | [7 empty] | RDC
RDC_NB_GF_VAV4310 | VAV | Included | Workstation N-0265 | [7 empty] | RDC
RDC_NB_GF_VAV4312 | VAV | Included | Breakout N-0265B | [7 empty] | RDC
RDC_NB_GF_VAV5000_EV5002 | EV | Included | Lobby North N-0101 | [7 empty] | RDC
RDC_NB_GF_VAV5001_EV5003 | EV | Included | Lobby North N-0101 | [7 empty] | RDC
RDC_NB_GF_VAV5010_EV5011 | EV | Included | Conf N-0106 | [7 empty] | RDC
RDC_NB_GF_VAV5015_EV5016 | EV | Included | Conference N-0107 | [7 empty] | RDC
RDC_NB_GF_VAV5025 | VAV | Included | Corridor N-0110 | [7 empty] | RDC
RDC_NB_GF_VAV5030_EV5031 | EV | Included | Confr Room N-0112 | [7 empty] | RDC
RDC_NB_GF_VAV5040_EV5041 | EV | Not Included | Normal Elec. N-0113 | [7 empty] | RDC
RDC_NB_GF_VAV5045_EV5046 | EV | Not Included | Emergency Elec. N-0114 | [7 empty] | RDC
RDC_NB_GF_VAV5050 | VAV | Not Included | Analytical Core Lab 1 N-0114A | [7 empty] | RDC
RDC_NB_GF_VAV5051 | VAV | Not Included | Analytical Core Lab 1 N-0114A | [7 empty] | RDC
RDC_NB_GF_VAV5054 | VAV | Not Included | Clean Lab N-0114B | [7 empty] | RDC
RDC_NB_GF_VAV5060_CEV5061 | CEV | Not Included | Clean Lab N-0114B | [7 empty] | RDC
RDC_NB_GF_VAV5070 | VAV | Not Included | Dirty Lab N-0114C | [7 empty] | RDC
RDC_NB_GF_VAV5080_VEV5081 | VEV | Not Included | Bio Analyt N-0114D | [7 empty] | RDC
RDC_NB_GF_VAV5090 | VAV | Not Included | Air Quality N-0114F | [7 empty] | RDC
RDC_NB_GF_VAV5091 | VAV | Not Included | Air Quality N-0114F | [7 empty] | RDC
RDC_NB_GF_VAV5100_EV5101 | EV | Included | Office N-0115 | [7 empty] | RDC
RDC_NB_GF_VAV5105 | VAV | Included | Office N-0116 | [7 empty] | RDC
RDC_NB_GF_VAV5110 | VAV | Included | Office N-0117 | [7 empty] | RDC
RDC_NB_GF_VAV5115 | VAV | Included | Office N-0118 | [7 empty] | RDC
RDC_NB_GF_VAV5120 | VAV | Included | Office N-0119 | [7 empty] | RDC
RDC_NB_GF_VAV5125 | VAV | Included | Office N-0120 | [7 empty] | RDC
RDC_NB_GF_VAV5130 | VAV | Included | Office N-0121 | [7 empty] | RDC
RDC_NB_GF_VAV5135 | VAV | Included | Office N-0122 | [7 empty] | RDC
RDC_NB_GF_VAV5140 | VAV | Included | Office N-0123 | [7 empty] | RDC
RDC_NB_GF_VAV5145 | VAV | Included | Office N-0124 | [7 empty] | RDC
RDC_NB_GF_VAV5150 | VAV | Included | Office N-0125 | [7 empty] | RDC
RDC_NB_GF_VAV5152 | VAV | Included | Office N-0126 | [7 empty] | RDC
RDC_NB_GF_VAV5155 | VAV | Included | Office N-0127 | [7 empty] | RDC
RDC_NB_GF_VAV5156 | VAV | Included | Office 04 N-0129 | [7 empty] | RDC
RDC_NB_GF_VAV5165_EV5166 | EV | Included | Serv Core N-0136 | [7 empty] | RDC
RDC_NB_GF_VAV5180 | VAV | Not Included | Analytical Core Lab 2 N-0140A | [7 empty] | RDC
RDC_NB_GF_VAV5181 | VAV | Not Included | Analytical Core Lab 2 N-0140A | [7 empty] | RDC
RDC_NB_GF_VAV5190 | VAV | Not Included | Furnace Room N-0140B | [7 empty] | RDC
RDC_NB_GF_VAV5200 | VAV | Not Included | Prep Lab N-0140C | [7 empty] | RDC
RDC_NB_GF_VAV5210 | VAV | Not Included | Sputter Room N-0140D | [7 empty] | RDC
RDC_NB_GF_VAV5220 | VAV | Not Included | MBE/Evap Room N-0140E | [7 empty] | RDC
RDC_NB_GF_VAV5230 | VAV | Not Included | ALD Room N-0140F | [7 empty] | RDC
RDC_NB_GF_VAV5250_VEV5251 | VEV | Included | Support Room N-0140H | [7 empty] | RDC
RDC_NB_GF_VAV5260_VEV5261 | VEV | Not Included | PLD Room N-0140J | [7 empty] | RDC
RDC_NB_GF_VAV5270A | VAV | Not Included | Organic Chemistry Lab N-0140K | [7 empty] | RDC
RDC_NB_GF_VAV5270B | VAV | Not Included | Org Chem N-0140K | [7 empty] | RDC
RDC_NB_GF_VAV5295_EV5296 | EV | Included | Conference Room N-0149 | [7 empty] | RDC
RDC_NB_GF_VAV5300 | VAV | Included | Corridor N-0150 | [7 empty] | RDC
RDC_NB_GF_VAV5305 | VAV | Included | Office N-0151 | [7 empty] | RDC
RDC_NB_GF_VAV5310 | VAV | Included | Office N-0152 | [7 empty] | RDC
RDC_NB_GF_VAV5315 | VAV | Included | Open Office N-0153 | [7 empty] | RDC
RDC_NB_GF_VAV5325 | VAV | Included | Office N-0155 | [7 empty] | RDC
RDC_NB_GF_VAV5330 | VAV | Included | Office N-0156 | [7 empty] | RDC
RDC_NB_GF_VAV5335 | VAV | Included | Office N-0157 | [7 empty] | RDC
RDC_NB_GF_VAV5340 | VAV | Included | Office N-0158 | [7 empty] | RDC
RDC_NB_GF_VAV5345 | VAV | Included | Office N-0159 | [7 empty] | RDC
RDC_NB_GF_VAV5355 | VAV | Included | Office N-0161 | [7 empty] | RDC
RDC_NB_GF_VAV5360 | VAV | Included | Office N-0162 | [7 empty] | RDC
RDC_NB_GF_VAV5365 | VAV | Included | Office N-0163 | [7 empty] | RDC
RDC_NB_GF_VAV5370 | VAV | Included | Office N-0164 | [7 empty] | RDC
RDC_NB_GF_VAV5380 | VAV | Included | Office N-0166 | [7 empty] | RDC
RDC_NB_GF_VAV5385 | VAV | Included | Office N-0167A | [7 empty] | RDC
RDC_NB_GF_VAV5390 | VAV | Included | Office 04 N-0168 | [7 empty] | RDC
RDC_NB_GF_VAV5395 | VAV | Included | Exp. Office N-0169 | [7 empty] | RDC
RDC_NB_GF_VAV5400 | VAV | Included | Reception Area N-0170 | [7 empty] | RDC
RDC_NB_GF_VAV5405 | VAV | Included | Exp. Office N-0172 | [7 empty] | RDC
RDC_NB_GF_VAV5410_EV5411 | EV | Included | Conf Room N-0173 | [7 empty] | RDC
RDC_NB_GF_VAV5415 | VAV | Included | Office 04 N-0174 | [7 empty] | RDC
RDC_NB_GF_VAV6000_EV6001 | EV | Included | Conf Room N-0301 | [7 empty] | RDC
RDC_NB_GF_VAV6010_EV6011 | EV | Included | Conf N-0304 | [7 empty] | RDC
RDC_NB_GF_VAV6025_EV6026 | EV | Not Included | Normal Elec. N-0310 | [7 empty] | RDC
RDC_NB_GF_VAV6130_EV6131 | EV | Included | Store N-0315 | [7 empty] | RDC
RDC_NB_GF_VAV6135 | VAV | Included | Store N-0316 | [7 empty] | RDC
RDC_NB_GF_VAV6140 | VAV | Included | Workstation N-0317 | [7 empty] | RDC
RDC_NB_GF_VAV6145 | VAV | Included | Office N-0318 | [7 empty] | RDC
RDC_NB_GF_VAV6150 | VAV | Included | Office N-0319 | [7 empty] | RDC
RDC_NB_GF_VAV6155 | VAV | Included | Workstation N-0320 | [7 empty] | RDC
RDC_NB_GF_VAV6160 | VAV | Included | Office N-0321 | [7 empty] | RDC
RDC_NB_GF_VAV6170 | VAV | Included | Office N-0323 | [7 empty] | RDC
RDC_NB_GF_VAV6175 | VAV | Included | Workstation N-0324 | [7 empty] | RDC
RDC_NB_GF_VAV6180 | VAV | Included | Office N-0325 | [7 empty] | RDC
RDC_NB_GF_VAV6185_EV6186 | EV | Included | Office N-0326 | [7 empty] | RDC
RDC_NB_GF_VAV6190_EV6191 | EV | Not Included | Normal Elec. N-0328 | [7 empty] | RDC
RDC_NB_GF_VAV6195 | VAV | Included | Store N-0329 | [7 empty] | RDC
RDC_NB_GF_VAV6200_EV6201 | EV | Included | Conf N-0330 | [7 empty] | RDC
RDC_NB_GF_VAV6205_EV6206 | EV | Included | Conf N-0331 | [7 empty] | RDC
RDC_NB_GF_VAV6210 | VAV | Included | Corr. +N-033B N-0332C | [7 empty] | RDC
RDC_NB_GF_VAV6220_EV6221 | EV | Not Included | Emergency Elec. N-0333 | [7 empty] | RDC
RDC_NB_GF_VAV6240_EV6241 | EV | Not Included | Emergency Electrical N-0350A | [7 empty] | RDC
RDC_NB_GF_VAV6285_EV6286 | EV | Included | Conf N-0358 | [7 empty] | RDC
RDC_NB_GF_VAV6295_EV6296 | EV | Included | Conference N-0360 | [7 empty] | RDC
RDC_NB_GF_VAV6300 | VAV | Included | Store N-0362B | [7 empty] | RDC
RDC_NB_GF_VAV6305 | VAV | Included | Office N-0363 | [7 empty] | RDC
RDC_NB_GF_VAV6310 | VAV | Included | Office N-0364 | [7 empty] | RDC
RDC_NB_GF_VAV6315_EV6316 | EV | Included | Conf Room N-0364A | [7 empty] | RDC
RDC_NB_GF_VAV6320 | VAV | Included | Corridor N-0365 | [7 empty] | RDC
RDC_NB_GF_VAV6325 | VAV | Included | Office N-0366 | [7 empty] | RDC
RDC_NB_GF_VAV6330 | VAV | Included | Office 04 N-0367 | [7 empty] | RDC
RDC_NB_GF_VAV6335 | VAV | Included | Office N-0368 | [7 empty] | RDC
RDC_NB_GF_VAV6340 | VAV | Included | Office N-0369 | [7 empty] | RDC
RDC_NB_GF_VAV6345 | VAV | Included | Office N-0370 | [7 empty] | RDC
RDC_NB_GF_VAV6350 | VAV | Included | Office N-0371 | [7 empty] | RDC
RDC_NB_GF_VAV6355 | VAV | Included | Workstation N-0372 | [7 empty] | RDC
RDC_NB_GF_VAV6360 | VAV | Included | Office N-0374 | [7 empty] | RDC
RDC_NB_GF_VAV6365 | VAV | Included | Office N-0375 | [7 empty] | RDC
RDC_NB_GF_VAV6370 | VAV | Included | Office N-0376 | [7 empty] | RDC
RDC_NB_GF_VAV6375 | VAV | Included | Office N-0377 | [7 empty] | RDC
RDC_NB_GF_VAV6380 | VAV | Included | Workstation N-0378 | [7 empty] | RDC
RDC_NB_GF_VAV6390 | VAV | Included | Office N-0379 | [7 empty] | RDC
RDC_NB_GF_VAV6395 | VAV | Included | Office N-0380 | [7 empty] | RDC
RDC_NB_GF_VAV6400 | VAV | Included | Workstation N-0381 | [7 empty] | RDC
RDC_NB_GF_VAV6405 | VAV | Included | Office N-0382 | [7 empty] | RDC
RDC_NB_GF_VAV6410 | VAV | Included | Office N-0383 | [7 empty] | RDC
RDC_NB_GF_VAV7000 | VAV | Included | Vestibule Staging N-0401 | [7 empty] | RDC
RDC_NB_GF_VAV7020A | VAV | Not Included | NMR Lab N-0404A | [7 empty] | RDC
RDC_NB_GF_VAV7020B | VAV | Not Included | NMR Lab N-0404A | [7 empty] | RDC
RDC_NB_GF_VAV7021A | VAV | Not Included | NMR Lab N-0404A | [7 empty] | RDC
RDC_NB_GF_VAV7021B | VAV | Not Included | NMR Lab N-0404A | [7 empty] | RDC
RDC_NB_GF_VAV7030_VEV7031 | VEV | Not Included | CONTROL ROOM N-0404B | [7 empty] | RDC
RDC_NB_GF_VAV7040 | VAV | Not Included | Service Equipm. Room N-0404C | [7 empty] | RDC
RDC_NB_GF_VAV7050_VEV7051 | VEV | Not Included | EM Prep 1 - MAT N-0404D | [7 empty] | RDC
RDC_NB_GF_VAV7060_VEV7061 | VEV | Not Included | EM Prep 2 - BIO N-0404E | [7 empty] | RDC
RDC_NB_GF_VAV7070A | VAV | Not Included | Surf Analysis Lab N-0404F | [7 empty] | RDC
RDC_NB_GF_VAV7070B | VAV | Not Included | Surf Analysis Lab N-0404F | [7 empty] | RDC
RDC_NB_GF_VAV7071A | VAV | Not Included | Surf Analysis Lab N-0404F | [7 empty] | RDC
RDC_NB_GF_VAV7071B | VAV | Not Included | Surf Analysis Lab N-0404F | [7 empty] | RDC
RDC_NB_GF_VAV7080 | VAV | Included | Exp. Office N-0410 | [7 empty] | RDC
RDC_NB_GF_VAV7085 | VAV | Included | Office N-0411 | [7 empty] | RDC
RDC_NB_GF_VAV7090 | VAV | Included | Office N-0412 | [7 empty] | RDC
RDC_NB_GF_VAV7095 | VAV | Included | Office N-0413 | [7 empty] | RDC
RDC_NB_GF_VAV7100 | VAV | Included | Office N-0414 | [7 empty] | RDC
RDC_NB_GF_VAV7105 | VAV | Included | Office N-0415 | [7 empty] | RDC
RDC_NB_GF_VAV7110 | VAV | Included | Office N-0416 | [7 empty] | RDC
RDC_NB_GF_VAV7115 | VAV | Included | Office N-0417 | [7 empty] | RDC
RDC_NB_GF_VAV7120 | VAV | Included | Office N-0418 | [7 empty] | RDC
RDC_NB_GF_VAV7125_EV7126 | EV | Not Included | Normal Elec. Room N-0420 | [7 empty] | RDC
RDC_NB_GF_VAV7130 | VAV | Included | Office N-0421 | [7 empty] | RDC
RDC_NB_GF_VAV7135 | VAV | Included | Office N-0422 | [7 empty] | RDC
RDC_NB_GF_VAV7140_EV7141 | EV | Included | Conference N-0423 | [7 empty] | RDC
RDC_NB_GF_VAV7145 | VAV | Included | Office N-0425 | [7 empty] | RDC
RDC_NB_GF_VAV7155 | VAV | Included | Office N-0427 | [7 empty] | RDC
RDC_NB_GF_VAV7165 | VAV | Included | Office N-0429 | [7 empty] | RDC
RDC_NB_GF_VAV7175 | VAV | Included | Corridor N-0432 | [7 empty] | RDC
RDC_NB_GF_VAV7176 | VAV | Included | Office 05-15-WS N-0431 | [7 empty] | RDC
RDC_NB_GF_VAV7180 | VAV | Included | Corridor N-0432 | [7 empty] | RDC
RDC_NB_GF_VAV7185_EV7186 | EV | Not Included | Emer. Elec. Room N-0433 | [7 empty] | RDC
RDC_NB_GF_VAV7195 | VAV | Included | Office 04 N-0436 | [7 empty] | RDC
RDC_NB_GF_VAV7205 | VAV | Included | Office 04 N-0438 | [7 empty] | RDC
RDC_NB_GF_VAV7215_EV7216 | EV | Included | Conference Room N-0440 | [7 empty] | RDC
RDC_NB_GF_VAV7220_CEV7221 | CEV | Included | Service Corridor N-0441 | [7 empty] | RDC
RDC_NB_GF_VAV7230_VEV7231 | VEV | Not Included | Inter Lab N-0442A | [7 empty] | RDC
RDC_NB_GF_VAV7240_VEV7241A | VAV | Not Included | Optical Lab N-0442B | [7 empty] | RDC
RDC_NB_GF_VAV7250_VEV7251 | VEV | Included | CONF N-0442C | [7 empty] | RDC
RDC_NB_GF_VAV7260_VEV7261 | VEV | Not Included | SEM 1 Room N-0442D | [7 empty] | RDC
RDC_NB_GF_VAV7270_VEV7271 | VEV | Not Included | SERV 1 N-0442E | [7 empty] | RDC
RDC_NB_GF_VAV7280_VEV7281 | VEV | Not Included | Confocal 2 Room N-0442F | [7 empty] | RDC
RDC_NB_GF_VAV7290_VEV7291 | VEV | Not Included | SEM 2 N-0442G | [7 empty] | RDC
RDC_NB_GF_VAV7300 | VAV | Not Included | Air Lock 1 N-0442H | [7 empty] | RDC
RDC_NB_GF_VAV7310_VEV7311 | VEV | Not Included | SEM 3 N-0442J | [7 empty] | RDC
RDC_NB_GF_VAV7320_VEV7321 | VEV | Not Included | SEM 4 N-0442K | [7 empty] | RDC
RDC_NB_GF_VAV7330_VEV7331 | VEV | Not Included | SEM 5 N-0442L | [7 empty] | RDC
RDC_NB_GF_VAV7340_VEV7341 | VEV | Not Included | SERV 2 N-0442M | [7 empty] | RDC
RDC_NB_GF_VAV7350_VEV7351 | VEV | Not Included | SEM Lab N-0442N | [7 empty] | RDC
RDC_NB_GF_VAV7360_VEV7361 | VEV | Not Included | SEM Lab N-0442p | [7 empty] | RDC
RDC_NB_GF_VAV7370_VEV7371 | VEV | Not Included | A/L 2 N-0442R | [7 empty] | RDC
RDC_NB_GF_VAV7385 | VAV | Included | Office N-0444 | [7 empty] | RDC
RDC_NB_GF_VAV7390 | VAV | Included | Office 04 N-0445 | [7 empty] | RDC
RDC_NB_GF_VAV7395 | VAV | Included | Workstation N-0446 | [7 empty] | RDC
RDC_NB_GF_VAV7400 | VAV | Included | Office N-0447 | [7 empty] | RDC
RDC_NB_GF_VAV7405 | VAV | Included | Office N-0448 | [7 empty] | RDC
RDC_NB_GF_VAV7410 | VAV | Included | Office N-0449 | [7 empty] | RDC
RDC_NB_GF_VAV7415 | VAV | Included | Office N-0450 | [7 empty] | RDC
RDC_NB_GF_VAV7425 | VAV | Included | Office 05-8-WKS N-0452 | [7 empty] | RDC
RDC_NB_GF_VAV7430 | VAV | Included | Office N-0453 | [7 empty] | RDC
RDC_NB_GF_VAV7435 | VAV | Included | Office N-0454 | [7 empty] | RDC
RDC_NB_GF_VAV7440 | VAV | Included | Office N-0455 | [7 empty] | RDC
RDC_NB_GF_VAV7445 | VAV | Included | Office 04 N-0456 | [7 empty] | RDC
RDC_NB_GF_VAV7460 | VAV | Included | Workstation N-0457 | [7 empty] | RDC
RDC_NB_GF_VAV7465 | VAV | Included | Office N-0458 | [7 empty] | RDC
RDC_NB_GF_VAV7470 | VAV | Included | Office N-0459 | [7 empty] | RDC
RDC_NB_GF_VAV7475 | VAV | Included | Office N-0460 | [7 empty] | RDC
RDC_NB_GF_VAV7480 | VAV | Included | Office N-0461 | [7 empty] | RDC
RDC_NB_GF_VAV7485 | VAV | Included | Office 05-8-WKS N-0462 | [7 empty] | RDC
RDC_NB_GF_VAV7490_EV7495 | EV | Included | Confer N-0463 | [7 empty] | RDC
RDC_NB_GF_VAV7496 | VAV | Included | Office 04 N-0464 | [7 empty] | RDC
RDC_NB_GF_VAV7498 | VAV | Included | Office N-0465 | [7 empty] | RDC
RDC_NB_GF_VAV7499 | VAV | Included | Office 04 N-0466 | [7 empty] | RDC
RDC_SB_1F_VAV0506 | VAV | Included | Conf. S-1110 | [7 empty] | RDC
RDC_SB_1F_VAV0507 | VAV | Not Included | Computer Research Lab-4 S-1112 | [7 empty] | RDC
RDC_SB_1F_VAV0508 | VAV | Included | Conf S-1113 | [7 empty] | RDC
RDC_SB_1F_VAV0509 | VAV | Included | NCIR Office S-1115 | [7 empty] | RDC
RDC_SB_1F_VAV0510 | VAV | Included | Workstation S-1115A | [7 empty] | RDC
RDC_SB_1F_VAV0511 | VAV | Included | NCIR Office S-1116 | [7 empty] | RDC
RDC_SB_1F_VAV0512 | VAV | Included | NCIR Office S-1117 | [7 empty] | RDC
RDC_SB_1F_VAV0513 | VAV | Included | NCIR Office S-1118 | [7 empty] | RDC
RDC_SB_1F_VAV0514 | VAV | Included | Sc.Comp.Office3 S-1119 | [7 empty] | RDC
RDC_SB_1F_VAV0518 | VAV | Included | Office S-1161 | [7 empty] | RDC
RDC_SB_1F_VAV0519 | VAV | Included | Office S-1162 | [7 empty] | RDC
RDC_SB_1F_VAV0520 | VAV | Included | Office S-1163 | [7 empty] | RDC
RDC_SB_1F_VAV0521 | VAV | Included | Office S-1164 | [7 empty] | RDC
RDC_SB_1F_VAV0522 | VAV | Included | Office S-1165 | [7 empty] | RDC
RDC_SB_1F_VAV0523 | VAV | Included | Office S-1166 | [7 empty] | RDC
RDC_SB_1F_VAV0526 | VAV | Included | Office S-1171 | [7 empty] | RDC
RDC_SB_1F_VAV0527 | VAV | Included | Office S-1172 | [7 empty] | RDC
RDC_SB_1F_VAV0528 | VAV | Included | Office S-1173 | [7 empty] | RDC
RDC_SB_1F_VAV0529 | VAV | Included | Corridor S-1174 | [7 empty] | RDC
RDC_SB_1F_VAV0530 | VAV | Included | Situation Room S-1175 | [7 empty] | RDC
RDC_SB_1F_VAV0531 | VAV | Not Included | Immersive Viz Lab S-1176 | [7 empty] | RDC
RDC_SB_1F_VAV0532 | VAV | Included | Conference Room S-1177 | [7 empty] | RDC
RDC_SB_1F_VAV0533 | VAV | Included | Telepresence S-1179 | [7 empty] | RDC
RDC_SB_1F_VAV0538 | VAV | Included | Workstation S-1151A | [7 empty] | RDC
RDC_SB_1F_VAV1501 | VAV | Included | Workstation S-1119A | [7 empty] | RDC
RDC_SB_1F_VAV1502 | VAV | Included | NCIR Office S-1120 | [7 empty] | RDC
RDC_SB_1F_VAV1503 | VAV | Included | NCIR Office S-1121 | [7 empty] | RDC
RDC_SB_1F_VAV1505 | VAV | Included | SC. Comp Office 2 S-1123 | [7 empty] | RDC
RDC_SB_1F_VAV1506 | VAV | Included | SC. Comp Office 3 S-1124 | [7 empty] | RDC
RDC_SB_1F_VAV1507 | VAV | Included | Workstation S-1124A | [7 empty] | RDC
RDC_SB_1F_VAV1508 | VAV | Included | Scientific Comp. Office 1 S-1125 | [7 empty] | RDC
RDC_SB_1F_VAV1509 | VAV | Included | Scientific Comp. Office S-1126 | [7 empty] | RDC
RDC_SB_1F_VAV1510 | VAV | Included | ALT Office 2 S-1127 | [7 empty] | RDC
RDC_SB_1F_VAV1511 | VAV | Included | ALT Office 3 S-1128 | [7 empty] | RDC
RDC_SB_1F_VAV1512 | VAV | Included | Workstation S-1128A | [7 empty] | RDC
RDC_SB_1F_VAV1513 | VAV | Included | ALT Office 1 S-1129 | [7 empty] | RDC
RDC_SB_1F_VAV1514 | VAV | Included | ALT Office S-1130 | [7 empty] | RDC
RDC_SB_1F_VAV1515 | VAV | Included | Distub. Syst Office 1 S-1131 | [7 empty] | RDC
RDC_SB_1F_VAV1516 | VAV | Included | Distub. Syst Office S-1132 | [7 empty] | RDC
RDC_SB_1F_VAV1517 | VAV | Included | Workstation S-1132A | [7 empty] | RDC
RDC_SB_1F_VAV1518 | VAV | Included | Distub. Syst Office S-1133 | [7 empty] | RDC
RDC_SB_1F_VAV1519 | VAV | Included | Distub. Syst Office S-1134 | [7 empty] | RDC
RDC_SB_1F_VAV1520 | VAV | Not Included | Data Analytic Office S-1135 | [7 empty] | RDC
RDC_SB_1F_VAV1521 | VAV | Not Included | Data Analytic Office S-1136 | [7 empty] | RDC
RDC_SB_1F_VAV1522 | VAV | Included | Workstation S-1136A | [7 empty] | RDC
RDC_SB_1F_VAV1523 | VAV | Not Included | Data Analytic Office S-1137 | [7 empty] | RDC
RDC_SB_1F_VAV1524 | VAV | Not Included | Data Analytic Office S-1138 | [7 empty] | RDC
RDC_SB_1F_VAV1525 | VAV | Included | Office S-1139 | [7 empty] | RDC
RDC_SB_1F_VAV1526 | VAV | Included | Office S-1140 | [7 empty] | RDC
RDC_SB_1F_VAV1527 | VAV | Included | Conference Room S-1141 | [7 empty] | RDC
RDC_SB_1F_VAV1528 | VAV | Included | Office S-1142 | [7 empty] | RDC
RDC_SB_1F_VAV1529 | VAV | Included | Office S-1144 | [7 empty] | RDC
RDC_SB_1F_VAV1530 | VAV | Included | Office S-1145 | [7 empty] | RDC
RDC_SB_1F_VAV1531 | VAV | Included | Office S-1146 | [7 empty] | RDC
RDC_SB_1F_VAV1532 | VAV | Included | Workstation S-1146A | [7 empty] | RDC
RDC_SB_1F_VAV1533 | VAV | Included | Office S-1148 | [7 empty] | RDC
RDC_SB_1F_VAV1534 | VAV | Included | Office S-1149 | [7 empty] | RDC
RDC_SB_1F_VAV1536 | VAV | Included | Office S-1150 | [7 empty] | RDC
RDC_SB_1F_VAV1539 | VAV | Included | Video Conf. Room S-1154 | [7 empty] | RDC
RDC_SB_1F_VAV1540 | VAV | Included | Conf S-1159 | [7 empty] | RDC
RDC_SB_1F_VAV1542 | VAV | Included | Office S-1182 | [7 empty] | RDC
RDC_SB_1F_VAV1543 | VAV | Included | Workstation S-1182A | [7 empty] | RDC
RDC_SB_1F_VAV1544 | VAV | Included | Office S-1182C | [7 empty] | RDC
RDC_SB_1F_VAV1545 | VAV | Included | Office S-1182D | [7 empty] | RDC
RDC_SB_1F_VAV1546 | VAV | Included | Office S-1182E | [7 empty] | RDC
RDC_SB_1F_VAV1547 | VAV | Included | Office S-1182F | [7 empty] | RDC
RDC_SB_1F_VAV1548 | VAV | Included | Office S-1183 | [7 empty] | RDC
RDC_SB_1F_VAV1549 | VAV | Included | Workstation S-1183A | [7 empty] | RDC
RDC_SB_1F_VAV1550 | VAV | Included | Office S-1184 | [7 empty] | RDC
RDC_SB_1F_VAV1551 | VAV | Included | Social Comp Office S-1185 | [7 empty] | RDC
RDC_SB_1F_VAV1552 | VAV | Included | Social Comp Office S-1186 | [7 empty] | RDC
RDC_SB_1F_VAV1553 | VAV | Included | Workstation S-1186A | [7 empty] | RDC
RDC_SB_1F_VAV1554 | VAV | Included | Social Comp Office S-1187 | [7 empty] | RDC
RDC_SB_1F_VAV1555 | VAV | Included | Social Comp Office S-1188 | [7 empty] | RDC
RDC_SB_1F_VAV1556 | VAV | Included | Cyber Sec Office S-1189 | [7 empty] | RDC
RDC_SB_1F_VAV1557 | VAV | Included | Cyber Sec Office S-1190 | [7 empty] | RDC
RDC_SB_1F_VAV1558 | VAV | Included | Workstation S-1190A | [7 empty] | RDC
RDC_SB_1F_VAV1559 | VAV | Included | Office S-1191 | [7 empty] | RDC
RDC_SB_1F_VAV1560 | VAV | Included | Cyber Sec Office S-1192 | [7 empty] | RDC
RDC_SB_1F_VAV1561 | VAV | Included | Cyber Sec Office S-1193 | [7 empty] | RDC
RDC_SB_1F_VAV2501 | VAV | Included | Lobby S-1201 | [7 empty] | RDC
RDC_SB_1F_VAV2502 | VAV | Included | Lobby S-1202 | [7 empty] | RDC
RDC_SB_1F_VAV2503 | VAV | Included | Lobby S-1202 | [7 empty] | RDC
RDC_SB_1F_VAV2504 | VAV | Included | Lobby S-1202 | [7 empty] | RDC
RDC_SB_1F_VAV2505 | VAV | Included | Lobby S-1202 | [7 empty] | RDC
RDC_SB_1F_VAV2506 | VAV | Included | Lobby S-1202 | [7 empty] | RDC
RDC_SB_1F_VAV2508 | VAV | Included | Female Prayer S-1207 | [7 empty] | RDC
RDC_SB_1F_VAV2509 | VAV | Included | Open Plan S-1210 | [7 empty] | RDC
RDC_SB_1F_VAV2510 | VAV | Not Included | Exc. Dir. Office S-1211 | [7 empty] | RDC
RDC_SB_1F_VAV2511 | VAV | Included | Office S-1212 | [7 empty] | RDC
RDC_SB_1F_VAV2512 | VAV | Included | Office S-1213 | [7 empty] | RDC
RDC_SB_1F_VAV2513 | VAV | Included | Office S-1214 | [7 empty] | RDC
RDC_SB_1F_VAV2514 | VAV | Included | Office S-1215 | [7 empty] | RDC
RDC_SB_1F_VAV2515 | VAV | Included | Office S-1216 | [7 empty] | RDC
RDC_SB_1F_VAV2516 | VAV | Not Included | Executive Director Office S-1217 | [7 empty] | RDC
RDC_SB_1F_VAV2517 | VAV | Not Included | Executive Director Office S-1218 | [7 empty] | RDC
RDC_SB_1F_VAV2518 | VAV | Included | Office S-1219 | [7 empty] | RDC
RDC_SB_1F_VAV2519 | VAV | Included | Office S-1220 | [7 empty] | RDC
RDC_SB_1F_VAV2520 | VAV | Included | Office S-1221 | [7 empty] | RDC
RDC_SB_1F_VAV2521 | VAV | Included | Office S-1222 | [7 empty] | RDC
RDC_SB_1F_VAV2522 | VAV | Included | Office S-1223 | [7 empty] | RDC
RDC_SB_1F_VAV2523 | VAV | Included | Office S-1224 | [7 empty] | RDC
RDC_SB_1F_VAV2524 | VAV | Included | Office S-1225 | [7 empty] | RDC
RDC_SB_1F_VAV2525 | VAV | Included | Office S-1226 | [7 empty] | RDC
RDC_SB_1F_VAV2526 | VAV | Included | Open Plan S-1227 | [7 empty] | RDC
RDC_SB_1F_VAV2527 | VAV | Not Included | Director Office S-1228 | [7 empty] | RDC
RDC_SB_1F_VAV2528 | VAV | Not Included | Director Office S-1230 | [7 empty] | RDC
RDC_SB_1F_VAV2529 | VAV | Included | Office S-1231 | [7 empty] | RDC
RDC_SB_1F_VAV2530 | VAV | Included | Office S-1232 | [7 empty] | RDC
RDC_SB_1F_VAV2531 | VAV | Not Included | Director Office S-1241 | [7 empty] | RDC
RDC_SB_1F_VAV2532 | VAV | Included | Office S-1242 | [7 empty] | RDC
RDC_SB_1F_VAV2533 | VAV | Included | Cooridor S-1246 | [7 empty] | RDC
RDC_SB_1F_VAV2534 | VAV | Included | Meeting Room S-1247 | [7 empty] | RDC
RDC_SB_1F_VAV2535 | VAV | Included | Store S-1248 | [7 empty] | RDC
RDC_SB_1F_VAV2536 | VAV | Not Included | Mech. Chasing S-1249 | [7 empty] | RDC
RDC_SB_1F_VAV2538 | VAV | Included | Office S-1257 | [7 empty] | RDC
RDC_SB_1F_VAV2539 | VAV | Included | Office S-1257B | [7 empty] | RDC
RDC_SB_1F_VAV2540 | VAV | Not Included | Executive Director S-1260 | [7 empty] | RDC
RDC_SB_1F_VAV2541 | VAV | Included | Assistant S-1261 | [7 empty] | RDC
RDC_SB_1F_VAV2542 | VAV | Included | Open Plan S-1263 | [7 empty] | RDC
RDC_SB_1F_VAV2543 | VAV | Included | Office S-1264 | [7 empty] | RDC
RDC_SB_1F_VAV2544 | VAV | Included | Office S-1265 | [7 empty] | RDC
RDC_SB_1F_VAV2545 | VAV | Included | Office S-1266 | [7 empty] | RDC
RDC_SB_1F_VAV2546 | VAV | Included | Office S-1267 | [7 empty] | RDC
RDC_SB_1F_VAV2547 | VAV | Included | Office S-1268 | [7 empty] | RDC
RDC_SB_1F_VAV2548 | VAV | Included | Office S-1269 | [7 empty] | RDC
RDC_SB_1F_VAV2549 | VAV | Included | Office S-1270 | [7 empty] | RDC
RDC_SB_1F_VAV2550 | VAV | Included | Office S-1271 | [7 empty] | RDC
RDC_SB_1F_VAV2551 | VAV | Included | Meeting Room S-1272 | [7 empty] | RDC
RDC_SB_1F_VAV2552 | VAV | Included | FPC S-1277 | [7 empty] | RDC
RDC_SB_1F_VAV2553 | VAV | Included | Male Prayer S-1278 | [7 empty] | RDC
RDC_SB_1F_VAV3504 | VAV | Included | Open Plan S-1229 | [7 empty] | RDC
RDC_SB_1F_VAV3505 | VAV | Included | Open Plan S-1229 | [7 empty] | RDC
RDC_SB_1F_VAV3506 | VAV | Included | Office S-1233 | [7 empty] | RDC
RDC_SB_1F_VAV3507 | VAV | Included | Office S-1234 | [7 empty] | RDC
RDC_SB_1F_VAV3508 | VAV | Included | Office S-1235 | [7 empty] | RDC
RDC_SB_1F_VAV3509 | VAV | Not Included | Policy Director Office S-1237 | [7 empty] | RDC
RDC_SB_1F_VAV3510 | VAV | Not Included | Policy Executive Director Office S-1240 | [7 empty] | RDC
RDC_SB_1F_VAV3511 | VAV | Included | Corridor S-1280 | [7 empty] | RDC
RDC_SB_1F_VAV3512 | VAV | Included | Pantry S-1282 | [7 empty] | RDC
RDC_SB_1F_VAV3513 | VAV | Included | Office S-1283 | [7 empty] | RDC
RDC_SB_1F_VAV3514 | VAV | Included | Office S-1284 | [7 empty] | RDC
RDC_SB_1F_VAV3515 | VAV | Not Included | S-1285 VP R&D | [7 empty] | RDC
RDC_SB_1F_VAV3516 | VAV | Included | Meeting Room S-1288 | [7 empty] | RDC
RDC_SB_1F_VAV3517 | VAV | Included | Dressing Room S-1290 | [7 empty] | RDC
RDC_SB_1F_VAV3518 | VAV | Included | Waiting Area S-1292 | [7 empty] | RDC
RDC_SB_1F_VAV3519 | VAV | Included | Open Plan S-1293 | [7 empty] | RDC
RDC_SB_1F_VAV3520 | VAV | Included | Office S-1294 | [7 empty] | RDC
RDC_SB_1F_VAV3521 | VAV | Included | Office S-1295 | [7 empty] | RDC
RDC_SB_1F_VAV3522 | VAV | Included | Conference Room S-1296 | [7 empty] | RDC
RDC_SB_1F_VAV3523 | VAV | Included | Office S-1299 | [7 empty] | RDC
RDC_SB_1F_VAV3524 | VAV | Not Included | Normal Elec. S-1238 | [7 empty] | RDC
RDC_SB_GF_VAV0001 | VAV | Included | Vestibule S-0101 | [7 empty] | RDC
RDC_SB_GF_VAV0002 | VAV | Included | Main Lobby S-0102 | [7 empty] | RDC
RDC_SB_GF_VAV0003 | VAV | Included | Entrance Lobby S-0102 | [7 empty] | RDC
RDC_SB_GF_VAV0007 | VAV | Included | Conference S-0109 | [7 empty] | RDC
RDC_SB_GF_VAV0008 | VAV | Not Included | Computer Research Lab 3 S-0110 | [7 empty] | RDC
RDC_SB_GF_VAV0009 | VAV | Included | Phone Booth S-0111 | [7 empty] | RDC
RDC_SB_GF_VAV0010 | VAV | Included | Phone Booth S-0112 | [7 empty] | RDC
RDC_SB_GF_VAV0011 | VAV | Included | Conference S-0113 | [7 empty] | RDC
RDC_SB_GF_VAV0012 | VAV | Not Included | Computer Research Lab 2 S-0114 | [7 empty] | RDC
RDC_SB_GF_VAV0013 | VAV | Included | Phone Booth S-0115 | [7 empty] | RDC
RDC_SB_GF_VAV0014 | VAV | Included | Phone Booth S-0116 | [7 empty] | RDC
RDC_SB_GF_VAV0016 | VAV | Included | Conference S-0118 | [7 empty] | RDC
RDC_SB_GF_VAV0017 | VAV | Not Included | Computer Research Lab 1 S-0119 | [7 empty] | RDC
RDC_SB_GF_VAV0018 | VAV | Included | Restaurant S-0123 | [7 empty] | RDC
RDC_SB_GF_VAV0019 | VAV | Included | Restaurant S-0123 | [7 empty] | RDC
RDC_SB_GF_VAV0025 | VAV | Included | Alt Recording Sound S-0135 | [7 empty] | RDC
RDC_SB_GF_VAV1003_VEV1002 | VEV | Not Included | NOC Lab S-0140A | [7 empty] | RDC
RDC_SB_GF_VAV1004 | VAV | Included | Dedicated Cyber SOC/NOC Lab S-0141 | [7 empty] | RDC
RDC_SB_GF_VAV1008 | VAV | Included | Cyber Embedded Sys. S-0146 | [7 empty] | RDC
RDC_SB_GF_VAV2002 | VAV | Included | Conference Room S-0207 | [7 empty] | RDC
RDC_SB_GF_VAV2003 | VAV | Included | Multi Purpose Hall S-0208 | [7 empty] | RDC
RDC_SB_GF_VAV2004 | VAV | Included | Multi Purpose Hall S-0208 | [7 empty] | RDC
RDC_SB_GF_VAV2005 | VAV | Included | Technical Open Plan S-0211 | [7 empty] | RDC
RDC_SB_GF_VAV2006 | VAV | Included | Meeting Room S-0212 | [7 empty] | RDC
RDC_SB_GF_VAV2007 | VAV | Included | Office S-0213 | [7 empty] | RDC
RDC_SB_GF_VAV2008 | VAV | Included | Office S-0214 | [7 empty] | RDC
RDC_SB_GF_VAV2009 | VAV | Included | Office S-0215 | [7 empty] | RDC
RDC_SB_GF_VAV2010 | VAV | Included | Office S-0216 | [7 empty] | RDC
RDC_SB_GF_VAV2011 | VAV | Included | Office S-0217 | [7 empty] | RDC
RDC_SB_GF_VAV2012 | VAV | Not Included | Director Office S-0218 | [7 empty] | RDC
RDC_SB_GF_VAV2013 | VAV | Included | Office S-0219 | [7 empty] | RDC
RDC_SB_GF_VAV2014 | VAV | Included | Office S-0220 | [7 empty] | RDC
RDC_SB_GF_VAV2015 | VAV | Not Included | Director Office S-0221 | [7 empty] | RDC
RDC_SB_GF_VAV2016 | VAV | Not Included | Director Office S-0222 | [7 empty] | RDC
RDC_SB_GF_VAV2017 | VAV | Included | Meeting Room S-0223 | [7 empty] | RDC
RDC_SB_GF_VAV2018 | VAV | Included | Print Hub S-0225 | [7 empty] | RDC
RDC_SB_GF_VAV2019 | VAV | Included | Office S-0227 | [7 empty] | RDC
RDC_SB_GF_VAV2020 | VAV | Included | Informal Meeting S-0231 | [7 empty] | RDC
RDC_SB_GF_VAV2021 | VAV | Included | Open Plan S-0228 | [7 empty] | RDC
RDC_SB_GF_VAV2022 | VAV | Not Included | Director Office S-0229 | [7 empty] | RDC
RDC_SB_GF_VAV2023 | VAV | Included | Office S-0230 | [7 empty] | RDC
RDC_SB_GF_VAV2024 | VAV | Not Included | Executive Director Office S-0232 | [7 empty] | RDC
RDC_SB_GF_VAV2025 | VAV | Not Included | Executive Director Office S-0233 | [7 empty] | RDC
RDC_SB_GF_VAV2026 | VAV | Included | Office S-0234 | [7 empty] | RDC
RDC_SB_GF_VAV2027 | VAV | Included | Office S-0235 | [7 empty] | RDC
RDC_SB_GF_VAV2028 | VAV | Included | Office S-0236 | [7 empty] | RDC
RDC_SB_GF_VAV2029 | VAV | Included | Waiting Area S-0251 | [7 empty] | RDC
RDC_SB_GF_VAV2030 | VAV | Included | Office S-0259 | [7 empty] | RDC
RDC_SB_GF_VAV2031 | VAV | Included | Office S-0260 | [7 empty] | RDC
RDC_SB_GF_VAV2032 | VAV | Included | Open Plan S-0269 | [7 empty] | RDC
RDC_SB_GF_VAV2033 | VAV | Included | Store S-0275 | [7 empty] | RDC
RDC_SB_GF_VAV2034 | VAV | Included | Meeting Room S-0274 | [7 empty] | RDC
RDC_SB_GF_VAV2035 | VAV | Included | Pantry S-0270 | [7 empty] | RDC
RDC_SB_GF_VAV2036 | VAV | Not Included | Emergency Elec. Room S-0278 | [7 empty] | RDC
RDC_SB_GF_VAV2037 | VAV | Included | Men S-0284 | [7 empty] | RDC
RDC_SB_GF_VAV2038 | VAV | Included | Informal Meeting S-0285 | [7 empty] | RDC
RDC_SB_GF_VAV2039 | VAV | Included | Meeting Room S-0286 | [7 empty] | RDC
RDC_SB_GF_VAV2040 | VAV | Included | Open Plan S-0289 | [7 empty] | RDC
RDC_SB_GF_VAV2041 | VAV | Included | Open Plan S-0289 | [7 empty] | RDC
RDC_SB_GF_VAV2042 | VAV | Included | Corridor S-0273 | [7 empty] | RDC
RDC_SB_GF_VAV2043 | VAV | Included | Women S-0281 | [7 empty] | RDC
RDC_SB_GF_VAV2044 | VAV | Included | Lobby S-0294 | [7 empty] | RDC
RDC_SB_GF_VAV2045 | VAV | Included | Lobby S-0294 | [7 empty] | RDC
RDC_SB_GF_VAV2046 | VAV | Included | Lobby S-0294 | [7 empty] | RDC
RDC_SB_GF_VAV2047 | VAV | Included | Lobby S-0294 | [7 empty] | RDC
RDC_SB_GF_VAV3001 | VAV | Not Included | Director Office S-0237 | [7 empty] | RDC
RDC_SB_GF_VAV3002 | VAV | Included | Office S-0238 | [7 empty] | RDC
RDC_SB_GF_VAV3003 | VAV | Included | Office S-0239 | [7 empty] | RDC
RDC_SB_GF_VAV3004 | VAV | Included | Office S-0240 | [7 empty] | RDC
RDC_SB_GF_VAV3005 | VAV | Included | Office S-0241 | [7 empty] | RDC
RDC_SB_GF_VAV3006 | VAV | Included | Office S-0242 | [7 empty] | RDC
RDC_SB_GF_VAV3007 | VAV | Not Included | Director Office S-0243 | [7 empty] | RDC
RDC_SB_GF_VAV3008 | VAV | Included | Open Plan S-0244 | [7 empty] | RDC
RDC_SB_GF_VAV3009 | VAV | Included | Open Plan S-0244 | [7 empty] | RDC
RDC_SB_GF_VAV3010 | VAV | Included | Open Plan S-0244 | [7 empty] | RDC
RDC_SB_GF_VAV3011 | VAV | Included | Meeting Room S-0245 | [7 empty] | RDC
RDC_SB_GF_VAV3012 | VAV | Included | Office S-0246 | [7 empty] | RDC
RDC_SB_GF_VAV3013 | VAV | Included | Office S-0247 | [7 empty] | RDC
RDC_SB_GF_VAV3014 | VAV | Included | Office S-0248 | [7 empty] | RDC
RDC_SB_GF_VAV3015 | VAV | Not Included | Security S-0249 | [7 empty] | RDC
RDC_SB_GF_VAV3016 | VAV | Included | Corridor S-0250 | [7 empty] | RDC
RDC_SB_GF_VAV3017 | VAV | Included | Office S-0251 | [7 empty] | RDC
RDC_SB_GF_VAV3018 | VAV | Included | Corridor S-0251 | [7 empty] | RDC
RDC_SB_GF_VAV3019 | VAV | Included | Corridor S-0251 | [7 empty] | RDC
RDC_SB_GF_VAV3020 | VAV | Included | Office S-0252 | [7 empty] | RDC
RDC_SB_GF_VAV3021 | VAV | Included | Office S-0252 | [7 empty] | RDC
RDC_SB_GF_VAV3022 | VAV | Included | Office S-0253 | [7 empty] | RDC
RDC_SB_GF_VAV3023 | VAV | Included | Office S-0253 | [7 empty] | RDC
RDC_SB_GF_VAV3024 | VAV | Included | Office S-0254 | [7 empty] | RDC
RDC_SB_GF_VAV3025 | VAV | Included | Office S-0255 | [7 empty] | RDC
RDC_SB_GF_VAV3026 | VAV | Included | Office S-0256 | [7 empty] | RDC
RDC_SB_GF_VAV3027 | VAV | Included | Office S-0257 | [7 empty] | RDC
RDC_SB_GF_VAV3028 | VAV | Included | Office S-0258 | [7 empty] | RDC
RDC_SB_GF_VAV3029 | VAV | Included | Open Plan S-0261 | [7 empty] | RDC
RDC_SB_GF_VAV3030 | VAV | Included | Open Plan S-0262 | [7 empty] | RDC
RDC_SB_GF_VAV3031 | VAV | Not Included | Server S-0264 | [7 empty] | RDC
RDC_SB_GF_VAV3032 | VAV | Included | Open Plan S-0265 | [7 empty] | RDC
RDC_SB_GF_VAV3033 | VAV | Not Included | Corridor / Print / Emergency Elec Rm / Normal Elec Rm S-0251 / S-0263 / S-0266 / S-0267 | [7 empty] | RDC
RDC_SB_GF_VAV3034 | VAV | Included | Vestibule S-0293 | [7 empty] | RDC
RDC_SB_GF_VAV3035 | VAV | Included | Lobby S-0294 | [7 empty] | RDC
RDC_SB_GF_VAV3036 | VAV | Included | Lobby S-0294 | [7 empty] | RDC
RDC_SB_GF_VAV3501 | VAV | Included | Lobby S-0294 | [7 empty] | RDC
RDC_SB_GF_VAV3502 | VAV | Included | Lobby S-0294 | [7 empty] | RDC
RDC_SB_GF_VAV3503 | VAV | Included | Vestibule S-0293 | [7 empty] | RDC
RDC_NB_1F_VAV4510 | VAV | Included | Corridor N-1202A | [7 empty] | RDC
RDC_NB_1F_VAV4515_EV4516 | EV | Not Included | Emergency Electrical Room N-1203 | [7 empty] | RDC
RDC_NB_1F_VAV4520_EV4521 | EV | Not Included | Normal Electrical Room N-1204 | [7 empty] | RDC
RDC_NB_1F_VAV4525_EV4526 | EV | Included | Conference Room N-1205 | [7 empty] | RDC
RDC_NB_1F_VAV4530_EV4531 | EV | Included | Office N-1206 | [7 empty] | RDC
RDC_NB_1F_VAV4535_EV4536 | EV | Included | Office N-1207 | [7 empty] | RDC
RDC_NB_1F_VAV4540_EV4541 | EV | Included | Office N-1208 | [7 empty] | RDC
RDC_NB_1F_VAV4545_EV4546 | EV | Included | Office N-1209 | [7 empty] | RDC
RDC_NB_1F_VAV4550_EV4551 | EV | Included | Office N-1210 | [7 empty] | RDC
RDC_NB_1F_VAV4555_EV4556 | EV | Included | Confer Room N-1211 | [7 empty] | RDC
RDC_NB_1F_VAV4560_EV4561 | EV | Included | Office N-1212 | [7 empty] | RDC
RDC_NB_1F_VAV4565_EV4566 | EV | Included | Storage Room N-1215 | [7 empty] | RDC
RDC_NB_1F_VAV4570_EV4571 | EV | Included | Office 04 N-1214 | [7 empty] | RDC
RDC_NB_1F_VAV4575_EV4576 | EV | Included | Storage N-1215 | [7 empty] | RDC
RDC_NB_1F_VAV4580 | VAV | Not Included | Photovoltaic Lab N-1216A | [7 empty] | RDC
RDC_NB_1F_VAV4600 | VAV | Not Included | Testing Room N-1216B | [7 empty] | RDC
RDC_NB_1F_VAV4601 | VAV | Not Included | Testing Room N-1216B | [7 empty] | RDC
RDC_NB_1F_VAV4620_VEV4621 | VEV | Not Included | EL Shop N-1216C | [7 empty] | RDC
RDC_NB_1F_VAV4630_VEV4631 | VEV | Not Included | GIS N-1216D | [7 empty] | RDC
RDC_NB_1F_VAV4650 | VAV | Included | Breakout N-1225 | [7 empty] | RDC
RDC_NB_1F_VAV4660 | VAV | Included | Expansion Workstation N-1227 | [7 empty] | RDC
RDC_NB_1F_VAV4665 | VAV | Included | Office N-1228 | [7 empty] | RDC
RDC_NB_1F_VAV4670 | VAV | Included | Office N-1229 | [7 empty] | RDC
RDC_NB_1F_VAV4675 | VAV | Included | Office N-1230 | [7 empty] | RDC
RDC_NB_1F_VAV4680 | VAV | Included | Office N-1231 | [7 empty] | RDC
RDC_NB_1F_VAV4685 | VAV | Included | Workstation N-1232 | [7 empty] | RDC
RDC_NB_1F_VAV4690 | VAV | Included | Office N-1233 | [7 empty] | RDC
RDC_NB_1F_VAV4695 | VAV | Included | Office N-1234 | [7 empty] | RDC
RDC_NB_1F_VAV4700 | VAV | Included | Office N-1235 | [7 empty] | RDC
RDC_NB_1F_VAV4705 | VAV | Included | Office N-1236 | [7 empty] | RDC
RDC_NB_1F_VAV4710 | VAV | Included | Workstation N-1237 | [7 empty] | RDC
RDC_NB_1F_VAV4715 | VAV | Included | Office N-1238 | [7 empty] | RDC
RDC_NB_1F_VAV4720 | VAV | Included | Office N-1239 | [7 empty] | RDC
RDC_NB_1F_VAV4725 | VAV | Included | Office N-1240 | [7 empty] | RDC
RDC_NB_1F_VAV4730 | VAV | Included | Office N-1241 | [7 empty] | RDC
RDC_NB_1F_VAV4735 | VAV | Included | Workstation N-1242 | [7 empty] | RDC
RDC_NB_1F_VAV4740 | VAV | Included | Exp Office N-1243 | [7 empty] | RDC
RDC_NB_1F_VAV4745 | VAV | Included | Office N-1244 | [7 empty] | RDC
RDC_NB_1F_VAV4900P | VAV | Not Included | Normal Electric N-2102 | [7 empty] | RDC
RDC_NB_1F_VAV4910P | VAV | Not Included | Emer. Elec. N-2104 | [7 empty] | RDC
RDC_NB_1F_VAV5500 | VAV | Included | Lobby N-1101 | [7 empty] | RDC
RDC_NB_1F_VAV5501 | VAV | Included | Lobby N-1101 | [7 empty] | RDC
RDC_NB_1F_VAV5510_EV5511 | EV | Included | Conference N-1101A | [7 empty] | RDC
RDC_NB_1F_VAV5515_EV5516 | EV | Not Included | Emergency Electrical Room N-1102 | [7 empty] | RDC
RDC_NB_1F_VAV5520_EV5521 | EV | Included | Conference N-1106 | [7 empty] | RDC
RDC_NB_1F_VAV5525_EV5526 | EV | Included | Conference N-1107 | [7 empty] | RDC
RDC_NB_1F_VAV5535_EV5536 | EV | Included | Conference N-1112 | [7 empty] | RDC
RDC_NB_1F_VAV5540_EV5541 | EV | Not Included | Normal Electrical Room N-1113 | [7 empty] | RDC
RDC_NB_1F_VAV5550_VEV5551 | VEV | Not Included | PCR N-1115A | [7 empty] | RDC
RDC_NB_1F_VAV5560_VEV5561 | VEV | Not Included | PRE-PCR N-1115B | [7 empty] | RDC
RDC_NB_1F_VAV5570 | VAV | Not Included | Met/Prot Lab N-1115C | [7 empty] | RDC
RDC_NB_1F_VAV5571 | VAV | Not Included | Met/Prot Lab N-1115C | [7 empty] | RDC
RDC_NB_1F_VAV5580_VEV5581 | VEV | Not Included | DNA/RNA N-1115D | [7 empty] | RDC
RDC_NB_1F_VAV5590 | VAV | Not Included | Cell Culture N-1115E | [7 empty] | RDC
RDC_NB_1F_VAV5600_VEV5601 | VEV | Included | Library N-1115H | [7 empty] | RDC
RDC_NB_1F_VAV5610_VEV5611 | VEV | Not Included | Cold Room N-1115F | [7 empty] | RDC
RDC_NB_1F_VAV5620_VEV5622 | VEV | Not Included | Sequence Lab N-1115K | [7 empty] | RDC
RDC_NB_1F_VAV5621_VEV5623 | VEV | Not Included | Sequence Lab N-1115K | [7 empty] | RDC
RDC_NB_1F_VAV5630_VEV5631 | VEV | Not Included | Genom Med Lab N-1115K1 | [7 empty] | RDC
RDC_NB_1F_VAV5650 | VAV | Included | Office N-1120 | [7 empty] | RDC
RDC_NB_1F_VAV5655_EV5656 | EV | Included | Store N-1120B | [7 empty] | RDC
RDC_NB_1F_VAV5660 | VAV | Included | Office N-1121 | [7 empty] | RDC
RDC_NB_1F_VAV5665 | VAV | Included | Office N-1122 | [7 empty] | RDC
RDC_NB_1F_VAV5670 | VAV | Included | Office N-1123 | [7 empty] | RDC
RDC_NB_1F_VAV5675 | VAV | Included | Office N-1124 | [7 empty] | RDC
RDC_NB_1F_VAV5680 | VAV | Included | Office N-1125 | [7 empty] | RDC
RDC_NB_1F_VAV5685 | VAV | Included | Corridor N-1126 | [7 empty] | RDC
RDC_NB_1F_VAV5690 | VAV | Included | Office N-1127 | [7 empty] | RDC
RDC_NB_1F_VAV5695 | VAV | Included | Office N-1128 | [7 empty] | RDC
RDC_NB_1F_VAV5700 | VAV | Included | Office N-1129 | [7 empty] | RDC
RDC_NB_1F_VAV5705 | VAV | Included | Office N-1130 | [7 empty] | RDC
RDC_NB_1F_VAV5710 | VAV | Included | Office N-1131 | [7 empty] | RDC
RDC_NB_1F_VAV5715_EV5716 | EV | Included | Conf Rm N-1132 | [7 empty] | RDC
RDC_NB_1F_VAV5730_EV5731 | EV | Included | Store N-1135 | [7 empty] | RDC
RDC_NB_1F_VAV5735_EV5736 | EV | Not Included | Normal Elec. N-1136 | [7 empty] | RDC
RDC_NB_1F_VAV5740_EV5741 | EV | Not Included | Emer. Elec. N-1137 | [7 empty] | RDC
RDC_NB_1F_VAV5745 | VAV | Included | Corridor N-1138 | [7 empty] | RDC
RDC_NB_1F_VAV5760_EV5761 | EV | Included | Conf N-1143 | [7 empty] | RDC
RDC_NB_1F_VAV5770_VEV5771 | VEV | Not Included | Histology N-1144A | [7 empty] | RDC
RDC_NB_1F_VAV5780_VEV5781 | VEV | Not Included | Culture & Gel Rm N-1144B | [7 empty] | RDC
RDC_NB_1F_VAV5790 | VAV | Not Included | Shafallah N-1144C | [7 empty] | RDC
RDC_NB_1F_VAV5792_VEV5793 | VEV | Not Included | Sample Accession N-1144C1 | [7 empty] | RDC
RDC_NB_1F_VAV5794_VEV5795A | VAV | Included | Storage and Archives N-1144C2 | [7 empty] | RDC
RDC_NB_1F_VAV5800_VEV5801 | VEV | Not Included | Pre-PCR N-1144D | [7 empty] | RDC
RDC_NB_1F_VAV5810 | VAV | Not Included | Nano Lab N-1144E | [7 empty] | RDC
RDC_NB_1F_VAV5814 | VAV | Not Included | Nano Lab N-1144E | [7 empty] | RDC
RDC_NB_1F_VAV5835_EV5836 | EV | Included | P/C/S Pantry N-1146 | [7 empty] | RDC
RDC_NB_1F_VAV5840 | VAV | Included | Corridor N-1150 | [7 empty] | RDC
RDC_NB_1F_VAV5845 | VAV | Included | Reception+N-1151B Storage N-1151 | [7 empty] | RDC
RDC_NB_1F_VAV5850 | VAV | Included | Office 04 N-1151A | [7 empty] | RDC
RDC_NB_1F_VAV5855 | VAV | Included | Office 04 N-1152 | [7 empty] | RDC
RDC_NB_1F_VAV5860 | VAV | Included | Office N-1154 | [7 empty] | RDC
RDC_NB_1F_VAV5865 | VAV | Included | Office N-1155 | [7 empty] | RDC
RDC_NB_1F_VAV5870 | VAV | Included | Exp Office N-1156 | [7 empty] | RDC
RDC_NB_1F_VAV5875 | VAV | Included | Office N-1157 | [7 empty] | RDC
RDC_NB_1F_VAV5880 | VAV | Included | Office N-1158 | [7 empty] | RDC
RDC_NB_1F_VAV5885 | VAV | Included | Office N-1159 | [7 empty] | RDC
RDC_NB_1F_VAV5890 | VAV | Included | Workstation N-1160 | [7 empty] | RDC
RDC_NB_1F_VAV5895 | VAV | Included | Office N-1161 | [7 empty] | RDC
RDC_NB_1F_VAV5900 | VAV | Included | Office N-1162 | [7 empty] | RDC
RDC_NB_1F_VAV5905 | VAV | Included | Office N-1163 | [7 empty] | RDC
RDC_NB_1F_VAV5910 | VAV | Included | Office N-1164 | [7 empty] | RDC
RDC_NB_1F_VAV5915 | VAV | Included | Office N-1167 | [7 empty] | RDC
RDC_NB_1F_VAV5920 | VAV | Included | Workstation N-1168 | [7 empty] | RDC
RDC_NB_1F_VAV5925 | VAV | Included | Office N-1169 | [7 empty] | RDC
RDC_NB_1F_VAV5930 | VAV | Included | Office N-1170 | [7 empty] | RDC
RDC_NB_1F_VAV5930P | VAV | Not Included | Normal Elec. N-2105 | [7 empty] | RDC
RDC_NB_1F_VAV5935 | VAV | Included | Office N-1166 | [7 empty] | RDC
RDC_NB_1F_VAV5940 | VAV | Included | Workstation N-1165 | [7 empty] | RDC
RDC_NB_1F_VAV5940P | VAV | Not Included | Emer. Elec. N-2106 | [7 empty] | RDC
RDC_NB_1F_VAV6505_EV6506 | EV | Included | Conference N-1302 | [7 empty] | RDC
RDC_NB_1F_VAV6510_EV6511 | EV | Included | Conference N-1303 | [7 empty] | RDC
RDC_NB_1F_VAV6525_EV6526 | EV | Not Included | Normal Electrical Room N-1310 | [7 empty] | RDC
RDC_NB_1F_VAV6530_VEV6531 | VEV | Not Included | AAV N-1316A | [7 empty] | RDC
RDC_NB_1F_VAV6540 | VAV | Not Included | Tissure Culture 1 N-1316B | [7 empty] | RDC
RDC_NB_1F_VAV6550 | VAV | Not Included | Gene Therapy Lab N-1316C | [7 empty] | RDC
RDC_NB_1F_VAV6551 | VAV | Not Included | Gene Therapy Lab N-1316C | [7 empty] | RDC
RDC_NB_1F_VAV6560_VEV6561 | VEV | Not Included | TC2 N-1316D | [7 empty] | RDC
RDC_NB_1F_VAV6570_VEV6571 | VEV | Included | STORE ROOM N-1316E | [7 empty] | RDC
RDC_NB_1F_VAV6590_VEV6591 | VEV | Not Included | LENTIV N-1316G | [7 empty] | RDC
RDC_NB_1F_VAV6600_VEV6601 | VEV | Not Included | Analytical Core N-1316H | [7 empty] | RDC
RDC_NB_1F_VAV6610_VEV6611 | VEV | Not Included | Microscope Room N-1316H | [7 empty] | RDC
RDC_NB_1F_VAV6620_VEV6621 | VEV | Not Included | Mscopy1 N-1316K | [7 empty] | RDC
RDC_NB_1F_VAV6630A | VAV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_VAV6630B | VAV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_VAV6631A | VAV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_VAV6631B | VAV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_VAV6650 | VAV | Included | Office N-1319 | [7 empty] | RDC
RDC_NB_1F_VAV6655 | VAV | Included | Office N-1320 | [7 empty] | RDC
RDC_NB_1F_VAV6660 | VAV | Included | Workstation N-1321 | [7 empty] | RDC
RDC_NB_1F_VAV6665 | VAV | Included | Office N-1322 | [7 empty] | RDC
RDC_NB_1F_VAV6670 | VAV | Included | Office N-1323 | [7 empty] | RDC
RDC_NB_1F_VAV6675 | VAV | Included | Workstation N-1324 | [7 empty] | RDC
RDC_NB_1F_VAV6680 | VAV | Included | Office N-1325 | [7 empty] | RDC
RDC_NB_1F_VAV6685 | VAV | Included | Office N-1326 | [7 empty] | RDC
RDC_NB_1F_VAV6690 | VAV | Included | Exp. Workstation N-1327 | [7 empty] | RDC
RDC_NB_1F_VAV6695 | VAV | Included | Office N-1328 | [7 empty] | RDC
RDC_NB_1F_VAV6700_EV6701 | EV | Not Included | NORMAL ELEC. N-1329 | [7 empty] | RDC
RDC_NB_1F_VAV6705 | VAV | Included | Office N-1330 | [7 empty] | RDC
RDC_NB_1F_VAV6710 | VAV | Included | Office N-1331 | [7 empty] | RDC
RDC_NB_1F_VAV6715 | VAV | Included | Office N-1332 | [7 empty] | RDC
RDC_NB_1F_VAV6720 | VAV | Included | Corridor N-1335 | [7 empty] | RDC
RDC_NB_1F_VAV6725_EV6726 | EV | Not Included | Emer. Elec. N-1336 | [7 empty] | RDC
RDC_NB_1F_VAV6750 | VAV | Not Included | Tissue Culture 1 N-1345A | [7 empty] | RDC
RDC_NB_1F_VAV6760 | VAV | Not Included | Diabetes Lab N-1345B | [7 empty] | RDC
RDC_NB_1F_VAV6761 | VAV | Not Included | Diabetes Lab N-1345B | [7 empty] | RDC
RDC_NB_1F_VAV6800_VEV6801 | VEV | Not Included | Tissue Culture 3 N-1345D | [7 empty] | RDC
RDC_NB_1F_VAV6810_VEV6811 | VEV | Not Included | Calc Imaging N-1345E | [7 empty] | RDC
RDC_NB_1F_VAV6820_VEV6821 | VEV | Not Included | Electro Physics N-1345F | [7 empty] | RDC
RDC_NB_1F_VAV6830_VEV6831 | VEV | Not Included | Shared Cold Lab N-1345G | [7 empty] | RDC
RDC_NB_1F_VAV6840_VEV6841 | VEV | Not Included | Bacterlgy Lab N-1345H | [7 empty] | RDC
RDC_NB_1F_VAV6850 | VAV | Not Included | Bio-Med Chem Lab 2 N-1345J | [7 empty] | RDC
RDC_NB_1F_VAV6851 | VAV | Not Included | Bio-Med Chem Lab 2 N-1345J | [7 empty] | RDC
RDC_NB_1F_VAV6870_EV6871 | EV | Not Included | Emergency Electrical Room N-1353 | [7 empty] | RDC
RDC_NB_1F_VAV6880 | VAV | Included | Reception+N-1355C Storage N-1355 | [7 empty] | RDC
RDC_NB_1F_VAV6885 | VAV | Included | Office 04 N-1355A | [7 empty] | RDC
RDC_NB_1F_VAV6890_EV6891 | EV | Included | Conference Room N-1355B | [7 empty] | RDC
RDC_NB_1F_VAV6895 | VAV | Included | Office 04 N-1356 | [7 empty] | RDC
RDC_NB_1F_VAV6900 | VAV | Included | Office N-1357 | [7 empty] | RDC
RDC_NB_1F_VAV6905 | VAV | Included | Open Plan N-1358 | [7 empty] | RDC
RDC_NB_1F_VAV6910 | VAV | Included | Office N-1359 | [7 empty] | RDC
RDC_NB_1F_VAV6915 | VAV | Included | Office N-1360 | [7 empty] | RDC
RDC_NB_1F_VAV6920 | VAV | Included | Office N-1360B | [7 empty] | RDC
RDC_NB_1F_VAV6925 | VAV | Included | Office N-1361 | [7 empty] | RDC
RDC_NB_1F_VAV6930 | VAV | Included | Office N-1362 | [7 empty] | RDC
RDC_NB_1F_VAV6935 | VAV | Included | Workstation N-1363 | [7 empty] | RDC
RDC_NB_1F_VAV6940 | VAV | Included | Office N-1364 | [7 empty] | RDC
RDC_NB_1F_VAV6945 | VAV | Included | Office N-1365 | [7 empty] | RDC
RDC_NB_1F_VAV6950 | VAV | Included | Office N-1366 | [7 empty] | RDC
RDC_NB_1F_VAV6955 | VAV | Included | Office N-1367 | [7 empty] | RDC
RDC_NB_1F_VAV6960 | VAV | Included | Workstation N-1368 | [7 empty] | RDC
RDC_NB_1F_VAV6965 | VAV | Included | Office N-1369 | [7 empty] | RDC
RDC_NB_1F_VAV6967 | VAV | Included | Office N-1370 | [7 empty] | RDC
RDC_NB_1F_VAV6968 | VAV | Included | Workstation N-1371 | [7 empty] | RDC
RDC_NB_1F_VAV6970_EV6971 | EV | Included | PANTRY N-1372 | [7 empty] | RDC
RDC_NB_1F_VAV6972 | VAV | Included | Office N-1374 | [7 empty] | RDC
RDC_NB_1F_VAV6974 | VAV | Included | Office N-1375 | [7 empty] | RDC
RDC_NB_1F_VAV6976 | VAV | Included | Office N-1376 | [7 empty] | RDC
RDC_NB_1F_VAV6978 | VAV | Included | Office N-1377 | [7 empty] | RDC
RDC_NB_1F_VAV6979P | VAV | Not Included | Normal Elec. N-2107 | [7 empty] | RDC
RDC_NB_1F_VAV6980P | VAV | Not Included | IDF N-2110 | [7 empty] | RDC
RDC_NB_1F_VAV7510_VEV7511 | VEV | Not Included | TC1 N-1404A | [7 empty] | RDC
RDC_NB_1F_VAV7530_VEV7532 | VEV | Not Included | Cell Bio N-1404C | [7 empty] | RDC
RDC_NB_1F_VAV7531_VEV7533 | VEV | Not Included | Cell Bio N-1404C | [7 empty] | RDC
RDC_NB_1F_VAV7540_VEV7541 | VEV | Not Included | Shared Eq Rm N-1404D | [7 empty] | RDC
RDC_NB_1F_VAV7550_VEV7551 | VEV | Not Included | TC2 N-1404E | [7 empty] | RDC
RDC_NB_1F_VAV7560_VEV7561 | VEV | Not Included | Imaging N-1404F | [7 empty] | RDC
RDC_NB_1F_VAV7570_VEV7571 | VEV | Not Included | Cell Bio Lab2 N-1404G | [7 empty] | RDC
RDC_NB_1F_VAV7580_VEV7581 | VEV | Not Included | TC3 N-1404H | [7 empty] | RDC
RDC_NB_1F_VAV7600_VEV7601 | VEV | Not Included | Cell Bio Lab3 N-1404K | [7 empty] | RDC
RDC_NB_1F_VAV7620 | VAV | Included | Office N-1415 | [7 empty] | RDC
RDC_NB_1F_VAV7625 | VAV | Included | Office N-1416 | [7 empty] | RDC
RDC_NB_1F_VAV7630 | VAV | Included | Office 05 - 2 WKS- N-1407 | [7 empty] | RDC
RDC_NB_1F_VAV7635 | VAV | Included | Office N-1418 | [7 empty] | RDC
RDC_NB_1F_VAV7640 | VAV | Included | Office N-1419 | [7 empty] | RDC
RDC_NB_1F_VAV7645 | VAV | Included | Exp. Workstation N-1420 | [7 empty] | RDC
RDC_NB_1F_VAV7650 | VAV | Included | Office N-1421 | [7 empty] | RDC
RDC_NB_1F_VAV7655 | VAV | Included | Office N-1422 | [7 empty] | RDC
RDC_NB_1F_VAV7660 | VAV | Included | Workstation N-1423 | [7 empty] | RDC
RDC_NB_1F_VAV7665_EV7666 | EV | Not Included | Normal Elec. N-1425 | [7 empty] | RDC
RDC_NB_1F_VAV7670 | VAV | Included | Office N-1426 | [7 empty] | RDC
RDC_NB_1F_VAV7675 | VAV | Included | Office N-1428 | [7 empty] | RDC
RDC_NB_1F_VAV7680_EV7681 | EV | Included | Conf N-1429 | [7 empty] | RDC
RDC_NB_1F_VAV7685 | VAV | Included | Office N-1433 | [7 empty] | RDC
RDC_NB_1F_VAV7690 | VAV | Included | Office N-1435 | [7 empty] | RDC
RDC_NB_1F_VAV7695 | VAV | Included | Office N-1437 | [7 empty] | RDC
RDC_NB_1F_VAV7700_EV7701 | EV | Not Included | Emer. Elec. N-1438 | [7 empty] | RDC
RDC_NB_1F_VAV7705 | VAV | Included | Office 05 - 24 WKS + N-1441 Room N-1442 | [7 empty] | RDC
RDC_NB_1F_VAV7710 | VAV | Included | Workstation N-1442 | [7 empty] | RDC
RDC_NB_1F_VAV7730_VEV7731 | VEV | Not Included | Microscope 2 N-1450A | [7 empty] | RDC
RDC_NB_1F_VAV7740_VEV7741 | VEV | Not Included | LN2 Stor N-1450B | [7 empty] | RDC
RDC_NB_1F_VAV7750_VEV7751 | VEV | Not Included | Flow Cyto N-1450C | [7 empty] | RDC
RDC_NB_1F_VAV7770_VEV7771 | VEV | Not Included | Qurnt N-1450E | [7 empty] | RDC
RDC_NB_1F_VAV7780_VEV7781 | VEV | Not Included | iPS-TC N-1450F | [7 empty] | RDC
RDC_NB_1F_VAV7800_VEV7801 | VEV | Not Included | IPS TISSUE CULTURE N-1450J | [7 empty] | RDC
RDC_NB_1F_VAV7810_VEV7811 | VEV | Not Included | TC1 N-1450L | [7 empty] | RDC
RDC_NB_1F_VAV7820_VEV7822 | VEV | Not Included | STEM/PCR Open Lab N-1450M | [7 empty] | RDC
RDC_NB_1F_VAV7821_VEV7823 | VEV | Not Included | STEM/PCR Open Lab N-1450M | [7 empty] | RDC
RDC_NB_1F_VAV7830_VEV7831 | VEV | Not Included | TC2 N-1450N | [7 empty] | RDC
RDC_NB_1F_VAV7840_EV7841 | EV | Included | Conf N-1458 | [7 empty] | RDC
RDC_NB_1F_VAV7845_EV7846 | EV | Included | Conf N-1459 | [7 empty] | RDC
RDC_NB_1F_VAV7850 | VAV | Included | Office N-1459A | [7 empty] | RDC
RDC_NB_1F_VAV7860 | VAV | Included | Exp. Workstation N-1461 | [7 empty] | RDC
RDC_NB_1F_VAV7865 | VAV | Included | Workstation N-1461A | [7 empty] | RDC
RDC_NB_1F_VAV7870 | VAV | Included | Office N-1462 | [7 empty] | RDC
RDC_NB_1F_VAV7875 | VAV | Included | Office N-1463 | [7 empty] | RDC
RDC_NB_1F_VAV7880 | VAV | Included | Office N-1464 | [7 empty] | RDC
RDC_NB_1F_VAV7885 | VAV | Included | Office N-1465 | [7 empty] | RDC
RDC_NB_1F_VAV7890 | VAV | Included | Workstation N-1466 | [7 empty] | RDC
RDC_NB_1F_VAV7895 | VAV | Included | Office N-1467 | [7 empty] | RDC
RDC_NB_1F_VAV7900 | VAV | Included | Office N-1468 | [7 empty] | RDC
RDC_NB_1F_VAV7905 | VAV | Included | Office N-1469 | [7 empty] | RDC
RDC_NB_1F_VAV7910 | VAV | Included | Office N-1470 | [7 empty] | RDC
RDC_NB_1F_VAV7915 | VAV | Included | Workstation N-1471 | [7 empty] | RDC
RDC_NB_1F_VAV7920 | VAV | Included | Office N-1472 | [7 empty] | RDC
RDC_NB_1F_VAV7925 | VAV | Included | Office N-1473 | [7 empty] | RDC
RDC_NB_1F_VAV7930 | VAV | Included | Office N-1474 | [7 empty] | RDC
RDC_NB_1F_VAV7935 | VAV | Included | Office N-1475 | [7 empty] | RDC
RDC_NB_1F_VAV7940 | VAV | Included | Workstation N-1476 | [7 empty] | RDC
RDC_NB_1F_VAV7945 | VAV | Included | Office N-1477 | [7 empty] | RDC
RDC_NB_1F_VAV7950 | VAV | Included | Office N-1478 | [7 empty] | RDC
RDC_NB_1F_VAV7955 | VAV | Included | Office N-1479 | [7 empty] | RDC
RDC_NB_1F_VAV7960 | VAV | Included | Office N-1480 | [7 empty] | RDC
RDC_NB_1F_VAV7975P | VAV | Not Included | Normal Elec. N-2111 | [7 empty] | RDC
RDC_NB_1F_VAV7980P | VAV | Not Included | Emer. Elec. N-2112 | [7 empty] | RDC
RDC_NB_1F_FCU4910 | FCU | Included | Stair 1 N-1ST01 | [7 empty] | RDC
RDC_NB_1F_FCU4914 | FCU | Not Included | Mech/ FPC N- L1 A2.1 | [7 empty] | RDC
RDC_NB_1F_FCU4915 | FCU | Not Included | MDF N-1201 | [7 empty] | RDC
RDC_NB_1F_FCU4916 | FCU | Included | Stair 1 N-1ST01 | [7 empty] | RDC
RDC_NB_1F_FCU4917 | FCU | Included | Stair N-1ST02 | [7 empty] | RDC
RDC_NB_1F_FCU5983 | FCU | Not Included | IDF N-1140 | [7 empty] | RDC
RDC_NB_1F_FCU5984 | FCU | Not Included | ROBOTICS N-115J | [7 empty] | RDC
RDC_NB_1F_FCU5985 | FCU | Included | Corridor N-1142 | [7 empty] | RDC
RDC_NB_1F_FCU5986 | FCU | Included | Corridor N-1142 | [7 empty] | RDC
RDC_NB_1F_FCU5987 | FCU | Included | Stair 3 N-L1 A2.3 | [7 empty] | RDC
RDC_NB_1F_FCU5993 | FCU | Included | Conference Room N-L0 A2.2 | [7 empty] | RDC
RDC_NB_1F_FCU5994 | FCU | Included | Conference Room N-L0 A2.2 | [7 empty] | RDC
RDC_NB_1F_FCU6988 | FCU | Included | Service Corridor N-1337 | [7 empty] | RDC
RDC_NB_1F_FCU6989 | FCU | Included | Service Corridor N-1337 | [7 empty] | RDC
RDC_NB_1F_FCU6990 | FCU | Not Included | Mech/ FPC N-L1 A2.3 | [7 empty] | RDC
RDC_NB_1F_FCU6991 | FCU | Not Included | Mech/ FPC N-L1 A2.3 | [7 empty] | RDC
RDC_NB_1F_FCU6992 | FCU | Included | Stair 4 N-L1 A2.3 | [7 empty] | RDC
RDC_NB_1F_FCU7790 | FCU | Included | Stair 6 N-1ST06 | [7 empty] | RDC
RDC_NB_1F_FCU7984 | FCU | Included | Stair 6 N-1ST06 | [7 empty] | RDC
RDC_NB_1F_FCU7985 | FCU | Not Included | IDF N-1424 | [7 empty] | RDC
RDC_NB_1F_FCU7986 | FCU | Not Included | IDF N-1424 | [7 empty] | RDC
RDC_NB_1F_FCU7987 | FCU | Included | Service Corridor N-1446 | [7 empty] | RDC
RDC_NB_1F_FCU7988 | FCU | Included | Service Corridor N-1446 | [7 empty] | RDC
RDC_NB_1F_FCU7989 | FCU | Included | Stair 5 N-1ST05 | [7 empty] | RDC
RDC_NB_2F_FCU4918 | FCU | Not Included | IDF N-2104 | [7 empty] | RDC
RDC_NB_2F_FCU4919 | FCU | Not Included | IDF N-2104 | [7 empty] | RDC
RDC_NB_2F_FCU5988 | FCU | Not Included | Mechanical (AHU 8512) | [7 empty] | RDC
RDC_NB_2F_FCU5989 | FCU | Included | Stair 2 N-2ST02 | [7 empty] | RDC
RDC_NB_2F_FCU5990 | FCU | Not Included | Mechanical (AHU 8512/8514) | [7 empty] | RDC
RDC_NB_2F_FCU6993 | FCU | Not Included | Mechanical (AHU 8516) | [7 empty] | RDC
RDC_NB_2F_FCU6994 | FCU | Not Included | Normal Elec. N-2105 | [7 empty] | RDC
RDC_NB_2F_FCU6995 | FCU | Not Included | IDF N-2110 | [7 empty] | RDC
RDC_NB_2F_FCU6996 | FCU | Not Included | IDF N-2110 | [7 empty] | RDC
RDC_NB_2F_FCU7991 | FCU | Not Included | Normal Elec. N-2111 | [7 empty] | RDC
RDC_NB_2F_FCU7992 | FCU | Not Included | Emer. Elec. N-2112 | [7 empty] | RDC
RDC_NB_GF_FCU4911 | FCU | Not Included | MDF Room N-0206A | [7 empty] | RDC
RDC_NB_GF_FCU4912 | FCU | Not Included | MDF Room N-0206A | [7 empty] | RDC
RDC_NB_GF_FCU4913 | FCU | Included | Store N-0201 | [7 empty] | RDC
RDC_NB_GF_FCU4920 | FCU | Not Included | Emergency Electrical Landing Room N-0205 | [7 empty] | RDC
RDC_NB_GF_FCU5980 | FCU | Not Included | Serv Core N-0136 | [7 empty] | RDC
RDC_NB_GF_FCU5981 | FCU | Not Included | Serv Core N-0136 | [7 empty] | RDC
RDC_NB_GF_FCU5982 | FCU | Included | Stair 3 N-OST03 | [7 empty] | RDC
RDC_NB_GF_FCU5991 | FCU | Included | Vestibule N-0103 | [7 empty] | RDC
RDC_NB_GF_FCU5992 | FCU | Included | Vestibule N-0102 | [7 empty] | RDC
RDC_NB_GF_FCU6981 | FCU | Not Included | IDF N-0133 | [7 empty] | RDC
RDC_NB_GF_FCU6982 | FCU | Not Included | IDF N-0133 | [7 empty] | RDC
RDC_NB_GF_FCU6983 | FCU | Included | Service Corridor N-0344 | [7 empty] | RDC
RDC_NB_GF_FCU6984 | FCU | Included | Service Corridor N-0344 | [7 empty] | RDC
RDC_NB_GF_FCU6985 | FCU | Not Included | IDF N-0311 | [7 empty] | RDC
RDC_NB_GF_FCU6986 | FCU | Not Included | IDF N-0311 | [7 empty] | RDC
RDC_NB_GF_FCU6987 | FCU | Included | Stair 4 N-0ST04 | [7 empty] | RDC
RDC_NB_GF_FCU7981 | FCU | Not Included | SURF ANALYSIS LAB N-0404F | [7 empty] | RDC
RDC_NB_GF_FCU7982 | FCU | Not Included | SURF ANALYSIS LAB N-0404F | [7 empty] | RDC
RDC_NB_GF_FCU7983 | FCU | Included | Stair 5 N-0ST05 | [7 empty] | RDC
RDC_NB_SB_Walkway_FCU9001 | FCU | Included | Pedestrian Walkway between North & South Buildings | [7 empty] | RDC
RDC_NB_SB_Walkway_FCU9002 | FCU | Included | Pedestrian Walkway between North & South Buildings | [7 empty] | RDC
RDC_NB_SB_Walkway_FCU9003 | FCU | Included | Pedestrian Walkway between North & South Buildings | [7 empty] | RDC
RDC_NB_SB_Walkway_FCU9004 | FCU | Included | Pedestrian Walkway between North & South Buildings | [7 empty] | RDC
RDC_NB_SB_Walkway_FCU9005 | FCU | Included | Pedestrian Walkway between North & South Buildings | [7 empty] | RDC
RDC_SB_1F_FCU0501 | FCU | Included | STAIR-04 1ST04 | [7 empty] | RDC
RDC_SB_1F_FCU0502 | FCU | Not Included | UPS ROOM S-1107D | [7 empty] | RDC
RDC_SB_1F_FCU0503 | FCU | Not Included | UPS ROOM S-1107D | [7 empty] | RDC
RDC_SB_1F_FCU1501 | FCU | Not Included | IDF ROOM S-1156 | [7 empty] | RDC
RDC_SB_1F_FCU1502 | FCU | Not Included | IDF ROOM S-1156 | [7 empty] | RDC
RDC_SB_1F_FCU1503 | FCU | Included | STAIR-01 1ST01 | [7 empty] | RDC
RDC_SB_1F_FCU2501 | FCU | Included | STAIR-03 1ST03 | [7 empty] | RDC
RDC_SB_1F_FCU2502 | FCU | Not Included | IDF ROOM S-1244 | [7 empty] | RDC
RDC_SB_1F_FCU2503 | FCU | Not Included | IDF ROOM S-1244 | [7 empty] | RDC
RDC_SB_1F_FCU2504 | FCU | Not Included | UPS ROOM S-1276 | [7 empty] | RDC
RDC_SB_1F_FCU2505 | FCU | Not Included | UPS ROOM S-1276 | [7 empty] | RDC
RDC_SB_1F_FCU3501 | FCU | Included | STAIR-04 1ST04 | [7 empty] | RDC
RDC_SB_2F_FCU0201 | FCU | Not Included | South Penthouse S-2101 | [7 empty] | RDC
RDC_SB_2F_FCU0202 | FCU | Not Included | South Penthouse S-2101 | [7 empty] | RDC
RDC_SB_2F_FCU0203 | FCU | Not Included | South Penthouse S-2101 | [7 empty] | RDC
RDC_SB_2F_FCU0204 | FCU | Not Included | South Penthouse S-2101 | [7 empty] | RDC
RDC_SB_2F_FCU0205 | FCU | Not Included | Normal Elec. S-2103 | [7 empty] | RDC
RDC_SB_2F_FCU0206 | FCU | Not Included | South Penthouse S-2101 | [7 empty] | RDC
RDC_SB_2F_FCU0207 | FCU | Not Included | Emerg. Elec. S-2104 | [7 empty] | RDC
RDC_SB_2F_FCU0208 | FCU | Not Included | South Penthouse S-2101 | [7 empty] | RDC
RDC_SB_2F_FCU1201 | FCU | Not Included | IDF S-2102 | [7 empty] | RDC
RDC_SB_2F_FCU1202 | FCU | Not Included | IDF S-2102 | [7 empty] | RDC
RDC_SB_2F_FCU2201 | FCU | Not Included | South Penthouse S-2101 | [7 empty] | RDC
RDC_SB_2F_FCU2202 | FCU | Not Included | South Penthouse S-2101 | [7 empty] | RDC
RDC_SB_2F_FCU2203 | FCU | Not Included | South Penthouse S-2101 | [7 empty] | RDC
RDC_SB_2F_FCU2204 | FCU | Not Included | Emerg. Elec. S-2105 | [7 empty] | RDC
RDC_SB_2F_FCU2205 | FCU | Not Included | South Penthouse S-2101 | [7 empty] | RDC
RDC_SB_2F_FCU2206 | FCU | Not Included | Normal Elec. S-2106 | [7 empty] | RDC
RDC_SB_2F_FCU2207 | FCU | Not Included | Normal Elec. S-2106 | [7 empty] | RDC
RDC_SB_2F_FCU2208 | FCU | Not Included | IDF S-2107 | [7 empty] | RDC
RDC_SB_2F_FCU2209 | FCU | Not Included | IDF S-2107 | [7 empty] | RDC
RDC_SB_2F_FCU2210 | FCU | Not Included | South Penthouse S-2101 | [7 empty] | RDC
RDC_SB_GF_FCU0001 | FCU | Included | STAIR-02 S-02T02 | [7 empty] | RDC
RDC_SB_GF_FCU1001 | FCU | Not Included | QTEL ROOM S-0132 | [7 empty] | RDC
RDC_SB_GF_FCU1002 | FCU | Not Included | QTEL ROOM S-0132 | [7 empty] | RDC
RDC_SB_GF_FCU1003 | FCU | Not Included | IDF ROOM S-0133 | [7 empty] | RDC
RDC_SB_GF_FCU1004 | FCU | Not Included | IDF ROOM S-0133 | [7 empty] | RDC
RDC_SB_GF_FCU1005 | FCU | Not Included | EC MDF ROOM S-0134 | [7 empty] | RDC
RDC_SB_GF_FCU1006 | FCU | Not Included | EC MDF ROOM S-0134 | [7 empty] | RDC
RDC_SB_GF_FCU1007 | FCU | Not Included | MECHANICAL ROOM S-0136 | [7 empty] | RDC
RDC_SB_GF_FCU1008 | FCU | Included | STAIR-01 S-01T01 | [7 empty] | RDC
RDC_SB_GF_FCU2001 | FCU | Included | STAIR-03 S-0ST03 | [7 empty] | RDC
RDC_SB_GF_FCU2002 | FCU | Not Included | AV ROOM S-0210 | [7 empty] | RDC
RDC_SB_GF_FCU2003 | FCU | Not Included | AV ROOM S-0210 | [7 empty] | RDC
RDC_SB_GF_FCU2004 | FCU | Not Included | IDF ROOM S-0271 | [7 empty] | RDC
RDC_SB_GF_FCU2005 | FCU | Not Included | IDF ROOM S-0271 | [7 empty] | RDC
RDC_SB_GF_FCU3001 | FCU | Included | STAIR-04 S-0ST04 | [7 empty] | RDC
RDC_UB_GF_FCU8001 | FCU | Included | GENERAL STORAGE ROOM U-0129 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8002 | FCU | Included | SHOP U-0135 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8003 | FCU | Included | MAIL ROOM U-0128 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8004 | FCU | Included | GENERAL STORAGE U-0108 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8005 | FCU | Included | RECYCLING ROOM U-0109 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8006 | FCU | Included | CYLINDER STORAGE U-0105 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8007 | FCU | Not Included | LN2 DISPENSER U-0104 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8008 | FCU | Included | FLAMMABLE STORAGE U-0103 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8009 | FCU | Included | FLAMMABLE WASTE STORAGE U-0102 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8010 | FCU | Not Included | BMS ROOM U-0117 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8011 | FCU | Included | BREAK ROOM U-0118 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8012 | FCU | Included | OFFICE SPACE U-0119 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8013 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8014 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 |  | ahu-8601 | [5 empty] | RDC
RDC_UB_GF_FCU8502 | FCU | Included | SHIPPING AND RECEIVING L0 | [7 empty] | RDC
RDC_UB_GF_FCU8503 | FCU | Included | SHIPPING AND RECEIVING L0 | [7 empty] | RDC
RDC_UB_GF_FCU8504 | FCU | Included | SHIPPING AND RECEIVING L0 | [7 empty] | RDC
RDC_UB_GF_FCU8505 | FCU | Included | SHIPPING AND RECEIVING L0 | [7 empty] | RDC
RDC_UB_GF_FCU8512 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 | [7 empty] | RDC
RDC_UB_GF_FCU8513 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 | [7 empty] | RDC
RDC_UB_GF_FCU8514 | FCU | Not Included | Pump Room U-0121 | [7 empty] | RDC
RDC_UB_GF_FCU8515 | FCU | Not Included | WET/MECH/FIRE ROOM U-0120 | [7 empty] | RDC
RDC_UB_MF_FCU8501 | FCU | Not Included | MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_MF_FCU8506 | FCU | Not Included | MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_MF_FCU8507 | FCU | Not Included | MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_MF_FCU8508 | FCU | Not Included | MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_MF_FCU8509 | FCU | Not Included | MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_MF_FCU8510 | FCU | Not Included | MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_UB_MF_FCU8511 | FCU | Not Included | MECHANICAL ROOM U-1101 | [7 empty] | RDC
RDC_SB_GF_CAV1001 | CAV | Included | [7 empty] | was RDC_SB_L0_AT-1001 - the historian carries the assembly, not the terminal; its parts named 2 different rooms - left blank | RDC
RDC_SB_GF_CAV1005 | CAV | Not Included | Normal & Emergency Elec. Landing S-0142 | [6 empty] | was RDC_SB_L0_AT-1005 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_GF_CAV1006 | CAV | Included | Corridor S-0137 | [6 empty] | was RDC_SB_L0_AT-1006 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_GF_CAV1007 | CAV | Not Included | UPS S-0145 | [6 empty] | was RDC_SB_L0_AT-1007 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_GF_CAV1009 | CAV | Included | Service Dock S-0151 | [6 empty] | was RDC_SB_L0_AT-1009 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_CAV4035 | CAV | Included | Corridor N-0207A | [6 empty] | was RDC_NB_GF_AT-4035 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_CAV4170 | CAV | Included | Storage Room N-0237 | [6 empty] | was RDC_NB_GF_AT-4170 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_CEV-4031 | CEV | Included | Service Corridor N-0207 | [7 empty] | RDC
RDC_NB_GF_EAV4028 | EAV | Not Included | MDF ROOM N-0206A | [6 empty] | was RDC_NB_GF_EV-4028 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV4236 | EAV | Included | Office 05 -8WS- N-0250 | [6 empty] | was RDC_NB_GF_EV-4236 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV4261 | EAV | Included | Office 05 -8WS- N-0255 | [6 empty] | was RDC_NB_GF_EV-4261 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV4286 | EAV | Included | Office 05 -8WS- N-0260 | [6 empty] | was RDC_NB_GF_EV-4286 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV4311 | EAV | Included | WORKSTATION N-0265 | [6 empty] | was RDC_NB_GF_EV-4311 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_VEV-4041 | VEV | Not Included | Air Quality High Bay N-0215A | [7 empty] | RDC
RDC_NB_GF_FEV-4193 | FEV | Not Included | CSP Lab N-0240B | [7 empty] | RDC
RDC_NB_GF_FEV-4194 | FEV | Not Included | CSP Lab N-0240B | [7 empty] | RDC
RDC_NB_GF_VEV-4213A | VEV | Not Included | Desal Lab N-0240D | [7 empty] | RDC
RDC_NB_GF_VEV-4213B | VEV | Not Included | Desal Lab N-0240D | [7 empty] | RDC
RDC_NB_GF_FEV-4214 | FEV | Not Included | Desal Lab N-0240D | [7 empty] | RDC
RDC_NB_GF_FEV-4215 | FEV | Not Included | Desal Lab N-0240D | [7 empty] | RDC
RDC_NB_GF_FEV-4216 | FEV | Not Included | Desal Lab N-0240D | [7 empty] | RDC
RDC_SB_GF_CAV0006 | CAV | Not Included | Normal Elec. S-0107 | [6 empty] | was RDC_SB_L0_AT-0006 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_GF_CAV0015 | CAV | Included | Corridor S-0117 | [6 empty] | was RDC_SB_L0_AT-0015 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_GF_CAV0020 | CAV | Included | Storage S-0120B | [6 empty] | was RDC_SB_L0_AT-0020 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_GF_CAV0021 | CAV | Included | Vestibule S-0125 | [6 empty] | was RDC_SB_L0_AT-0021 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_GF_CAV0022 | CAV | Included | Men S-0126 | [6 empty] | was RDC_SB_L0_AT-0022 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_GF_CAV0023 | CAV | Included | Women S-0127 | [6 empty] | was RDC_SB_L0_AT-0023 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_GF_CAV0024 | CAV | Not Included | NORM. ELEC. S-0129 | [6 empty] | was RDC_SB_L0_AT-0024 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_CAV4315_EV4316 | CAV | Included | Vestibule N-0270A | [6 empty] | was RDC_NB_GF_AT-4315 - the historian carries the assembly, not the terminal; room kept from its 2 part row(s) | RDC
RDC_NB_GF_CAV5160_EV5161 | CAV | Included | [7 empty] | was RDC_NB_GF_AT-5160 - the historian carries the assembly, not the terminal; its parts named 2 different rooms - left blank | RDC
RDC_NB_GF_CAV5280 | CAV | Included | Serv Core N-0136 | [6 empty] | was RDC_NB_GF_AT-5280 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_CAV5290_EV5291 | CAV | Included | Pantry N-0148 | [6 empty] | was RDC_NB_GF_AT-5290 - the historian carries the assembly, not the terminal; room kept from its 2 part row(s) | RDC
RDC_NB_GF_CAV5320 | CAV | Included | Office N-0154 | [6 empty] | was RDC_NB_GF_AT-5320 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_CAV5350 | CAV | Included | Open Office N-0160 | [6 empty] | was RDC_NB_GF_AT-5350 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_CAV5375 | CAV | Included | Open Office N-0165 | [6 empty] | was RDC_NB_GF_AT-5375 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV5026 | EAV | Included | Corridor N-0110 | [6 empty] | was RDC_NB_GF_EV-5026 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV5163 | EAV | Not Included | IDF N-0133 | [6 empty] | was RDC_NB_GF_EV-5163 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_VEV-5052A | VEV | Not Included | Analytical Core Lab 1 N-0114A | [7 empty] | RDC
RDC_NB_GF_VEV-5052B | VEV | Not Included | Analytical Core Lab 1 N-0114A | [7 empty] | RDC
RDC_NB_GF_FEV-5053 | FEV | Not Included | Analytical Core Lab 1 N-0114A | [7 empty] | RDC
RDC_NB_GF_VEV-5055 | VEV | Not Included | Analytical Core Lab 1 N-0114A | [7 empty] | RDC
RDC_NB_GF_FEV-5062 | FEV | Not Included | Clean Lab N-0114B | [7 empty] | RDC
RDC_NB_GF_VEV-5071 | VEV | Not Included | Dirty Lab N-0114C | [7 empty] | RDC
RDC_NB_GF_FEV-5072 | FEV | Not Included | Dirty Lab N-0114C | [7 empty] | RDC
RDC_NB_GF_FEV-5073 | FEV | Not Included | Dirty Lab N-0114C | [7 empty] | RDC
RDC_NB_GF_FEV-5074 | FEV | Not Included | Dirty Lab N-0114C | [7 empty] | RDC
RDC_NB_GF_FEV-5082 | FEV | Not Included | Bio Analyt N-0114D | [7 empty] | RDC
RDC_NB_GF_FEV-5083 | FEV | Not Included | Bio Analyt N-0114D | [7 empty] | RDC
RDC_NB_GF_VEV-5092 | VEV | Not Included | Air Quality N-0114F | [7 empty] | RDC
RDC_NB_GF_FEV-5093 | FEV | Not Included | Air Quality N-0114F | [7 empty] | RDC
RDC_NB_GF_FEV-5094 | FEV | Not Included | Air Quality N-0114F | [7 empty] | RDC
RDC_NB_GF_FEV-5095A | FEV | Not Included | Air Quality N-0114F | [7 empty] | RDC
RDC_NB_GF_FEV-5095B | FEV | Not Included | Air Quality N-0114F | [7 empty] | RDC
RDC_NB_GF_VEV-5182A | VEV | Not Included | Analyt Core-2 N-0140A | [7 empty] | RDC
RDC_NB_GF_VEV-5182B | VEV | Not Included | Analyt Core-2 N-0140A | [7 empty] | RDC
RDC_NB_GF_FEV-5183 | FEV | Not Included | Analytical Core Lab 2 N-0140A | [7 empty] | RDC
RDC_NB_GF_FEV5192A | FEV | Not Included | Furnace Room N-0140B | [6 empty] | was RDC_NB_GF_VEV-5192a - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_FEV5192B | FEV | Not Included | Furnace Room N-0140B | [6 empty] | was RDC_NB_GF_VEV-5192b - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_FEV-5203 | FEV | Not Included | Prep Lab N-0140C | [7 empty] | RDC
RDC_NB_GF_VEV-5211 | VEV | Not Included | MBE EVAP Room N-0140E | [7 empty] | RDC
RDC_NB_GF_VEV-5221 | VEV | Not Included | MBE/Evap Room N-0140E | [7 empty] | RDC
RDC_NB_GF_FEV-5222 | FEV | Not Included | Evap Room N-0140E | [7 empty] | RDC
RDC_NB_GF_FEV-5223 | FEV | Not Included | Evap Room N-0140E | [7 empty] | RDC
RDC_NB_GF_VEV-5231 | VEV | Not Included | ALD Room N-0140F | [7 empty] | RDC
RDC_NB_GF_CAV5240_CEV5241 | CAV | Not Included | Air Lock N-0140G | [6 empty] | was RDC_NB_GF_CEV-5241 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_FEV-5271 | FEV | Not Included | Org Chem N-0140K | [7 empty] | RDC
RDC_NB_GF_FEV-5272 | FEV | Not Included | Org Chem N-0140K | [7 empty] | RDC
RDC_NB_GF_FEV-5273 | FEV | Not Included | Org Chem N-0140K | [7 empty] | RDC
RDC_NB_GF_FEV-5274 | FEV | Not Included | Org Chem N-0140K | [7 empty] | RDC
RDC_NB_GF_FEV-5275 | FEV | Not Included | Org Chem N-0140K | [7 empty] | RDC
RDC_NB_GF_FEV-5276 | FEV | Not Included | Org Chem N-0140K | [7 empty] | RDC
RDC_NB_GF_FEV-5277 | FEV | Not Included | Org Chem N-0140K | [7 empty] | RDC
RDC_SB_GF_CAV0004 | CAV | Included | Corridor S-0104 | [6 empty] | was RDC_SB_L0_AT-0004 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_GF_CAV0005 | CAV | Included | Men S-0105 | [6 empty] | was RDC_SB_L0_AT-0005 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_GF_CAV2001 | CAV | Included | [7 empty] | was RDC_SB_L0_A1.2_AT-2001 - the historian carries the assembly, not the terminal; its parts named 2 different rooms - left blank | RDC
RDC_NB_GF_CAV5005 | CAV | Included | Vestibule N-0105 | [6 empty] | was RDC_NB_GF_AT-5005 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_CAV5020_EV5021 | CAV | Included | Mens + Vestibule + N-0109 N-0108 | [6 empty] | was RDC_NB_GF_AT-5020 - the historian carries the assembly, not the terminal; room kept from its 2 part row(s) | RDC
RDC_NB_GF_CAV6005 | CAV | Included | Vestibule N-0302 | [6 empty] | was RDC_NB_GF_AT-6005 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_CAV6015_EV6016 | CAV | Included | Men N-0306 | [6 empty] | was RDC_NB_GF_AT-6015 - the historian carries the assembly, not the terminal; room kept from its 2 part row(s) | RDC
RDC_NB_GF_CAV6020 | CAV | Included | Vestibule N-0308 | [6 empty] | was RDC_NB_GF_AT-6020 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV6127 | EAV | Not Included | IDF N-0311 | [6 empty] | was RDC_NB_GF_EV-6127 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_CAV7005_EV7006 | CAV | Included | WOMEN N-0402 | [6 empty] | was RDC_NB_GF_AT-7005 - the historian carries the assembly, not the terminal; room kept from its 2 part row(s) | RDC
RDC_NB_GF_CAV7380_EV7381 | CAV | Not Included | Pipe Chase N-0443B | [6 empty] | was RDC_NB_GF_AT-7380 - the historian carries the assembly, not the terminal; room kept from its 2 part row(s) | RDC
RDC_NB_GF_CAV6280_EV6281 | CAV | Included | Pantry N-0356 | [6 empty] | was RDC_NB_GF_AT-6280 - the historian carries the assembly, not the terminal; room kept from its 2 part row(s) | RDC
RDC_NB_GF_EAV6141 | EAV | Included | Workstation N-0317 | [6 empty] | was RDC_NB_GF_EV-6141 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV6156 | EAV | Included | Workstation N-0320 | [6 empty] | was RDC_NB_GF_EV-6156 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV6176 | EAV | Included | Workstation N-0324 | [6 empty] | was RDC_NB_GF_EV-6176 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV6356 | EAV | Included | Office 05-8-WKS N-0372 | [6 empty] | was RDC_NB_GF_EV-6356 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV6381 | EAV | Included | Office 05-8-WKS N-0378 | [6 empty] | was RDC_NB_GF_EV-6381 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV6401 | EAV | Included | Office 05-8-WKS N-0381 | [6 empty] | was RDC_NB_GF_EV-6401 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV7091 | EAV | Included | Office N-0412A | [6 empty] | was RDC_NB_GF_EV-7091 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV7106 | EAV | Included | Office N-0415A | [6 empty] | was RDC_NB_GF_EV-7106 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV7121 | EAV | Included | Office 05-4-WS N-0418 | [6 empty] | was RDC_NB_GF_EV-7121 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV7122 | EAV | Not Included | IDF Room N-0419 | [6 empty] | was RDC_NB_GF_EV-7122 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV7396 | EAV | Included | Office 05-8-WKS N-0446 | [6 empty] | was RDC_NB_GF_EV-7396 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV7426 | EAV | Included | Office 05-8-WKS N-0452 | [6 empty] | was RDC_NB_GF_EV-7426 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV7461 | EAV | Included | Office 05-8-WKS N-0457 | [6 empty] | was RDC_NB_GF_EV-7461 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_EAV7486 | EAV | Included | Office 05-8-WKS N-0462 | [6 empty] | was RDC_NB_GF_EV-7486 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_GF_VEV-7022A | VEV | Not Included | NMR Lab N-0404A | [7 empty] | RDC
RDC_NB_GF_VEV-7022B | VEV | Not Included | NMR Lab N-0404A | [7 empty] | RDC
RDC_NB_GF_VEV-7023A | VEV | Not Included | NMR Lab N-0404A | [7 empty] | RDC
RDC_NB_GF_VEV-7023B | VEV | Not Included | NMR Lab N-0404A | [7 empty] | RDC
RDC_NB_GF_VEV-7024A | VEV | Not Included | NMR Lab N-0404A | [7 empty] | RDC
RDC_NB_GF_VEV-7024B | VEV | Not Included | NMR Lab N-0404A | [7 empty] | RDC
RDC_NB_GF_FEV-7052 | FEV | Not Included | EM Prep 1 - MAT N-0404D | [7 empty] | RDC
RDC_NB_GF_FEV-7053 | FEV | Not Included | EM Prep 1 - MAT N-0404D | [7 empty] | RDC
RDC_NB_GF_FEV-7062 | FEV | Not Included | EM Prep 2 - BIO N-0404E | [7 empty] | RDC
RDC_NB_GF_VEV-7072A | VEV | Not Included | Surf Analysis Lab N-0404F | [7 empty] | RDC
RDC_NB_GF_VEV-7072B | VEV | Not Included | Surf Analysis Lab N-0404F | [7 empty] | RDC
RDC_NB_GF_VEV-7073 | VEV | Not Included | Surf Analysis Lab N-0404F | [7 empty] | RDC
RDC_NB_GF_FEV-7074 | FEV | Not Included | Surf Analysis Lab N-0404F | [7 empty] | RDC
RDC_NB_GF_FEV-7075 | FEV | Not Included | Surf Analysis Lab N-0404F | [7 empty] | RDC
RDC_NB_GF_FEV-7232 | FEV | Not Included | Inter Lab N-0442A | [7 empty] | RDC
RDC_NB_GF_VEV-7241B | VEV | Not Included | Optical Lab N-0442B | [7 empty] | RDC
RDC_NB_GF_VEV-7301 | VEV | Not Included | A/L 1 N-0442H | [7 empty] | RDC
RDC_SB_1F_CAV1504 | CAV | Included | Corridor S-1122 | [6 empty] | was RDC_SB_1F_AT-1504 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV1535 | CAV | Included | Pantry S-1149A | [6 empty] | was RDC_SB_1F_AT-1535 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV1537 | CAV | Not Included | Normal Elec. S-1147 | [6 empty] | was RDC_SB_1F_AT-1537 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV4500 | EAV | Not Included | MDF N-1201 | [6 empty] | was RDC_NB_1F_EV-4500 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_CEV-4502 | CEV | Included | Corridor N-1202 | [7 empty] | RDC
RDC_NB_1F_EAV4661 | EAV | Included | Office 05 - 8 WKS- N-1227 | [6 empty] | was RDC_NB_1F_EV-4661 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV4686 | EAV | Included | Office 05 - 8 WKS- N-1232 | [6 empty] | was RDC_NB_1F_EV-4686 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV4711 | EAV | Included | Office 05 - 8 WKS- N-1237 | [6 empty] | was RDC_NB_1F_EV-4711 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV4736 | EAV | Included | Office 05 - 8 WKS- N-1242 | [6 empty] | was RDC_NB_1F_EV-4736 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_VEV-4602 | VEV | Not Included | Testing Room N-1216B | [7 empty] | RDC
RDC_NB_1F_FEV-4603 | FEV | Not Included | Testing Room N-1216B | [7 empty] | RDC
RDC_NB_1F_FEV-4604 | FEV | Not Included | Testing Room N-1216B | [7 empty] | RDC
RDC_NB_1F_FEV-4605 | FEV | Not Included | Testing Room N-1216B | [7 empty] | RDC
RDC_NB_1F_FEV-4606 | FEV | Not Included | Testing Room N-1216B | [7 empty] | RDC
RDC_NB_1F_FEV-4622 | FEV | Not Included | EL Shop N-1216C | [7 empty] | RDC
RDC_NB_1F_CAV-4581B | CAV | Not Included | Photovoltaic Lab N-1216A | [7 empty] | RDC
RDC_NB_1F_VEV-4585A | VEV | Not Included | Photovoltaic Lab N-1216A | [7 empty] | RDC
RDC_NB_1F_VEV-4585B | VEV | Not Included | Photovoltaic Lab N-1216A | [7 empty] | RDC
RDC_NB_1F_VEV-4586A | VEV | Not Included | Photovoltaic Lab N-1216A | [7 empty] | RDC
RDC_NB_1F_VEV-4586B | VEV | Not Included | Photovoltaic Lab N-1216A | [7 empty] | RDC
RDC_NB_1F_FEV-4587 | FEV | Not Included | Photovoltaic Lab N-1216A | [7 empty] | RDC
RDC_NB_1F_FEV-4588 | FEV | Not Included | Photovoltaic Lab N-1216A | [7 empty] | RDC
RDC_SB_1F_CAV0501 | CAV | Included | Lobby S-1102 | [6 empty] | was RDC_SB_1F_AT-0501 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV0502 | CAV | Included | Vestibule S-1105 | [6 empty] | was RDC_SB_1F_AT-0502 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV0503 | CAV | Included | Women S-1106B | [6 empty] | was RDC_SB_1F_AT-0503 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV0504 | CAV | Included | Vestibule S-1107 | [6 empty] | was RDC_SB_1F_AT-0504 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV0505 | CAV | Not Included | EMERGENCY Elec. S-1107B | [6 empty] | was RDC_SB_1F_AT-0505 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV0515 | CAV | Included | Corridor S-1122 | [6 empty] | was RDC_SB_1F_AT-0515 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV0516 | CAV | Included | Pantry S-1158 | [6 empty] | was RDC_SB_1F_AT-0516 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV0517 | CAV | Not Included | Normal Elec. S-1160 | [6 empty] | was RDC_SB_1F_AT-0517 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV0524 | CAV | Included | Women S-1169 | [6 empty] | was RDC_SB_1F_AT-0524 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV0525 | CAV | Included | Men S-1170 | [6 empty] | was RDC_SB_1F_AT-0525 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV0534 | CAV | Included | CORRIDOR S-1180 | [6 empty] | was RDC_SB_1F_AT-0534 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV0535 | CAV | Included | Cooridor S-1180 | [6 empty] | was RDC_SB_1F_AT-0535 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_SB_1F_CAV1541 | CAV | Included | Cooridor S-1181 | [6 empty] | was RDC_SB_1F_AT-1541 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_CAV5720_EV5721 | CAV | Included | Men N-1134 | [6 empty] | was RDC_NB_1F_AT-5720 - the historian carries the assembly, not the terminal; room kept from its 2 part row(s) | RDC
RDC_NB_1F_CAV5750 | CAV | Included | Store N-1141 | [6 empty] | was RDC_NB_1F_AT-5750 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_CAV4640_EV4641 | CAV | Included | Women N-1221 | [6 empty] | was RDC_NB_1F_AT-4640 - the historian carries the assembly, not the terminal; room kept from its 2 part row(s) | RDC
RDC_NB_1F_EAV5686 | EAV | Included | Corridor N-1126 | [6 empty] | was RDC_NB_1F_EV-5686 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV5747 | EAV | Not Included | IDF N-1140 | [6 empty] | was RDC_NB_1F_EV-5747 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV5891 | EAV | Included | Office 05 - 8 WKS- North N-1160 | [6 empty] | was RDC_NB_1F_EV-5891 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV5921 | EAV | Included | Office 05 - 8 WKS- N-1168 | [6 empty] | was RDC_NB_1F_EV-5921 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV5941 | EAV | Included | Office 05 - 8 WKS- N-1165 | [6 empty] | was RDC_NB_1F_EV-5941 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_FEV-5624 | FEV | Not Included | Robotics N-1115J | [7 empty] | RDC
RDC_NB_1F_VEV-5572 | VEV | Not Included | Met/Prot Lab N-1115C | [7 empty] | RDC
RDC_NB_1F_VEV-5573A | VEV | Not Included | Met/Prot Lab N-1115C | [7 empty] | RDC
RDC_NB_1F_VEV-5573B | VEV | Not Included | Met/Prot Lab N-1115C | [7 empty] | RDC
RDC_NB_1F_FEV-5574 | FEV | Not Included | PRe-PCR N-1115B | [7 empty] | RDC
RDC_NB_1F_FEV-5575 | FEV | Not Included | Cell Culture N-1115E | [7 empty] | RDC
RDC_NB_1F_VEV-5591 | VEV | Not Included | Cell Culture N-1115E | [7 empty] | RDC
RDC_NB_1F_FEV-5772 | FEV | Not Included | Histology N-1144A | [7 empty] | RDC
RDC_NB_1F_VEV-5791 | VEV | Not Included | Culture & Gel Rm N-1144B | [7 empty] | RDC
RDC_NB_1F_VEV-5795B | VEV | Included | PRE-PCR N-1144D | [7 empty] | RDC
RDC_NB_1F_FEV-5796 | FEV | Not Included | PRE-PCR N-1144D | [7 empty] | RDC
RDC_NB_1F_VEV-5811A | VEV | Not Included | Nano Lab N-1144E | [7 empty] | RDC
RDC_NB_1F_VEV-5811B | VEV | Not Included | Nano Lab N-1144E | [7 empty] | RDC
RDC_NB_1F_FEV-5812 | FEV | Not Included | Nano Lab N-1144E | [7 empty] | RDC
RDC_NB_1F_FEV-5813 | FEV | Not Included | Nano Lab N-1144E | [7 empty] | RDC
RDC_NB_1F_VEV-5821 | VEV | Not Included | Nano Lab N-1144E | [7 empty] | RDC
RDC_SB_1F_CAV2507 | CAV | Included | Female S-1204 | [6 empty] | was RDC_SB_1F_AT-2507 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_CAV6740_EV6741 | CAV | Included | Men N-1340 | [6 empty] | was RDC_NB_1F_AT-6740 - the historian carries the assembly, not the terminal; room kept from its 2 part row(s) | RDC
RDC_NB_1F_CAV7500_EV7501 | CAV | Included | Women N-1403 | [6 empty] | was RDC_NB_1F_AT-7500 - the historian carries the assembly, not the terminal; room kept from its 2 part row(s) | RDC
RDC_NB_1F_EAV6661 | EAV | Included | Workstation N-1321 | [6 empty] | was RDC_NB_1F_EV-6661 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV6676 | EAV | Included | Workstation N-1324 | [6 empty] | was RDC_NB_1F_EV-6676 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV6691 | EAV | Included | Exp. Workstation N-1327 | [6 empty] | was RDC_NB_1F_EV-6691 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV6936 | EAV | Included | Workstation N-1363 | [6 empty] | was RDC_NB_1F_EV-6936 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV6961 | EAV | Included | Workstation N-1368 | [6 empty] | was RDC_NB_1F_EV-6961 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV6969 | EAV | Included | Workstation N-1371 | [6 empty] | was RDC_NB_1F_EV-6969 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_VEV-6541 | VEV | Not Included | TC1 N-1316B | [7 empty] | RDC
RDC_NB_1F_VEV-6552 | VEV | Not Included | Gene Therapy Lab N-1316C | [7 empty] | RDC
RDC_NB_1F_VEV-6553 | VEV | Not Included | Gene Therapy Lab N-1316C | [7 empty] | RDC
RDC_NB_1F_FEV-6554 | FEV | Not Included | Gene Therapy Lab N-1316C | [7 empty] | RDC
RDC_NB_1F_FEV-6555 | FEV | Not Included | Gene Therapy Lab N-1316C | [7 empty] | RDC
RDC_NB_1F_CEV-6581 | CEV | Not Included | TC3 N-1316F | [7 empty] | RDC
RDC_NB_1F_FEV-6602 | FEV | Not Included | Analytical Core N-1316H | [7 empty] | RDC
RDC_NB_1F_FEV-6632 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_FEV-6633 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_FEV-6634 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_FEV-6635 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_FEV-6636 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_FEV-6637 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_FEV-6638 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_FEV-6639 | FEV | Not Included | Bio-Med Chem Lab 1 N-1316L | [7 empty] | RDC
RDC_NB_1F_FEV-6731 | FEV | Included | SERIVICE CORRRIDOR N-1337 | [7 empty] | RDC
RDC_NB_1F_VEV-6751 | VEV | Not Included | TC1 N-1345A | [7 empty] | RDC
RDC_NB_1F_VEV-6762 | VEV | Not Included | Diabetes Lab / Open Lab N-1345B | [7 empty] | RDC
RDC_NB_1F_VEV-6763 | VEV | Not Included | Diabetes Lab / Open Lab N-1345B | [7 empty] | RDC
RDC_NB_1F_FEV-6764 | FEV | Not Included | Diabetes Lab / Open Lab N-1345B | [7 empty] | RDC
RDC_NB_1F_FEV-6765 | FEV | Not Included | Diabetes Lab / Open Lab N-1345B | [7 empty] | RDC
RDC_NB_1F_FEV-6766 | FEV | Not Included | Diabetes Lab / Open Lab N-1345B | [7 empty] | RDC
RDC_NB_1F_CAV6790_CEV6791 | CAV | Not Included | TC2 N-1345C | [6 empty] | was RDC_NB_1F_CEV-6791 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_FEV-6852 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J | [7 empty] | RDC
RDC_NB_1F_FEV-6853 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J | [7 empty] | RDC
RDC_NB_1F_FEV-6854 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J | [7 empty] | RDC
RDC_NB_1F_FEV-6855 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J | [7 empty] | RDC
RDC_NB_1F_FEV-6856 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J | [7 empty] | RDC
RDC_NB_1F_FEV-6857 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J | [7 empty] | RDC
RDC_NB_1F_FEV-6858 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J | [7 empty] | RDC
RDC_NB_1F_FEV-6859 | FEV | Not Included | Bio-Med Chem Lab 2 N-1345J | [7 empty] | RDC
RDC_NB_1F_EAV7631 | EAV | Included | Office 05 - 2 WKS- N-1407 | [6 empty] | was RDC_NB_1F_EV-7631 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV7646 | EAV | Included | Exp. Workstation N-1420 | [6 empty] | was RDC_NB_1F_EV-7646 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV7661 | EAV | Included | Office 05 - 2 WKS- N-1401 | [6 empty] | was RDC_NB_1F_EV-7661 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV7663 | EAV | Not Included | IDF N-1424 | [6 empty] | was RDC_NB_1F_EV-7663 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV7711 | EAV | Included | Workstation N-1442 | [6 empty] | was RDC_NB_1F_EV-7711 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV7712 | EAV | Included | Workstation N-1442 | [6 empty] | was RDC_NB_1F_EV-7712 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV7861 | EAV | Included | Office 05 - 9 WKS N-1461 | [6 empty] | was RDC_NB_1F_EV-7861 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_EAV7916 | EAV | Included | Office 05 - 8 WKS N-1471 | [6 empty] | was RDC_NB_1F_EV-7916 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_CAV7520_CEV7521 | CAV | Not Included | Isotope N-1404B | [6 empty] | was RDC_NB_1F_CEV-7521 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_FEV-7522 | FEV | Not Included | Isotope N-1404B | [7 empty] | RDC
RDC_NB_1F_CAV7590_CEV7591 | CAV | Not Included | HY Room N-1404J | [6 empty] | was RDC_NB_1F_CEV-7591 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_FEV-7602 | FEV | Not Included | CELL BIO LABS N-1404K | [7 empty] | RDC
RDC_NB_1F_CAV7610_CEV7611 | CAV | Not Included | TC1 N-1404L | [6 empty] | was RDC_NB_1F_CEV-7611 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_CAV7760_CEV7761 | CAV | Not Included | A/L N-1450D | [6 empty] | was RDC_NB_1F_CEV-7761 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_CAV7790_CEV7791 | CAV | Not Included | A/L N-1450G | [6 empty] | was RDC_NB_1F_CEV-7791 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_1F_FEV-7824 | FEV | Not Included | STEM/PCR Open Lab N-1450M | [7 empty] | RDC
RDC_NB_2F_EAV4920 | EAV | Not Included | IDF N-2104 | [6 empty] | was RDC_NB_2F_EV-4920 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
RDC_NB_2F_EAV6981 | EAV | Not Included | IDF N-2110 | [6 empty] | was RDC_NB_2F_EV-6981 - the historian carries the assembly, not the terminal; room kept from its 1 part row(s) | RDC
Note on D835: Ahmad Sharaf Al Masri: HMI reads 56.3 C on IMG_9601.jpeg - by far the highest reading seen across all QNL drawings, against 19.6 C on FCU-1F-058 directly beneath it. Almost certainly a failed sensor; worth raising with the BMS team.
Note on D878: Ahmad Sharaf Al Masri: IMG_9592.jpeg (Basement Zone-3-P2): FCU-B-001 is drawn outside the plan outline on the left with no leader line to any room. Nearest labels are 'IDF Rooom' and 'VIP Restroom', both of which would make this Not Included (technical / executive). Key Plan name used per the agreed rule - please confirm.
Note on D915: Ahmad Sharaf Al Masri: FCU-B-038 shows '??????' instead of a temperature on the HMI (no sensor reading). Room name taken from its yellow leader line pointing into the Pantry.
Note on D945: Ahmad Sharaf Al Masri: HMI reads 34.1 C on IMG_9599.jpeg - well above the ~17-20 C of the adjacent media studios. Consistent with an unconditioned store, but worth checking.
Note on D1091: Ahmad Sharaf Al Masri: CONFLICT: previously recorded as 'Plant Room 1 / Plant Room 2 (IMG_9588.jpeg)', Not Included. Honeywell BMS VAV Summary Type-01 (IMG_9563.jpeg) groups VAV/B/S11/022 (Master) and /023 (Slave) together under 'Basement Zone 1 Corridor Leading To Reception & Lounge B009'. Updated to match the BMS and changed to Included. Verify against the basement drawing before final sign-off.
Note on D1127: Ahmad Sharaf Al Masri: HMI label on IMG_9589.jpeg reads 'VAV-B-S11-005'. Positionally it sits between VAV-B-S14-004 and VAV-B-S14-006 in the Digitization Room, and VAV_B_S11_005 (row 1075) is already assigned to Tech, Services & Collections Office from IMG_9587.jpeg. Recorded here as S14_005 - please confirm the correct HMI tag.
Note on D1159: Ahmad Sharaf Al Masri: Flagged for the executive-room rule, not for the room name. 'Asst. Head' is a management office - confirm whether it counts as an executive room (Not Included) or a senior staff office (currently Included).
Note on D1160: Ahmad Sharaf Al Masri: Flagged for the executive-room rule, not for the room name. 'Asst. Head' is a management office - confirm whether it counts as an executive room (Not Included) or a senior staff office (currently Included).
Note on D1219: Ahmad Sharaf Al Masri: No B083 in the room-name list supplied (list jumps B082 TRANSFORMER ROOM to B084 UPS BATTERY ROOM). Name needed.
Note on D1220: Ahmad Sharaf Al Masri: No B083 in the room-name list supplied (list jumps B082 TRANSFORMER ROOM to B084 UPS BATTERY ROOM). Name needed.
Note on D1231: Ahmad Sharaf Al Masri: No B045 / B045A in the room-name list supplied. Name needed.
Note on D1232: Ahmad Sharaf Al Masri: No B045 / B045A in the room-name list supplied. Name needed.
Note on D1233: Ahmad Sharaf Al Masri: No B045 / B045A in the room-name list supplied. Name needed.
Note on D1235: Ahmad Sharaf Al Masri: DX/RP/21 is a Roof unit (Zone C) — no room number on HMI.
Note on D1236: Ahmad Sharaf Al Masri: Ambiguous: list has two B106 entries - 'REST ROOM SECURITY B106_RES' and 'SECURITY STORES SECURITY UPS B106_SEC'. Confirm which applies to DX_B22.
Note on D1238: Ahmad Sharaf Al Masri: DX/RP/21 is a Roof unit (Zone C) — no room number on HMI.
Note on D1293: Ahmad Sharaf Al Masri: Ambiguous: list has two B141 entries - 'HL PLANT ROOM B141_HLP' and 'VAULT B141_VAU'. Confirm which applies to CCU_B08.
Note on D1294: Ahmad Sharaf Al Masri: Ambiguous: list has two B141 entries - 'HL PLANT ROOM B141_HLP' and 'VAULT B141_VAU'. Confirm which applies to CCU_B09.
Note on D1610: Ahmad Sharaf Al Masri: Corrected from Emergency Elec. N-0333. B2.1 places AT-6205/EV-6206 (20.8 C) at Conference N-0331 and AT-6220/EV-6221 (18.1 C) at Emergency Elec. N-0333 - the two rows were swapped. Temperatures support it: 18.1 C is an electrical room, 20.8 C an occupied conference room.
Note on D1612: Ahmad Sharaf Al Masri: Corrected from Conf N-0331 - swapped with row 1463. See note on D1463.
Note on D1632: Ahmad Sharaf Al Masri: Corrected from Office N-0376. B2.1 places AT-6380 (22.9 C) at Workstation N-0378 and AT-6370 (23.3 C) at Office N-0376; N-0376 is now held by VAV6370 (row 1483).
Note on D1664: Ahmad Sharaf Al Masri: Corrected from Office N-0427, which duplicated row 1518. B2.2 places AT-7145 (22.9 C) at Office N-0425 and AT-7155 (21.1 C) at Office N-0427.
Note on D1666: Ahmad Sharaf Al Masri: Corrected from Office N-0428. B2.2 places AT-7165 (20.5 C) at Office N-0429; no room N-0428 appears on the Level 0 drawing.
Note on D1670: Ahmad Sharaf Al Masri: Corrected from Office N-0426. B2.2 places AT-7185/EV-7186 at Emer. Elec. Room N-0433 - it reads 15.0 C, consistent with an electrical room, not an office.
Note on D1715: Ahmad Sharaf Al Masri: Resolved by elimination, NOT read directly off a drawing. VAV0509 was the only unassigned VAV row in the South Building Level 1 block and NCIR Office S-1115 the only unassigned room in the AT-0510/0511/0512/0513/0514 group (S-1115A, S-1116, S-1117, S-1118, S-1119). B1.1 shows a sensor inside S-1115 labelled AT-0503, but A1.3 - the dedicated close-up of that core - places AT-0503 at Women S-1106B in a clean 0502/0503/0505 -> S-1105/S-1106B/S-1107B sequence. Most likely the B1.1 graphic is mislabelled and that sensor is AT-0509. VERIFY AGAINST THE BMS POINT LIST before relying on this row.
Note on D2034: Ahmad Sharaf Al Masri: Corrected from Office N-1126. A2.2 labels N-1126 as CORRIDOR (the label appears twice along the corridor run); AT-5685/EV-5686 sit on that corridor, not in an office.
Note on D2055: Ahmad Sharaf Al Masri: Corrected from Office N-1163, which duplicated row 1923. On A2.2 the bottom office band has exactly 17 tags for 17 rooms (AT-5860 to AT-5940), all accounted for; AT-5840 is the extra tag and sits above the band on the Corridor N-1150 run beside EV-5941. N-1163 is held by VAV5905 (row 1923).
Note on D2181: Ahmad Sharaf Al Masri: Corrected from Flow Cyto N-1450C, which duplicated row 2034. B2.2 (Level 1) places VEV-7781 at iPS-TC N-1450F and VEV-7751 at Flow Cyto N-1450C.
Note on D2218: Ahmad Sharaf Al Masri: Corrected from Corridor N-1138. On A2.2 FCU-5983 and FCU-5984 are adjacent boxes serving the JC N-1139 / IDF N-1140 pair; Corridor N-1138 is further west where AT-5745 sits.
Note on D2219: Ahmad Sharaf Al Masri: Corrected from Corridor N-1138. On A2.2 FCU-5983 and FCU-5984 are adjacent boxes serving the JC N-1139 / IDF N-1140 pair; Corridor N-1138 is further west where AT-5745 sits.
Note on D2264: Ahmad Sharaf Al Masri: Corrected from Stair 5 N-0STO5. B2.2 (Level 0) places FCU-7981 (20.9 C) at IDF N-0419; Stair 5 N-0ST05 is served by FCU-7993 (26.5 C on the same drawing), appended at row 2631.
Note on D2265: Ahmad Sharaf Al Masri: Corrected from Service Corridor N-0344. B2.2 (Level 0) places FCU-7982 (21.2 C) at Mech/FPC N-0434, directly below FCU-7981.
Note on D2273: Ahmad Sharaf Al Masri: From B1.1 (South Building Level 1): FCU-0502 (21.3 C) sits beside FPC S-1108 / Service Vestibule S-1105.
Note on D2274: Ahmad Sharaf Al Masri: From B1.1 (South Building Level 1): FCU-0503 (20.9 C) sits beside Normal Elec. Room S-1107C / UPS S-1107D.
Note on D2316: Ahmad Sharaf Al Masri: BMS screen shows the room name as "IDF-S-0271"; written as "IDF ROOM" for consistency with the other IDF entries.
Note on D2318: Ahmad Sharaf Al Masri: BMS screen shows the room name as "STAIR-OST04"; written as "STAIR-04" for consistency with the other stair entries.
Note on D2333: Ahmad Sharaf Al Masri: BMS screen shows no room number for FCU-8502/8503/8504/8505 (merged room-name cell).
Note on D2487: Ahmad Sharaf Al Masri: CONFLICT between drawings. A1.3 (close-up of the Level 1 core) places AT-0503 at Women S-1106B, forming a clean sequence with AT-0502 -> Vestibule S-1105 and AT-0505 -> Emergency Elec. S-1107B. B1.1 instead shows a sensor labelled AT-0503 reading 22.5 C inside NCIR Office S-1115. A1.3 was taken as authoritative; the S-1115 sensor is most likely AT-0509 (see note on D1569). Verify against the BMS point list.

## Room name changes
ROOM NAMES REWRITTEN BY THIS PASS
Building | Tag No. | Room before | Room after | Source
HQ | AHU12_0001 | HQ RF | RF.001 ROOF | D->E
HQ | AHU12_0002 | HQ RF | RF.001 ROOF | D->E
HQ | AHU12_0003 | HQ RF | RF.001 ROOF | D->E
HQ | AHU12_0004 | HQ RF | RF.001 ROOF | D->E
HQ | AHU12_0006 | HQ RF | RF.001 ROOF | D->E
HQ | AHU12_0007 | HQ RF | RF.001 ROOF | D->E
HQ | AHU12_0008 | HQ RF | RF.001 ROOF | D->E
HQ | AHU12_0009 | HQ RF | RF.001 ROOF | D->E
HQ | AHU12_0010 | HQ RF | RF.001 ROOF | D->E
HQ | AHU2_0001 | SPA PLANT ROOM 2.302 | 2.302 SPA PLANT ROOM | D
HQ | AHU5_0001 | PLANT ROOM 5.301 | 5.301 PLANT ROOM | D
HQ | AHU5_0002 | PLANT ROOM 5.301 | 5.301 PLANT ROOM | D
HQ | AHU9_0001 | PLANT ROOM 9.111 | 9.111 PLANT ROOM | D
HQ | AHU9_0002 | PLANT ROOM 9.111 | 9.111 PLANT ROOM | D
HQ | AHU9_0003 | AHU ROOM 9.109 | 9.109 AHU ROOM | D
HQ | AHUB_0001 | B.001 | B1.001 AHU 4 | D->E
HQ | AHUB_0002 | B.001 | B1.001 AHU 4 | D->E
HQ | AHUB_0003 | B.006 | B1.006 AHU 1 | D->E
HQ | AHUB_0004 | B.006 | B1.006 AHU 1 | D->E
HQ | AHUB_0005 | B.016 | B1.016 AHU 2 | D->E
HQ | AHUB_0006 | B.016 | B1.016 AHU 2 | D->E
HQ | AHUB_0007 | B.022 | B1.022 AHU 3 | D->E
HQ | AHUB_0008 | B.001 | B1.001 AHU 4 | D->E
HQ | AHUB_0009 | B.019 | B1.019 AHU | D->E
HQ | AHUB_0010 | B.019 | B1.019 AHU | D->E
HQ | AHUB_0011 | B.019 | B1.019 AHU | D->E
HQ | FCU0001 | IDF ROOM B.512 | B1.512 IDF ROOM | D
HQ | FCU0002 | SECURITY CONTROL B.003 | B1.003 CONTROL ROOM | D->E
HQ | FCU0003 | DOCK MASTER OFFICE B.107 | B1.107 DOCK MASTER OFFICE | D
HQ | FCU0004 | HH SECURITY B.113 | B1.116 SHEIKHA LOBBY | J
HQ | FCU0005 | MALE TOILET B.401 | B1.003 CONTROL ROOM | H
HQ | FCU0006 | ROOM B.122 | B1.122 SUPPORT SPACE FOOD STORAGE | D->E
HQ | FCU0007 | ROOM B.123 | B1.123 SUPPORT SPACE FOOD STORAGE | D->E
HQ | FCU0008 | ROOM B.014 | B1.015 SUPPORT SPACE LOADING | H
HQ | FCU0009 | ROOM B.014 | B1.014 SUPPORT SPACE DRY WASTE STORAGE | D->E
HQ | FCU0010 | ROOM B.124 | B1.124 WASTE BIN WASH UP | H
HQ | FCU0011 | CHAUFFEUR ROOM B.117 | B1.117 CHAUFFER ROOM | J
HQ | FCU0012 | IDF ROOM G.531 | G.531 IDF ROOM | D
HQ | FCU0013 | IDF ROOM G.531 | G.531 IDF ROOM | J
HQ | FCU0014 | IDF ROOM G.512 | G.512 IDF ROOM | D
HQ | FCU0015 | NURSERY CONSULT. G.031 | G.031 PR AND MARKET STAFF | D->E
HQ | FCU0016 | COPY PRINT G.017 | G.017 COPY PRINT | D
HQ | FCU0017 | CONTROL CENTER G.005 | G.005 EMERGENCY CONTROL CENTER | J
HQ | FCU0018 | VESTIBULE G.511 | G.511 VESTIBULE | D
HQ | FCU0019 | IDF ROOM 1.531 | 1.531 IDF ROOM | D
HQ | FCU0020 | IDF ROOM 1.531 | 1.531 IDF ROOM | D
HQ | FCU0021 | IDF ROOM 1.512 | 1.512 IDF ROOM | J
HQ | FCU0022 | PRINT COPY 1.112 | 1.112 PRINT COPY | D
HQ | FCU0023 | IDF ROOM 2.531 | 2.531 IDF ROOM | D
HQ | FCU0024 | IDF ROOM 2.531 | 2.531 IDF ROOM | D
HQ | FCU0025 | TERRACE 2.701 | 2.701 TERRACE | D
HQ | FCU0026 | TERRACE 2.701 | 2.701 TERRACE | D
HQ | FCU0027 | TERRACE 2.701 | 2.701 TERRACE | D
HQ | FCU0028 | PRINT COPY 2.103 | 2.103 PRINT COPY | D
HQ | FCU0029 | SPA LOUNGE BAR 2.207 | 2.207 SPA LOUNGE BAR | D
HQ | FCU0030 | SPA LOUNGE BAR 2.207 | 2.207 SPA LOUNGE BAR | D
HQ | FCU0031 | SPA FITNESS STUDIO 2.208 | 2.208 SPA FITNESS STUDIO | D
HQ | FCU0032 | SPA FITNESS STUDIO 2.208 | 2.208 SPA FITNESS STUDIO | D
HQ | FCU0033 | SPA FITNESS STUDIO 2.208 | 2.208 SPA FITNESS STUDIO | D
HQ | FCU0034 | SPA OFFICE 2.209 | 2.209 SPA OFFICE | D
HQ | FCU0035 | STAFF FEMALE WC 2.210 | 2.210 SPA STAFF WAITING AREA | D->E
HQ | FCU0036 | SPA. FM BEAUTY SALON 2.211 | 2.211 SPA FEMALE BEAUTY SALON | D->E
HQ | FCU0037 | SPA. FM BEAUTY SALON 2.211 | 2.211 SPA FEMALE BEAUTY SALON | D->E
HQ | FCU0038 | SPA FM TREATMENT 2.212 | 2.212 SPA FM TREATMENT 1 | D->E
HQ | FCU0039 | SPA CHANGING ROOM 2.213 | 2.213 SPA CHANGING ROOM | D
HQ | FCU0040 | SPA CHANGING ROOM 2.213 | 2.213 SPA CHANGING ROOM | D
HQ | FCU0041 | SPA FM TREATMENT 2.214 | 2.214 SPA FM TREATMENT 2 | D->E
HQ | FCU0042 | SPA FM TREATMENT 2.215 | 2.215 SPA FM TREATMENT 3 | D->E
HQ | FCU0043 | SPA FM RELAXATION 2.216 | 2.216 SPA FM RELAXATION | D
HQ | FCU0044 | SPA FM RELAXATION 2.216 | 2.216 SPA FM RELAXATION | J
HQ | FCU0045 | SPA MALE RELAXATION 2.201 | 2.201 SPA MALE RELAXATION | D
HQ | FCU0046 | SPA MALE RELAXATION 2.201 | 2.201 SPA MALE RELAXATION | D
HQ | FCU0047 | SPA MALE RELAXATION 2.201 | 2.201 SPA MALE RELAXATION | D
HQ | FCU0048 | SPA MALE TREATMENT 3 2.202 | 2.202 SPA MALE TREATMENT 3 | D
HQ | FCU0049 | SPA MALE TREATMENT 2 2.203 | 2.203 SPA MALE TREATMENT 2 | D
HQ | FCU0050 | SPA MALE TREATMENT 1 2.204 | 2.204 SPA MALE TREATMENT 1 | D
HQ | FCU0051 | MALE CHANGING ROOM 2.205 | 2.205 SPA MALE CHANGING ROOM | D->E
HQ | FCU0052 | MALE CHANGING ROOM 2.205 | 2.205 SPA MALE CHANGING ROOM | D->E
HQ | FCU0053 | SPA ENTRANCE 2.206 | 2.206 SPA ENTRANCE | D
HQ | FCU0054 | SPA LOBBY 2.603 | 2.603 SPA LOBBY | D
HQ | FCU0055 | SPA LOBBY 2.603 | 2.603 SPA LOBBY | D
HQ | FCU0056 | IDF ROOM 2.512 | 2.512 MECHANICAL ROOM | D->E
HQ | FCU0057 | SPA PLANT ROOM 2.302 | 2.302 SPA PLANT ROOM | D
HQ | FCU0058 | SPA PLANT ROOM 2.302 | 2.311 SPA MALE HEAT EXP | J
HQ | FCU0059 | IDF ROOM 3.531 | 3.531 IDF ROOM | J
HQ | FCU0060 | IDF ROOM 3.531 | 3.531 IDF ROOM | D
HQ | FCU0061 | IDF ROOM 3.512 | 3.512 IDF ROOM | J
HQ | FCU0062 | COPY/PRINT 3.203 | 3.203 COPY PRINT | D
HQ | FCU0063 | PRINT COPY 3.103 | 3.103 PRINT COPY | D
HQ | FCU0064 | CORRIDOR BRIDGE 3.63 | 3.630 CORRIDOR BRIDGE | J
HQ | FCU0065 | CORRIDOR BRIDGE 3.63 | 3.630 CORRIDOR BRIDGE | J
HQ | FCU0066 | CORRIDOR BRIDGE 3.63 | 3.630 CORRIDOR BRIDGE | J
HQ | FCU0067 | NORTH EAST ZONE | 5.602 BRIDGE | H
HQ | FCU0068 | NORTH EAST ZONE | 5.602 BRIDGE | H
HQ | FCU0069 | NORTH EAST ZONE | 5.602 BRIDGE | H
HQ | FCU0070 | NORTH EAST ZONE | 5.602 BRIDGE | H
HQ | FCU0071 | IDF ROOM 04.531 | 4.531 IDF ROOM | D
HQ | FCU0072 | IDF ROOM 04.531 | 4.105 PANTRY | J
HQ | FCU0073 | IDF ROOM 04.512 | 4.512 IDF ROOM | J
HQ | FCU0074 | PRINT COPY 05.202 | 4.202 PRINT COPY | J
HQ | FCU0075 | GSM ROOM 05.214 | 4.214 GSM ROOM | J
HQ | FCU0076 | GSM ROOM 05.214 | 4.214 GSM ROOM | J
HQ | FCU0077 | VP ADM TERRACE 04.701 | 4.701 VP ADM TERRACE | D
HQ | FCU0078 | VP ADM TERRACE 04.701 | 4.701 VP ADM TERRACE | D
HQ | FCU0079 | VP ADM TERRACE 04.701 | 4.701 VP ADM TERRACE | D
HQ | FCU0080 | VP ADM TERRACE 04.701 | 4.701 VP ADM TERRACE | D
HQ | FCU0081 | TERRACE 04.702 | 4.702 TERRACE | D
HQ | FCU0082 | TERRACE 04.703 | 4.703 TERRACE | D
HQ | FCU0083 | TERRACE 04.702 | 4.702 TERRACE | D
HQ | FCU0084 | PRINT COPY 04.110 | 4.110 PRINT COPY | D
HQ | FCU0085 | IDF ROOM 5.531 | 5.531 IDF ROOM | J
HQ | FCU0086 | IDF ROOM 5.531 | 5.531 IDF ROOM | J
HQ | FCU0087 | IDF ROOM 5.512 | 5.512 IDF ROOM | J
HQ | FCU0088 | PRINT COPY 5.103 | 5.103 PRINT COPY | D
HQ | FCU0089 | BRIDGE 06.604 | 6.604 BRIDGE CORRIDOR | D->E
HQ | FCU0090 | BRIDGE 06.604 | 6.604 BRIDGE CORRIDOR | D->E
HQ | FCU0091 | BRIDGE 06.604 | 6.604 BRIDGE CORRIDOR | D->E
HQ | FCU0092 | BRIDGE 5.602 | 5.602 BRIDGE | D
HQ | FCU0093 | BRIDGE 5.602 | 5.602 BRIDGE | D
HQ | FCU0094 | BRIDGE 5.602 | 5.602 BRIDGE | D
HQ | FCU0095 | BRIDGE 5.602 | 5.602 BRIDGE | D
HQ | FCU0096 | IDF ROOM 06.531 | 6.531 IDF ROOM | J
HQ | FCU0097 | NOT FOUND ON THE DRAWING OR SCHEDULE | B1.512 IDF ROOM | J
HQ | FCU0098 | IDF ROOM 06.512 | 6.512 IDF ROOM | J
HQ | FCU0099 | BRIDGE 07.602 | 7.602 BRIDGE | D
HQ | FCU0100 | BRIDGE 07.602 | 7.602 BRIDGE | D
HQ | FCU0101 | BRIDGE 07.602 | 7.602 BRIDGE | D
HQ | FCU0102 | PRINT COPY 06.104 | 6.104 PRINT COPY | D
HQ | FCU0103 | PRINT COPY 06.208 | 6.208 PRINT COPY | D
HQ | FCU0104 | IDF ROOM 7.531 | 7.531 IDF ROOM | J
HQ | FCU0105 | IDF ROOM 7.531 | 7.531 IDF ROOM | J
HQ | FCU0106 | IDF ROOM 7.512 | 7.512 IDF ROOM | J
HQ | FCU0107 | PRINT COPY 7.101 | 7.101 PRINT COPY | D
HQ | FCU0108 | PRINT COPY 7.104 | 7.104 PRINT COPY | D
HQ | FCU0109 | IDF ROOM 8.512 | 8.512 IDF ROOM | J
HQ | FCU0110 | IDF ROOM 9.531 | 9.531 IDF ROOM | D
HQ | FCU0111 | IDF ROOM G.512 | G.512 IDF ROOM | D
HQ | FCU0112 | IDF ROOM 9.512 | 9.512 IDF ROOM | J
HQ | FCU0113 | IDF ROOM 10.531 | 10.531 IDF ROOM | J
HQ | FCU0114 | STAFF LOUNGE STORAGE 1.114 | 1.114 STAFF LOUNGE STORAGE | J
HQ | FCU0115 | IDF ROOM 10.512 | 10.512 IDF ROOM | J
HQ | FCU0116 | PRINT COPY 10.038 | 10.038 PRINT COPY | D
HQ | FCU0117 | PRINT COPY 10.014 | 10.014 PRINT COPY | D
HQ | FCU0118 | TRANSLATOR ROOM 10.111 | 10.111 AV ROOM | D->E
HQ | FCU0119 | IDF ROOM 11.531 | 11.531 IDF ROOM | J
HQ | FCU0120 | IDF ROOM 11.531 | 11.531 IDF ROOM | J
HQ | FCU0121 | ELECT. CLOSET 11.110 | 11.110 ELECTRIC CLOSET | J
HQ | FCU0122 | MCC/ELEC ROOM 11.106 | 11.108 PRINT COPY ROOM | J
HQ | FCU0123 | PRINT COPY ROOM 11.108 | 11.106 MCC ELEC ROOM | J
HQ | FCU0124 | AV ROOM 11.107 | 11.107 AV IT | J->E
HQ | FCU0125 | IDF ROOM 11.512 | 11.512 IDF ROOM | J
HQ | FCU0131 | ROOF PLANT / WALKWAY (NEAR CSRR-0008) | RF.002 ROOF PLANT WALKWAY | D->E
HQ | FCU0132 | VISITOR CENTER 9.101 | 9.112 AV ROOM IN VISITOR CENTER | H
HQ | VAV0001 | STAFF ENTRANCE B.004 | B1.103 STAFF LOBBY | H
HQ | VAV0002 | STAFF LOBBY B.103 | B1.103 STAFF LOBBY | D
HQ | VAV0003 | STAFF LOBBY B.103 | B1.103 STAFF LOBBY | D
HQ | VAV0004 | SPORT SPACE B.110 | B1.110 MALE BREAK ROOM | H
HQ | VAV0005 | LOBBY B.116 | B1.116 SHEIKHA LOBBY | D->E
HQ | VAV0006 | LOBBY B.116 | B1.116 SHEIKHA LOBBY | D->E
HQ | VAV0007 | CONTROL ROOM G.008 | G.008 CONTROL ROOM | J
HQ | VAV0008 | PR & MARKET MANAGER G.009 | G.009 PR AND MARKET MANAGER | D
HQ | VAV0009 | PR & MARKET STAFF G.010 | G.010 PR AND MARKET STAFF | J
HQ | VAV0011 | PR & MARK. MANA. G.011 | G.011 PR AND MARKET MANAGER | D->E
HQ | VAV0012 | PR & MARKET STAFF G.012 | G.012 PR AND MARKET STAFF | J
HQ | VAV0013 | VISITOR OFF. G.014 | G.014 VISITOR CENT OFFICE | D->E
HQ | VAV0014 | PR & MARKET STAFF G.015 | G.015 PR AND MARKET STAFF | J
HQ | VAV0015 | PR & MAR. STAFF G.018 | G.018 PR AND MARKET STAFF | D->E
HQ | VAV0016 | PR & MAR. STAFF G.019 | G.019 PR AND MARKET STAFF | D->E
HQ | VAV0017 | PR & MAR. STAFF G.020 | G.020 PR AND MARKET STAFF | D->E
HQ | VAV0018 | PR & MAR. STAFF G.021 | G.021 PR AND MARKET STAFF | D->E
HQ | VAV0019 | PR & MARKET SEC. G.022 | G.022 PR AND MARKET SECRETARY | D->E
HQ | VAV0020 | PR & MARKET STAFF G.023 | G.023 PR AND MARKET STAFF | D
HQ | VAV0021 | CORRIDOR G.601 | G.601 CORRIDOR | J
HQ | VAV0022 | CORRIDOR G.601 | G.601 CORRIDOR | J
HQ | VAV0023 | SHOP G.105 | G.105 SHOP | J
HQ | VAV0024 | LOBBY G.104 | G.104 LOBBY | J
HQ | VAV0025 | LOBBY G.104 | G.104 LOBBY | J
HQ | VAV0026 | BMS ROOM G.103 | G.103 BMS | J->E
HQ | VAV0027 | PR & MARKET MANAGER G.004 | G.004 PR AND MARKET MANAGER | D
HQ | VAV0028 | PR & MARKET MANAGER G.003 | G.003 PR AND MARKET MANAGER | D
HQ | VAV0029 | PR & MARKET MANAGER G.002 | G.002 PR AND MARKET MANAGER | D
HQ | VAV0030 | G.CORIDOR | G.400 CORRIDOR SOUTH WEST SW | H
HQ | VAV0031 | PR & MARKET STAFF G.001 | G.001 PR AND MARKET STAFF | D
HQ | VAV0032 | PR & MARKET STAFF G.038 | G.038 PR AND MARKET STAFF | D
HQ | VAV0033 | PR & MARKET STAFF G.037 | G.037 PR AND MARKET STAFF | D
HQ | VAV0034 | PR & MARKET STAFF G.036 | G.036 PR AND MARKET STAFF | D
HQ | VAV0035 | PR & MARKET STAFF G.035 | G.035 PR AND MARKET STAFF | D
HQ | VAV0036 | PR & MARKET STAFF G.034 | G.034 PR AND MARKET STAFF | D
HQ | VAV0037 | PR & MARKET STAFF G.033 | G.033 PR AND MARKET STAFF | D
HQ | VAV0038 | PR & MARKET STAFF G.032 | G.032 PR AND MARKET STAFF | D
HQ | VAV0039 | STAFF G.030 | G.030 PR AND MARKET STAFF | D
HQ | VAV0040 | SENSORY G.029 | G.029 PR AND MARKET STAFF | D
HQ | VAV0041 | SENSORY G.029 | G.029 PR AND MARKET STAFF | J
HQ | VAV0042 | PR& MARKET DIRECTOR ENSUIT G.028 | G.028 PR AND MARKET DIRECTOR ENSUIT | D
HQ | VAV0043 | FINANCE CASHIER G.026 | G.026 FINANCE CASHIER | D
HQ | VAV0044 | VIP LOUNGE G.025 | G.025 VIP LOUNGE | D
HQ | VAV0045 | E-TOWER LOBBY G.107 | G.107 E TOWER LOBBY | J
HQ | VAV0046 | CORRIDOR (SOUTH EAST) G.602 | G.602 CORRIDOR SOUTH EAST | D
HQ | VAV0047 | CORRIDOR (SOUTH EAST) G.603 | G.603 CORRIDOR SOUTH EAST | D
HQ | VAV0048 | CONFERENCE ROOM G.101 | G.101 CONFERENCE ROOM | D
HQ | VAV0049 | CONFERENCE ROOM G.101 | G.101 CONFERENCE ROOM | D
HQ | VAV0050 | CONFERENCE ROOM G.101 | G.101 CONFERENCE ROOM | J
HQ | VAV0051 | CONFERENCE ROOM G.101 | G.101 CONFERENCE ROOM | J
HQ | VAV0052 | SOFT PLAY & CREATIVE LEARNING G.108 | G.108 CONSULTANT SPACE TRAINEES | D->E
HQ | VAV0053 | SOFT PLAY & CREATIVE LEARNING G.108 | G.108 CONSULTANT SPACE TRAINEES | J->E
HQ | VAV0054 | FINANCE MANAGER 1.011 | 1.011 FINANCE MANAGER | D
HQ | VAV0055 | FINANCE MANAGER 1.012 | 1.012 FINANCE MANAGER | D
HQ | VAV0056 | FINANCE MANAGER 1.013 | 1.013 FINANCE MANAGER | D
HQ | VAV0057 | FINANCE STAFF 1.014 | 1.014 FINANCE PROFSTAFF | D->E
HQ | VAV0058 | FINANCE STAFF 1.015 | 1.015 FINANCE PROFSTAFF | D->E
HQ | VAV0059 | FINANCE SECRETARY 1.016 | 1.016 FINANCE SECRETARY | D
HQ | VAV0060 | FINANCE DIRECTOR 1.017 | 1.017 FINANCE DIRECTOR ENSUIT | D->E
HQ | VAV0061 | FINANCE MANAGER 1.018 | 1.018 FINANCE MANAGER | D
HQ | VAV0062 | FINANCE MANAGER 1.019 | 1.019 FINANCE MANAGER | D
HQ | VAV0063 | FINANCE MANAGER 1.020 | 1.020 FINANCE MANAGER | J
HQ | VAV0064 | FINANCE SEC 1.021 | 1.021 FINANCE SECRETARY | D->E
HQ | VAV0065 | FINANCE SEC 1.022 | 1.022 FINANCE SECRETARY | D->E
HQ | VAV0066 | FINANCE AUDIT 1.023 | 1.023 FINANCE AUDIT | D
HQ | VAV0067 | FINANCE AUDIT 1.024 | 1.024 FINANCE AUDIT | D
HQ | VAV0068 | FINANCE STAFF 1.025 | 1.025 FINANCE PROFSTAFF | D->E
HQ | VAV0069 | FINANCE STAFF 1.026 | 1.026 FINANCE PROFSTAFF | D->E
HQ | VAV0070 | FINANCE MANAGER 1.027 | 1.027 FINANCE AUDITOR | D->E
HQ | VAV0071 | FINANCE MANAGER 1.028 | 1.028 FINANCE MANAGER | D
HQ | VAV0072 | FINANCE MANAGER 1.029 | 1.029 FINANCE MANAGER | D
HQ | VAV0073 | FINANCE SECRETARY 1.001 | 1.001 FINANCE CLERICAL SECRETARIES | D->E
HQ | VAV0074 | FINANCE MANAGER 1.002 | 1.002 FINANCE MANAGER | D
HQ | VAV0075 | FINANCE MANAGER 1.003 | 1.003 FINANCE MANAGER | D
HQ | VAV0076 | FINANCE MANAGER 1.004 | 1.004 FINANCE MANAGER | D
HQ | VAV0077 | FINANCE SECRETARY 1.005 | 1.005 FINANCE SECRETARY | J
HQ | VAV0078 | FINANCE STAFF 1.006 | 1.006 FINANCE PROFSTAFF | D->E
HQ | VAV0079 | FINANCE STAFF 1.007 | 1.007 FINANCE CLERICAL PROFSTAFF | D->E
HQ | VAV0080 | GROUND FLOOR VIP ENTRANCE 1.401 | 1.401 GROUND FLOOR VIP ENTRANCE | D
HQ | VAV0081 | GROUND FLOOR VIP ENTRANCE 1.401 | 1.401 GROUND FLOOR VIP ENTRANCE | D
HQ | VAV0082 | GROUND FLOOR VIP ENTRANCE 1.401 | 1.401 GROUND FLOOR VIP ENTRANCE | D
HQ | VAV0083 | STAFF LOUNGE 1.101 | 1.101 STAFF LOUNGE | D
HQ | VAV0084 | STAFF LOUNGE 1.101 | 1.101 STAFF LOUNGE | D
HQ | VAV0085 | STAFF LOUNGE 1.101 | 1.101 STAFF LOUNGE | D
HQ | VAV0086 | STAFF LOUNGE 1.101 | 1.101 STAFF LOUNGE | D
HQ | VAV0087 | FINANCE MEETING ROOM 1.108 | 1.108 FINANCE MEETING ROOM | D
HQ | VAV0088 | CONSULTANT SPACE 1.109 | 1.109 CONSULTANT SPACE TRAINEES | D->E
HQ | VAV0089 | CONSULTANT SPACE 1.109 | 1.109 CONSULTANT SPACE TRAINEES | J->E
HQ | VAV0090 | CONFERENCE ROOM 1.110 | G.104 LOBBY | D->E
HQ | VAV0091 | PRAYER ROOM 1.105 | 1.105 PRAYER ROOM | D
HQ | VAV0092 | FINANCE CASHIER 1.106 | 1.106 FINANCE CASHIER | D
HQ | VAV0093 | FINANCE ROOM 1.116 | 1.116 FINANCE SECURE ROOM | D->E
HQ | VAV0094 | FINANCE AUDITOR 1.117 | 1.117 FINANCE AUDITOR | D
HQ | VAV0095 | FINANCE AUDITOR 1.115 | 1.115 FINANCE AUDITOR | D
HQ | VAV0096 | STAFF LOUNGE 1.101 | 1.101 STAFF LOUNGE | J
HQ | VAV0097 | CORRIDOR 1.602 | 1.602 CORRIDOR | D
HQ | VAV0098 | CORRIDOR 1.602 | 1.602 CORRIDOR | D
HQ | VAV0099 | SOUTH EAST ZONE | 1.601 CORRIDOR | D->E
HQ | VAV0100 | FINANCE RECORD STORAGE 1.111 | 1.111 FINANCE RECORD STORAGE | D
HQ | VAV0101 | FOOD HEAT UP 1.702 | 1.702 FOOD HEAT UP | D
HQ | VAV0102 | WASHING AREA 1.706 | 1.706 WASHING AREA | J
HQ | VAV0103 | LOBBY (GROUND FLOOR) | G.104 LOBBY | D->E
HQ | VAV0104 | LOBBY (GROUND FLOOR) | G.104 LOBBY | D->E
HQ | VAV0105 | LOBBY (GROUND FLOOR) | G.104 LOBBY | D->E
HQ | VAV0106 | LOBBY (GROUND FLOOR) | G.104 LOBBY | D->E
HQ | VAV0107 | STAFF CAFETERIA 1.701 | 1.701 STAFF CAFETERIA | J
HQ | VAV0108 | STAFF CAFETERIA 1.701 | 1.701 STAFF CAFETERIA | J
HQ | VAV0109 | DIRECTOR ENSUIT 2.018 | 2.018 SUPPSERV DIRECTOR ENSUIT | D->E
HQ | VAV0110 | SUPP. SER. ADMIN 2.019 | 2.019 SUPPSERVADMINIST | D->E
HQ | VAV0111 | SUPP. SER. ADMIN 2.020 | 2.020 SUPPSERVADMINIST | D->E
HQ | VAV0112 | SUPP. SER. ADMIN 2.021 | 2.021 SUPPSERVADMINIST | D->E
HQ | VAV0113 | SUPP. SER. SECRETARY 2.022 | 2.022 SUPP SER SECRETARY | D
HQ | VAV0114 | SUPP. SER. ADMIN 2.023 | 2.023 SUPPSERVADMINIST | D->E
HQ | VAV0115 | SUPP. SER. ADMIN 2.024 | 2.024 SUPPSERVADMINIST | D->E
HQ | VAV0116 | SUPP. SER. ADMIN 2.025 | 2.025 SUPPSERVADMINIST | D->E
HQ | VAV0117 | SUPP. SER. SECRETARY 2.026 | 2.026 SUPP SER SECRETARY | D
HQ | VAV0118 | SUPP. SER. ADMIN 2.027 | 2.027 SUPPSERVADMINIST | D->E
HQ | VAV0119 | SUPP. SER. ADMIN 2.028 | 2.028 SUPPSERVADMINIST | D->E
HQ | VAV0120 | SUPP. SER. ADMIN 2.029 | 2.029 SUPPSERVADMINIST | D->E
HQ | VAV0121 | SUPP. SER. SECRETARY 2.030 | 2.030 SUPP SER SECRETARY | D
HQ | VAV0122 | SUPP. SER. ADMIN 2.031 | 2.031 SUPPSERVADMINIST | D->E
HQ | VAV0123 | SUPP. SER. ADMIN 2.032 | 2.032 SUPPSERVADMINIST | D->E
HQ | VAV0124 | SUPP. SER. ADMIN 2.033 | 2.033 SUPPSERVADMINIST | D->E
HQ | VAV0125 | SUPP. SER. SECRETARY 2.034 | 2.034 SUPP SER SECRETARY | D
HQ | VAV0126 | SUPP. SER. ADMIN 2.035 | 2.035 SUPPSERVADMINIST | D->E
HQ | VAV0127 | SUPP. SER. ADMIN 2.036 | 2.036 SUPPSERVADMINIST | D->E
HQ | VAV0128 | OFFICE SPACE 2.110A | 2.110A OFFICE SPACE | D
HQ | VAV0129 | 02.CORIDOR | 2.601 S TOWER CORRIDOR | D->E
HQ | VAV0130 | 02.CORIDOR | 2.601 S TOWER CORRIDOR | D->E
HQ | VAV0131 | FEMALE PRAYER ROOM 2.109 | 2.109 SHELL SPACE | D->E
HQ | VAV0132 | MEETING ROOM 2.108 | 2.108 SUPPSERV MEETING ROOM | D->E
HQ | VAV0133 | MEETING ROOM 2.108 | 2.108 SUPPSERV MEETING ROOM | D->E
HQ | VAV0134 | LOUNGE 2.105 | 2.105 LOUNGE | D
HQ | VAV0135 | CONSULTANT SPACE 2.104 | 2.104 CONSULTANTS SPACE OTHERS | D->E
HQ | VAV0136 | CONSULTANT SPACE 2.104 | 2.104 CONSULTANTS SPACE OTHERS | D->E
HQ | VAV0137 | CONSULTANT SPACE 2.102 | 2.102 CONSULTANTS SPACE OTHERS | D->E
HQ | VAV0138 | SUPP. SER. SECRETARY 2.017 | 2.017 SUPP SER SECRETARY | D
HQ | VAV0139 | SUPP. SER. ADMIN 2.016 | 2.016 SUPPSERVADMINIST | D->E
HQ | VAV0140 | SUPP. SER. ADMIN 2.015 | 2.015 SUPPSERVADMINIST | D->E
HQ | VAV0141 | SUPP. SER. ADMIN 2.014 | 2.014 SUPPSERVADMINIST | D->E
HQ | VAV0142 | SUPP. SER. SECRETARY 2.013 | 2.013 SUPP SER SECRETARY | D
HQ | VAV0143 | SUPP. SER. ADMIN 2.012 | 2.012 SUPPSERVADMINIST | D->E
HQ | VAV0144 | SUPP. SER. ADMIN 2.011 | 2.011 SUPPSERVADMINIST | D->E
HQ | VAV0145 | SUPP. SER. ADMIN 2.010 | 2.010 SUPPSERVADMINIST | D->E
HQ | VAV0146 | SUPP. SER. SECRETARY 2.009 | 2.009 SUPP SER SECRETARY | D
HQ | VAV0147 | DEBATE EXECUTIVE 2.008 | 2.008 DOHA DEBATE EXECUTIVE | D->E
HQ | VAV0148 | DEBATE EXECUTIVE 2.007 | 2.007 DOHA DEBATE EXECUTIVE | D->E
HQ | VAV0149 | DEBATE EXECUTIVE 2.006 | 2.006 DOHA DEBATE EXECUTIVE | D->E
HQ | VAV0150 | DEBATE EXECUTIVE 2.005 | 2.005 DOHA DEBATE EXECUTIVE | D->E
HQ | VAV0151 | DEBATE SECRETARY 2.004 | 2.004 DOHA DEBATE SECRETARY | D->E
HQ | VAV0152 | DEBATE EXECUTIVE 2.003 | 2.003 DOHA DEBATE EXECUTIVE | D->E
HQ | VAV0153 | DEBATE EXECUTIVE 2.002 | 2.002 DOHA DEBATE EXECUTIVE | D->E
HQ | VAV0154 | STORAGE ROOM 2.001 | 2.001 STORAGE ROOM | D
HQ | VAV0155 | OFFICE SPACE 2.101A | 2.101A OFFICE SPACE | D
HQ | VAV0156 | 02.CORIDOR | 2.601 S TOWER CORRIDOR | D->E
HQ | VAV0157 | HR IMMIG STAFF 3.017 | 3.017 HR IMMIG STAFF | D
HQ | VAV0158 | HR IMMIG STAFF 3.018 | 3.018 HR IMMIG STAFF | D
HQ | VAV0159 | HR IMMIG STAFF 3.019 | 3.019 HR IMMIG STAFF | D
HQ | VAV0160 | HR IMMIG STAFF 3.020 | 3.020 HR IMMIG STAFF | D
HQ | VAV0161 | HR IMMIG STAFF 3.021 | 3.021 HR IMMIG STAFF | D
HQ | VAV0162 | HR IMMIG STAFF 3.022 | 3.022 HR IMMIG SECRETARY | D->E
HQ | VAV0163 | HR IMMIG STAFF 3.023 | 3.023 HR IMMIG STAFF | D
HQ | VAV0164 | HR IMMIG STAFF 3.024 | 3.024 HR IMMIG STAFF | D
HQ | VAV0165 | HR IMMIG STAFF 3.025 | 3.025 HR IMMIG STAFF | D
HQ | VAV0166 | HR IMMIG STAFF 3.026 | 3.026 HR IMMIG STAFF | D
HQ | VAV0167 | HR IMMIG STAFF 3.027 | 3.027 HR IMMIG STAFF | D
HQ | VAV0168 | HR IMMIG STAFF 3.028 | 3.028 HR IMMIG STAFF | D
HQ | VAV0169 | HR IMMIG STAFF 3.029 | 3.029 HR IMMIG STAFF | D
HQ | VAV0170 | HR IMMIG STAFF 3.030 | 3.030 HR IMMIG STAFF | D
HQ | VAV0171 | HR IMMIG STAFF 3.031 | 3.031 HR IMMIG STAFF | D
HQ | VAV0172 | HR IMMIG STAFF 3.032 | 3.032 HR IMMIG SECRETARY | D->E
HQ | VAV0173 | MEETING ROOM 3.033 | 3.033 MEETING ROOM | J
HQ | VAV0174 | MEETING ROOM 3.033 | 3.033 MEETING ROOM | J
HQ | VAV0175 | OFFICE SPACE 3.105B | 3.105B OFFICE SPACE | D
HQ | VAV0176 | 03.CORIDOR | 3.601 S TOWER CORRIDOR | D->E
HQ | VAV0177 | ABLUTION ROOM 3.36 | 3.360 ABLUTION ROOM | D
HQ | VAV0178 | FEMALE PRAYER ROOM 3.105A | 3.105A FEMALE PRAYER ROOM | J
HQ | VAV0179 | 03.CORIDOR | 3.601 S TOWER CORRIDOR | D->E
HQ | VAV0180 | LOUNGE 3.001 | 3.001 LOUNGE | J
HQ | VAV0181 | CONSULTANT SPACE TRAINEES 3.102 | 3.102 CONSULTANT SPACE TRAINEES | J
HQ | VAV0182 | CONSULTANT SPACE TRAINEES 3.102 | 3.102 CONSULTANT SPACE TRAINEES | J
HQ | VAV0183 | CONSULTANT SPACE TRAINEES 3.102 | 3.102 CONSULTANT SPACE TRAINEES | J
HQ | VAV0184 | HR IMMG SECRETARY 3.104 | 3.104 HR IMMG SECRETARY | D
HQ | VAV0185 | HR IMMIG STAFF 3.012 | 3.012 HR IMMIG STAFF | D
HQ | VAV0186 | HR IMMIG STAFF 3.013 | 3.013 HR IMMIG STAFF | D
HQ | VAV0187 | HR IMMIG STAFF 3.014 | 3.014 HR IMMIG STAFF | D
HQ | VAV0188 | HR IMMIG STAFF 3.015 | 3.015 HR IMMIG STAFF | D
HQ | VAV0189 | HR IMMIG STAFF 3.016 | 3.016 HR IMMIG STAFF | D
HQ | VAV0190 | HR IMMIG STAFF 3.003 | 3.003 HR IMMIG STAFF | D
HQ | VAV0191 | HR IMMIG STAFF 3.004 | 3.004 HR IMMIG STAFF | D
HQ | VAV0192 | HR IMMIG STAFF 3.005 | 3.005 HR IMMIG STAFF | D
HQ | VAV0193 | HR IMMIG STAFF 3.006 | 3.006 HR IMMIG STAFF | D
HQ | VAV0194 | HR IMMIG STAFF 3.007 | 3.007 HR IMMIG STAFF | D
HQ | VAV0195 | HR IMMIG STAFF 3.008 | 3.008 HR IMMIG STAFF | D
HQ | VAV0196 | HR IMMIG STAFF 3.009 | 3.009 HR IMMIG STORAGE | D->E
HQ | VAV0197 | HR IMMIG STAFF 3.010 | 3.010 HR IMMIG STAFF | D
HQ | VAV0198 | HR IMMIG STAFF 3.011 | 3.011 HR IMMIG STAFF | D
HQ | VAV0199 | OFFICE SPACE 3.101 | 3.101 SHELL SPACE | D->E
HQ | VAV0200 | HR IMMIG STAFF 3.002 | 3.002 HR IMMIG STAFF | D
HQ | VAV0201 | 03.CORIDOR | 3.601 S TOWER CORRIDOR | D->E
HQ | VAV0202 | OFFICE SPACE 3.202A | 3.202A OFFICE SPACE | D
HQ | VAV0203 | OFFICE SPACE 3.202B | 3.202B OFFICE SPACE | D
HQ | VAV0204 | HR IMMIGRATION 3.205 | 3.205 HR IMMIG IMMIGRATION | D->E
HQ | VAV0205 | HR IMMIG MANAGER 3.206 | 3.206 HR IMMIG MANAGER | D
HQ | VAV0206 | HR IMMIG MANAGER 3.207 | 3.207 HR IMMIG MANAGER | D
HQ | VAV0207 | HR IMMIG MANAGER 3.208 | 3.208 HR IMMIG MANAGER | D
HQ | VAV0208 | HR IMMIG MANAGER 3.209 | 3.209 HR IMMIG MANAGER | D
HQ | VAV0209 | HR IMMIG OFFICER 3.210 | 3.210 HR IMMIG OFFICER | D
HQ | VAV0210 | HR IMMIG OFFICER 3.210 | 3.210 HR IMMIG OFFICER | J
HQ | VAV0211 | HR IMMIG MANAGER 3.211 | 3.211 HR IMMIG MANAGER | D
HQ | VAV0212 | HR IMMIG SEC. 3.212 | 3.212 HR IMMIG SECRETARIES | D->E
HQ | VAV0213 | HR IMMIG DIR. ENSUIT 3.213 | 3.213 HR IMMIG DIR ENSUIT | D
HQ | VAV0214 | IT DIR. ENSUIT 3.214 | 3.214 IT SECRETARY | D->E
HQ | VAV0215 | IT DIR. ENSUIT 3.215 | 3.215 IT DIR ENSUIT | D
HQ | VAV0216 | PROC. CONTR. SECRETARY 3.216 | 3.216 PROC CONTR SECRETARY | D
HQ | VAV0217 | PROC. & CONTR. DIR. E 3.201 | 3.201 PROC AND CONTRLDIRENSUIT | D->E
HQ | VAV0218 | PROC. & CONTR. MEETING ROOM 3.301 | 3.301 PROC AND CONTR MEETING ROOM | D
HQ | VAV0219 | PROC. & CONTR. MEETING ROOM 3.301 | 3.301 PROC AND CONTR MEETING ROOM | J
HQ | VAV0220 | HR IMMG. MEETING ROOM 3.302 | 3.302 HR IMMG MEETING ROOM | D
HQ | VAV0221 | SOUTH EAST CORRIDOR 3.602 | 3.602 E TOWER CORRIDOR | J->E
HQ | VAV0222 | STR. PL. DIR. ENSUIT 04.004 | 4.004 STR PL DIR ENSUIT | J
HQ | VAV0223 | STR. PL. DIR. MEETING ROOM 04.005 | 4.005 STR PL DIR MEETING ROOM | D
HQ | VAV0224 | STR. PL. DIR. MANAGER 04.006 | 4.006 STR PL DIR MANAGER | J
HQ | VAV0225 | STR. PL. DIR. MANAGER 04.007 | 4.007 STR PL DIR MANAGER | J
HQ | VAV0226 | STR. PL. DIR. MANAGER 04.008 | 4.008 STR PL DIR MANAGER | J
HQ | VAV0227 | STR. PL. DIR. HEAD OF PL. 04.009 | 4.009 STR PL DIR HEAD OF PL | J
HQ | VAV0228 | STR. PL. DIR. HEAD OF PL. 04.010 | 4.010 STR PL DIR HEAD OF PL | J
HQ | VAV0229 | STR. PL. DIR. HEAD OF PL. 04.011 | 4.011 STR PL DIR HEAD OF PL | J
HQ | VAV0230 | STR. PL. DIR. HEAD OF PL. 04.012 | 4.012 STR PL DIR HEAD OF PL | J
HQ | VAV0231 | STR. PL. DIR. HEAD OF PL. 04.013 | 4.013 STR PL DIR HEAD OF PL | J
HQ | VAV0232 | STR. PL. DIR. MANAGER 04.014 | 4.014 STR PL DIR MANAGER | J
HQ | VAV0233 | OFFICE SPACE 04.015C | 4.015A OFFICE SPACE | J
HQ | VAV0234 | OFFICE SPACE 04.015A | 4.015C OFFICE SPACE | J
HQ | VAV0235 | S-TOWER CORRIDOR 4.601 | 4.601 S TOWER CORRIDOR | D
HQ | VAV0236 | VP EDU STORAGE 04.109 | 4.109 VP EDU STORAGE | D
HQ | VAV0237 | S-TOWER CORRIDOR 4.601 | 4.601 S TOWER CORRIDOR | D
HQ | VAV0238 | STR. PL. DIR. TECH. STAFF 04.108 | 4.108 STR PL DIR ARCHIVE ROOM | D->E
HQ | VAV0239 | STR. PL. DIR. TECH. STAFF 04.107 | 4.107 STR PL DIR TECH STAFF | D
HQ | VAV0240 | WAITING LOUNGE 04.104 | 4.104 WAITING LOUNGE | J
HQ | VAV0241 | WAITING LOUNGE 04.104 | 4.104 WAITING LOUNGE | J
HQ | VAV0242 | STR. PL. DIR. MANAGER 04.002 | 4.002 STR PL DIR MANAGER | D
HQ | VAV0243 | STR. PL. DIR. EXEC. SECRE. 04.003 | 4.003 STR PL DIR EXEC SECRE | D
HQ | VAV0244 | OFFICE SPACE 04.001B | 4.001B OFFICE SPACE | D
HQ | VAV0245 | OFFICE SPACE 04.001D | 4.001D OFFICE SPACE | D
HQ | VAV0246 | OFFICE SPACE 04.001F | 4.001F OFFICE SPACE | D
HQ | VAV0247 | OFFICE SPACE 04.001G | 4.001G OFFICE SPACE | D
HQ | VAV0248 | STORAGE SPACE 04.103 | 4.103 STORAGE SPACE | J
HQ | VAV0249 | OFFICE SPACE 04.102 | 4.102 SHELL SPACE | D->E
HQ | VAV0250 | OFFICE SPACE 04.101 | 4.101 SHELL SPACE | D->E
HQ | VAV0251 | S-TOWER CORRIDOR 4.601 | 4.601 S TOWER CORRIDOR | D
HQ | VAV0252 | OFFICE SPACE 04.201 | 4.201 SHELL SPACE | D->E
HQ | VAV0253 | OFFICE SPACE 04.204 | 4.204 SHELL SPACE | D->E
HQ | VAV0254 | VP ADM MANAGER 04.205 | 4.205 VP ADM MANAGER | D
HQ | VAV0255 | VP ADM MANAGER 04.206 | 4.206 VP ADM MANAGER | D
HQ | VAV0256 | VP ADM SEC. 04.208 | 4.208 VP ADM EXECSECRET | D->E
HQ | VAV0257 | VP ADM SEC. 04.208 | 4.208 VP ADM EXECSECRET | J->E
HQ | VAV0258 | VP ADM MANAGER 04.209 | 4.209 VP ADM MANAGER | D
HQ | VAV0259 | VP ADM MANAGER 04.210 | 4.210 VP ADM MANAGER | D
HQ | VAV0260 | VP ADM MANAGER 04.211 | 4.211 VP ADM MANAGER | D
HQ | VAV0261 | VP ADM PERS. ASS. 04.212 | 4.212 VP ADM PERSASSIST | D->E
HQ | VAV0262 | VP ADM ENSUIT 04.213 | 4.213 VP ADM ENSUIT | D
HQ | VAV0263 | VP ADM MEETING ROOM 04.301 | 4.301 VP ADM MEETING ROOM | D
HQ | VAV0264 | VP ADM MEETING ROOM 04.301 | 4.301 VP ADM MEETING ROOM | J
HQ | VAV0265 | E-TOWER CORRIDOR 4.603 | 4.603 E TOWER CORRIDOR | D
HQ | VAV0266 | E-TOWER CORRIDOR 4.603 | 4.603 E TOWER CORRIDOR | D
HQ | VAV0267 | VP EDU DIR ENSUIT 5.012 | 5.012 VP EDU OFFICE DIRECTOR ENSUIT | D->E
HQ | VAV0268 | VP EDU SECR. 5.013 | 5.013 VP EDU SECRETARY | D->E
HQ | VAV0269 | VP EDU ASSIS. 5.014 | 5.014 VP EDU ASSISTANT | D->E
HQ | VAV0270 | VP EDU ASSIS. 5.015 | 5.015 VP EDU ASSISTANT | D->E
HQ | VAV0271 | VP EDU ASSIS. 5.016 | 5.016 VP EDU ASSISTANT | D->E
HQ | VAV0272 | VP EDU ASSIS. 5.017 | 5.017 VP EDU ASSISTANT | D->E
HQ | VAV0273 | VP EDU OFF. 5.018 | 5.018 VP EDU OFFICERS | D->E
HQ | VAV0274 | VP EDU OFF. 5.019 | 5.019 VP EDU OFFICERS | D->E
HQ | VAV0275 | VP EDU OFF. 5.020 | 5.020 VP EDU OFFICERS | D->E
HQ | VAV0276 | VP EDU OFF. 5.021 | 5.021 VP EDU OFFICERS | D->E
HQ | VAV0277 | VP EDU OFF. 5.022 | 5.022 VP EDU OFFICERS | D->E
HQ | VAV0278 | VP EDU OFF. 5.023 | 5.023 VP EDU OFFICERS | D->E
HQ | VAV0279 | VP EDU SEC. 5.024 | 5.024 VP EDU SECRETARY | D->E
HQ | VAV0280 | VP EDU DIR ENSUIT 5.025 | 5.025 VP EDU OFFICE DIRECTOR ENSUIT | D->E
HQ | VAV0281 | VP EDU ASS. 5.026 | 5.026 VP EDU ASSISTANT | D->E
HQ | VAV0282 | S-TOWER CORRIDOR 5.601 | 5.601 S TOWER CORRIDOR | D
HQ | VAV0283 | VP EDU OFF. 5.110 | 5.110 VP EDU OFFICERS | D->E
HQ | VAV0284 | VP EDU ASS. 5.109 | 5.109 ELECTRICAL CABINET | D->E
HQ | VAV0285 | VP EDU SEC. 5.108 | 5.108 VP EDU ASSISTANT | D->E
HQ | VAV0286 | VP EDU SEC. 5.107 | 5.107 VP EDUCATION SUPPSECRET | D->E
HQ | VAV0287 | VP EDU SEC. 5.107 | 5.107 VP EDUCATION SUPPSECRET | J->E
HQ | VAV0288 | VP EDU LOUNGE WAITING 5.104 | 5.104 VP EDU LOUNGE WAITING | J
HQ | VAV0289 | VP EDU LOUNGE WAITING 5.104 | 5.104 VP EDU LOUNGE WAITING | J
HQ | VAV0290 | VP EDU OFFICERS 5.009 | 5.009 VP1 VP EDU OFFICERS | J->E
HQ | VAV0291 | VP EDU OFFICERS 5.010 | 5.010 VP EDU OFFICERS | J
HQ | VAV0292 | VP EDU ASSISTANT 5.011 | 5.011 VP EDU ASSISTANT | J
HQ | VAV0293 | VP EDU OFF. DIR ENSUIT 5.002 | 5.002 VP EDU OFF DIR ENSUIT | D
HQ | VAV0294 | VP EDU SECRE. 5.003 | 5.003 VP EDU SECRETARY | D->E
HQ | VAV0295 | VP EDU ASSISTANT 5.004 | 5.004 VP EDU ASSISTANT | J
HQ | VAV0296 | VP EDU OFFICERS 5.005 | 5.005 VP EDU OFFICERS | J
HQ | VAV0297 | VP EDU OFFICERS 5.006 | 5.006 VP EDU OFFICERS | J
HQ | VAV0298 | VP EDU ASSISTANT 5.007 | 5.007 VP EDU OFFICERS | J->E
HQ | VAV0299 | VP EDU ASSISTANT 5.008 | 5.008 VP EDU ASSISTANT | J
HQ | VAV0300 | MEETING ROOM 5.102 | 5.102 MEETING ROOM | J
HQ | VAV0301 | MEETING ROOM 5.102 | 5.102 MEETING ROOM | J
HQ | VAV0302 | VP EDU SECRETARY 5.101 | 5.101 VP EDU SECRET | J->E
HQ | VAV0303 | VP EDU ASSISTANT 5.001 | 5.001 VP EDU ASSISTANT | J
HQ | VAV0304 | S-TOWER CORRIDOR 5.601 | 5.601 S TOWER CORRIDOR | D
HQ | VAV0305 | VP EDU MEMB. 5.201 | 5.201 VP EDU MEMBERS OF EDU | D->E
HQ | VAV0306 | VP EDU MEMB. 5.202 | 5.202 VP EDU MEMBERS OF EDU | D->E
HQ | VAV0307 | VP EDU MEMB. 5.203 | 5.203 VP EDU MEMBERS OF EDU | D->E
HQ | VAV0308 | VP EDU MEMB. 5.205 | 5.205 VP EDU MEETING ROOM | D->E
HQ | VAV0309 | VP EDU MEMB. 5.205 | 5.205 VP EDU MEETING ROOM | J->E
HQ | VAV0310 | VP EDU MEMB. 5.206 | 5.206 VP EDU MEMBERS OF EDU | D->E
HQ | VAV0311 | VP EDU MEMB. 5.207 | 5.207 VP EDU MEMBERS OF EDU | D->E
HQ | VAV0312 | VP EDU MEMB. 5.208 | 5.208 VP EDU MEMBERS OF EDU | D->E
HQ | VAV0313 | VP EDU MEMB. 5.209 | 5.209 VP EDU MEMBERS OF EDU | D->E
HQ | VAV0314 | VP EDU ENSUIT 5.210 | 5.210 VP EDU ENSUIT | J
HQ | VAV0315 | VP EDU SEC. 5.211 | 5.211 VP EDU CHPEXECSECRET | D->E
HQ | VAV0316 | VP EDU MEMB. 5.212 | 5.212 VP EDU MEMBERS OF EDU | D->E
HQ | VAV0317 | VP EDU DIR. ENSUIT 5.213 | 5.213 VP EDU OFFICE DIRECTOR ENSUIT | D->E
HQ | VAV0318 | 05.CORIDOR | 5.350 CORRIDOR | D->E
HQ | VAV0319 | 05.CORIDOR | 5.350 CORRIDOR | D->E
HQ | VAV0320 | 05.CORIDOR | 5.350 CORRIDOR | D->E
HQ | VAV0321 | 05.CORIDOR | 5.350 CORRIDOR | D->E
HQ | VAV0322 | VP EDU OFF. 5.027 | 5.027 VP EDU OFFICERS | D->E
HQ | VAV0323 | INT. AUDIT 06.012 | 6.012 INTAUDIT SEN JNTAUD | D->E
HQ | VAV0324 | INT. AUDIT SEC. 06.013 | 6.013 INTAUDIT SECRETARY | D->E
HQ | VAV0325 | ACA. AUDIT 06.014 | 6.014 ACA AUDIT SUPP AUDIT | D->E
HQ | VAV0326 | ACA. AUDIT 06.015 | 6.015 ACA AUDIT SUPP AUDIT | D->E
HQ | VAV0327 | ACA. AUDIT 06.016 | 6.016 ACA AUDIT SUPP AUDIT | D->E
HQ | VAV0328 | ACA. AUDIT 06.017 | 6.017 ACA AUDIT SUPP AUDIT | D->E
HQ | VAV0329 | ACA. AUDIT 06.018 | 6.018 ACA AUDIT SUPP AUDIT | D->E
HQ | VAV0330 | ACA. AUDIT 06.019 | 6.019 ACA AUDIT SUPP AUDIT | D->E
HQ | VAV0331 | ACA. AUDIT 06.020 | 6.020 ACA AUDIT SUPP AUDIT | D->E
HQ | VAV0332 | ACA. AUDIT SEC. 06.021 | 6.021 ACA AUDIT SECRETARY | D->E
HQ | VAV0333 | ACA. AUDIT SEC. 06.022 | 6.022 ACA AUDIT SECRETARY | D->E
HQ | VAV0334 | ACA. SEN. AUDIT 06.023 | 6.023 ACA AUDIT ACA SENAUD | D->E
HQ | VAV0335 | ACA. SEN. AUDIT 06.024 | 6.024 ACA AUDIT ACA SENAUD | D->E
HQ | VAV0336 | FACI. MANA. SEC. 06.025 | 6.025 FACILITY MANAGSECRETARY | D->E
HQ | VAV0337 | FACILITY MANAG. DIR. ENSUIT 06.026 | 6.026 FACILITY MANAG DIR ENSUIT | D
HQ | VAV0338 | VP CAPITAL CONSUL. 06.027 | 6.027 VP CAPITAL CONSULTANT | D->E
HQ | VAV0339 | VP CAPITAL CONSUL. 06.028 | 6.028 VP CAPITAL CONSULTANT | D->E
HQ | VAV0340 | S-TOWER CORRIDOR 6.601 | 6.601 S TOWER CORRIDOR | D
HQ | VAV0341 | VP CAPITAL WORK ASSIST 06.109 | 6.109 VP CAPITAL WORK ASSIST | D
HQ | VAV0342 | VP CAPITAL PROJ. COORD 06.108 | 6.108 VP CAPITAL PROJ COORD | D
HQ | VAV0343 | S-TOWER CORRIDOR 6.601 | 6.601 S TOWER CORRIDOR | D
HQ | VAV0344 | LOUNGE 06.105 | 6.105 LOUNGE | J
HQ | VAV0345 | LOUNGE 06.105 | 6.105 LOUNGE | J
HQ | VAV0346 | INT. AUDIT SUPP. AUDIT 06.009 | 6.009 INT AUDIT SUPP AUDIT | D
HQ | VAV0347 | INT. AUDIT SEC. 06.010 | 6.010 INTAUDIT SECRETARY | D->E
HQ | VAV0348 | INT. AUDIT 06.011 | 6.011 INTAUDIT SEN JNTAUD | D->E
HQ | VAV0349 | INT. AUDIT ARCHIVE ROOM 06.002 | 6.002 INT AUDIT ARCHIVE ROOM | D
HQ | VAV0350 | INT. AUDIT SUPP. AUDIT 06.003 | 6.003 INT AUDIT SUPP AUDIT | D
HQ | VAV0351 | INT. AUDIT SUPP. AUDIT 06.004 | 6.004 INT AUDIT SUPP AUDIT | D
HQ | VAV0352 | INT. AUDIT SUPP. AUDIT 06.005 | 6.005 INT AUDIT SUPP AUDIT | D
HQ | VAV0353 | INT. AUDIT SUPP. AUDIT 06.006 | 6.006 INT AUDIT SUPP AUDIT | D
HQ | VAV0354 | INT. AUDIT SUPP. AUDIT 06.007 | 6.007 INT AUDIT SUPP AUDIT | D
HQ | VAV0355 | INT. AUDIT SUPP. AUDIT 06.008 | 6.008 INT AUDIT SUPP AUDIT | D
HQ | VAV0356 | OFFICE SPACE 06.103 | 6.103 SHELL SPACE | D->E
HQ | VAV0357 | OFFICE SPACE 06.102 | 6.102 SHELL SPACE | D->E
HQ | VAV0358 | OFFICE SPACE 06.101 | 6.101 SHELL SPACE | D->E
HQ | VAV0359 | AUDIT ARCHIVE 06.001 | 6.001 ACA AUDIT ARCHIVE | D->E
HQ | VAV0360 | S-TOWER CORRIDOR 6.601 | 6.601 S TOWER CORRIDOR | D
HQ | VAV0361 | VP CAPITAL PROJ. MANAGER 06.201 | 6.201 VP CAPITAL PROJ MANAGER | D
HQ | VAV0362 | VP CAPITAL PROJ. MANAGER 06.202 | 6.202 VP CAPITAL PROJ MANAGER | D
HQ | VAV0363 | VP CAPITAL PROJ. MANAGER 06.204 | 6.204 VP CAPITAL PROJ MANAGER | D
HQ | VAV0364 | VP CAPITAL CONSU. 06.205 | 6.205 VP CAPITAL CONSULTANT | D->E
HQ | VAV0365 | VP CAPITAL STORAGE 06.206 | 6.206 VP CAPITAL STORAGE | J
HQ | VAV0366 | VP CAPITAL SEC. 06.207 | 6.207 VP CAPITAL SECRETARIES | D->E
HQ | VAV0367 | VP CAPITAL ENSUIT 06.209 | 6.209 VP CAPITAL ENSUIT | J
HQ | VAV0368 | VP CAPITAL SEC. 06.210 | 6.210 VP CAPITAL SECRETARIES | D->E
HQ | VAV0369 | VP CAPITAL SEC. 06.211 | 6.211 VP CAPITAL SECRETARIES | D->E
HQ | VAV0370 | VP CAPITAL DIR. ENSUIT 06.212 | 6.212 VP CAPITAL DIRECTOR ENSUIT | D->E
HQ | VAV0371 | E-TOWER CORRIDOR 6.603 | 6.603 E TOWER CORRIDOR | D
HQ | VAV0372 | E-TOWER CORRIDOR 6.603 | 6.603 E TOWER CORRIDOR | D
HQ | VAV0373 | CA ENSUIT 7.017 | 7.017 CA ENSUIT | J
HQ | VAV0374 | CA SEC. 7.018 | 7.018 CA SECRETARY | D->E
HQ | VAV0375 | BD UNIT SEC. 7.019 | 7.019 BD UNIT SECRETARY | D->E
HQ | VAV0376 | BD UNIT EXECU. 7.020 | 7.020 BD UNIT EXECUTIVE | D->E
HQ | VAV0377 | BD UNIT EXECU. 7.021 | 7.021 BD UNIT EXECUTIVE | D->E
HQ | VAV0378 | BD UNIT EXECU. 7.022 | 7.022 BD UNIT EXECUTIVE | D->E
HQ | VAV0379 | BD UNIT EXECU. 7.023 | 7.023 BD UNIT EXECUTIVE | D->E
HQ | VAV0380 | BD UNIT EXECU. 7.024 | 7.024 BD UNIT EXECUTIVE | D->E
HQ | VAV0381 | BD UNIT EXECU. 7.025 | 7.025 BD UNIT EXECUTIVE | D->E
HQ | VAV0382 | BD UNIT EXECU. 7.026 | 7.026 BD UNIT EXECUTIVE | D->E
HQ | VAV0383 | BD UNIT EXECU. 7.027 | 7.027 BD UNIT EXECUTIVE | D->E
HQ | VAV0384 | BD UNIT EXECU. 7.028 | 7.028 BD UNIT EXECUTIVE | D->E
HQ | VAV0385 | MEETING ROOM 7.029 | 7.029 MEETING ROOM | J
HQ | VAV0386 | MEETING ROOM 7.029 | 7.029 MEETING ROOM | J
HQ | VAV0387 | OFFICE SPACE 7.030 | 7.030 SHELL SPACE | D->E
HQ | VAV0388 | OFFICE SPACE 7.031A | 7.031A OFFICE SPACE | D
HQ | VAV0389 | S-TOWER CORRIDOR 7.601 | 7.601 S TOWER CORRIDOR | D
HQ | VAV0390 | S-TOWER CORRIDOR 7.601 | 7.601 S TOWER CORRIDOR | D
HQ | VAV0391 | OFFICE SPACE 7.032 | 7.032 SHELL SPACE | D->E
HQ | VAV0392 | OFFICE SPACE 7.032 | 7.032 SHELL SPACE | J->E
HQ | VAV0393 | LOUNGE 7.106 | 7.106 LOUNGE | J
HQ | VAV0394 | CA SECRETARY 7.105 | 7.105 CA SECRETARY | J
HQ | VAV0395 | CA SECRETARY 7.103 | 7.103 CA SECRETARY | J
HQ | VAV0396 | CA SECRETARY 7.102 | 7.102 CA SECRETARY | J
HQ | VAV0397 | DOC. UNIT EMPLOYEE 07.001 | 7.001 DOC UNIT EMPLOYEE | D
HQ | VAV0398 | DOC. UNIT MULTIMEDIA STUDIO 07.002 | 7.002 DOC UNIT MULTIMEDIA STUDIO | D
HQ | VAV0399 | S-TOWER CORRIDOR 7.601 | 7.601 S TOWER CORRIDOR | D
HQ | VAV0400 | DOC. UNIT MULTIMEDIA STUDIO 07.002 | 7.002 DOC UNIT MULTIMEDIA STUDIO | J
HQ | VAV0401 | DOC. UNIT EMPLOYEE 7.003 | 7.003 DOC UNIT EMPLOYEE | D
HQ | VAV0402 | DOC. UNIT EMPLOYEE 7.004 | 7.004 DOC UNIT EMPLOYEE | D
HQ | VAV0403 | DOC. UNIT EMPLOYEE 7.005 | 7.005 DOC UNIT EMPLOYEE | D
HQ | VAV0404 | DOC. UNIT EMPLOYEE 7.006 | 7.006 DOC UNIT EMPLOYEE | D
HQ | VAV0405 | CA COORD 7.007 | 7.007 CA COORD | J
HQ | VAV0406 | CA COORD 7.008 | 7.008 CA COORD | J
HQ | VAV0407 | CA COORD 7.009 | 7.009 CA COORD | J
HQ | VAV0408 | CA COORD 7.010 | 7.010 CA COORD | J
HQ | VAV0409 | CA COORD 7.011 | 7.011 CA COORD | J
HQ | VAV0410 | CA COORD 7.012 | 7.012 CA COORD | J
HQ | VAV0411 | CA COORD 7.013 | 7.013 CA COORD | J
HQ | VAV0412 | CA COORD 7.014 | 7.014 CA COORD | J
HQ | VAV0413 | CA COORD 7.015 | 7.015 CA COORD | J
HQ | VAV0414 | CA COORD 7.016 | 7.016 CA COORD | J
HQ | VAV0415 | CONSULTANT SPACE 7.201 | 7.201 CONSULTANT SPACE | J
HQ | VAV0416 | PRE. EXEC. OFFICE 7.202 | 7.202 PRESIDENT EXECOFFICE | D->E
HQ | VAV0417 | PRE. EXEC. OFFICE 7.204 | 7.204 PRESIDENT EXECOFFICE | D->E
HQ | VAV0418 | PRE. EXEC. OFFICE 7.204 | 7.204 PRESIDENT EXECOFFICE | D->E
HQ | VAV0419 | PRE. EXEC. OFFICE 7.205 | 7.205 PRESIDENT EXECOFFICE | D->E
HQ | VAV0420 | PRE. EXEC. OFFICE 7.205 | 7.205 PRESIDENT EXECOFFICE | D->E
HQ | VAV0421 | PRESIDENT SUPP. SEC. 7.208 | 7.208 PRESIDENT SUPPORT SECRET | D->E
HQ | VAV0422 | E-TOWER CORRIDOR 7.603 | 7.603 E TOWER CORRIDOR | J
HQ | VAV0423 | PRESIDENT EXEC. SEC. 7.209 | 7.209 PRESIDENT EXECSECRET | D->E
HQ | VAV0424 | PRESIDENT EXEC. SEC. 7.210 | 7.210 PRESIDENT EXECSECRET | D->E
HQ | VAV0425 | PRESIDENT ENSUIT 7.211 | 7.211 PRESIDENT ENSUIT | D
HQ | VAV0426 | PRESIDENT MEETING ROOM 7.212 | 7.212 PRESIDENT MEETING ROOM | D
HQ | VAV0427 | VICE CHAIRPERSON ENSULT 7.213 | 7.213 VICE CHAIRPERSON ENSULT | D
HQ | VAV0428 | VICE CHAIRPERSON SEC. 7.214 | 7.214 VICE CHAIRSECRETARY | D->E
HQ | VAV0429 | MEETING ROOM 7.215 | 7.215 VICE CHAIRPERSON MEETING ROOM | D->E
HQ | VAV0430 | MEETING ROOM 7.301 | 7.301 MEETING ROOM | D
HQ | VAV0431 | MEETING ROOM 7.301 | 7.301 MEETING ROOM | J
HQ | VAV0432 | MEETING ROOM 7.301 | 7.301 MEETING ROOM | J
HQ | VAV0433 | OBSERVATION SPACE 8.001 | 8.001 OBSERVATION SPACE | J
HQ | VAV0434 | OBSERVATION SPACE 8.001 | 8.001 OBSERVATION SPACE | J
HQ | VAV0435 | OBSERVATION SPACE 8.001 | 8.001 OBSERVATION SPACE | J
HQ | VAV0436 | OBSERVATION SPACE 8.001 | 8.001 OBSERVATION SPACE | J
HQ | VAV0437 | OBSERVATION SPACE 8.001 | 8.001 OBSERVATION SPACE | J
HQ | VAV0438 | VISITORS CENTER OFFICE 8.002 | 8.002 VISITORS CENTER OFFICE | J
HQ | VAV0439 | VISITORS CENTER CORRIDOR 8.602 | 8.602 VISITORS CENTER CORRIDOR | D
HQ | VAV0440 | VISITORS CENTER CORRIDOR 8.602 | 8.602 VISITORS CENTER CORRIDOR | J
HQ | VAV0441 | VISITORS CENTER CORRIDOR 8.602 | 8.602 VISITORS CENTER CORRIDOR | J
HQ | VAV0442 | VISITORS CENTER CORRIDOR 8.602 | 8.602 VISITORS CENTER CORRIDOR | J
HQ | VAV0443 | VISITORS CENTER CORRIDOR 8.602 | 8.602 VISITORS CENTER CORRIDOR | J
HQ | VAV0444 | BMO EXEC. ASSIST. 9.011 | 9.011 BMO EXEC ASSIST | D
HQ | VAV0445 | BMO EXEC. ASSIST. 9.012 | 9.012 BMO EXEC ASSIST | D
HQ | VAV0446 | BMO EXEC. ASSIST. 9.013 | 9.013 BMO EXEC ASSIST | D
HQ | VAV0447 | BMO EXEC. ASSIST. 9.014 | 9.014 BMO EXEC ASSIST | D
HQ | VAV0448 | BMO EXEC. ASSIST. 9.015 | 9.015 BMO EXEC ASSIST | D
HQ | VAV0449 | BMO EXEC. ASSIST. 9.016 | 9.016 BMO EXEC ASSIST | D
HQ | VAV0450 | BMO EXEC. ASSIST. 9.017 | 9.017 BMO EXEC ASSIST | D
HQ | VAV0451 | BMO EXEC. SEC. 9.018 | 9.018 BMO EXECSECRET | D->E
HQ | VAV0452 | BMO EXEC. SEC. 9.019 | 9.019 BMO EXECSECRET | D->E
HQ | VAV0453 | BMO EXEC. SEC. 9.020 | 9.020 BMO EXECSECRET | D->E
HQ | VAV0454 | BMO OPER. DIR. ENSUIT 9.021 | 9.021 BMO OPER DIR ENSUIT | D
HQ | VAV0455 | BMO EXEC. ASSIST. 9.022 | 9.022 BMO EXEC ASSIST | D
HQ | VAV0456 | BMO EXEC. SEC. 9.023 | 9.023 BMO EXECSECRET | D->E
HQ | VAV0457 | BMO EXEC. SEC. 9.024 | 9.024 BMO EXECSECRET | D->E
HQ | VAV0458 | BMO EXEC. SEC. 9.025 | 9.025 BMO EXECSECRET | D->E
HQ | VAV0459 | BMO EXEC. SEC. 9.025 | 9.025 BMO EXECSECRET | J->E
HQ | VAV0460 | BMO SUPP. SEC. 9.026 | 9.026 BMO SUPPSECRET | D->E
HQ | VAV0461 | BMO SUPP. SEC. 9.027 | 9.027 BMO SUPPSECRET | D->E
HQ | VAV0462 | BMO SUPP. SEC. 9.028 | 9.028 BMO SUPPSECRET | D->E
HQ | VAV0463 | BMO SUPP. SEC. 9.029 | 9.029 BMO SUPPSECRET | D->E
HQ | VAV0464 | BMO SUPP. SEC. 9.030 | 9.030 BMO SUPPSECRET | D->E
HQ | VAV0465 | BMO PRINT COPY 9.031 | 9.031 BMO PRINT COPY | J
HQ | VAV0466 | BMO STORAGE 9.032 | 9.032 BMO STORAGE | D
HQ | VAV0467 | HR EDU. ADV. ENSUIT 9.033 | 9.033 HR EDUADVADVISOR ENSUIT | D->E
HQ | VAV0468 | HR EDU. ADV. ENSUIT 9.034 | 9.034 HR EDUADVADVISOR ENSUIT | D->E
HQ | VAV0469 | HR EDU. ADV. ENSUIT 9.035 | 9.035 HR EDUADVADVISOR ENSUIT | D->E
HQ | VAV0470 | BOD EXECUTIVE 9.036 | 9.036 BOD EXECUTIVE | J
HQ | VAV0471 | BOD SEC. 9.037 | 9.037 BOD SECRETARY | D->E
HQ | VAV0472 | BOD EXECUTIVE 9.038 | 9.038 BOD EXECUTIVE | D
HQ | VAV0473 | HH-WING CORRIDOR 9.601 | 9.601 HH WING CORRIDOR | D
HQ | VAV0474 | HH-WING CORRIDOR 9.601 | 9.601 HH WING CORRIDOR | J
HQ | VAV0475 | MEETING ROOM 9.039 | 9.039 MEETING ROOM | J
HQ | VAV0476 | BMO SAFE 9.040 | 9.040 BMO SAFE ROOM | D->E
HQ | VAV0477 | BMO ARCHIVE ROOM 9.041 | 9.041 BMO ARCHIVE ROOM | J
HQ | VAV0478 | HH-WING CORRIDOR 9.601 | 9.601 HH WING CORRIDOR | D
HQ | VAV0479 | LEGAL ARCHIVE 9.001 | 9.001 LEGAL ARCHIVE | J
HQ | VAV0480 | LEGAL CONSULE 9.002 | 9.002 LEGAL CONSULE | J
HQ | VAV0481 | LEGAL CONSULE 9.003 | 9.003 LEGAL LEGAL CONSULE | J->E
HQ | VAV0482 | LEGAL CONSULE 9.004 | 9.004 LEGAL LEGAL CONSULE | J->E
HQ | VAV0483 | LEGAL CONSULE 9.005 | 9.005 LEGAL LEGAL CONSULE | J->E
HQ | VAV0484 | LEGAL CONSULE 9.006 | 9.006 LEGAL LEGAL CONSULE | J->E
HQ | VAV0485 | LEGAL CONSULE 9.007 | 9.007 LEGAL LEGAL CONSULE | J->E
HQ | VAV0486 | LEGAL SUP. SEC. 9.008 | 9.008 LEGAL LEGSUPSEC | J->E
HQ | VAV0487 | LEGAL SUP. SEC. 9.009 | 9.009 LEGAL LEGSUPSEC | J->E
HQ | VAV0488 | LEGAL ADV. ENSUIT 9.010 | 9.010 LEGAL LEGADVENSUIT | J->E
HQ | VAV0489 | LOUNGE 9.105 | 9.105 LOUNGE | J
HQ | VAV0490 | BMO WAITING AREA 9.104 | 9.104 BMO WAITING AREA | J
HQ | VAV0491 | NORTH WEST TOILETS 9.403 | 9.104 BMO WAITING AREA | J
HQ | VAV0492 | HH-WING CORRIDOR 9.601 | 9.601 HH WING CORRIDOR | D
HQ | VAV0493 | SHEIKA WING DINING AREA 9.110 | 9.110 SHEIKA WING DINING AREA | D
HQ | VAV0494 | SHEIKA WING DINING AREA 9.110 | 9.110 SHEIKA WING DINING AREA | J
HQ | VAV0495 | SOUTH EAST CORRIDOR 9.11 | 9.110 SHEIKA WING DINING AREA | D->E
HQ | VAV0496 | KITCHEN 9.108 | 9.108 SUPPORT SPACE PREP KITCHEN | J->E
HQ | VAV0497 | SHEIKA WING DINING AREA 9.110 | 9.110 SHEIKA WING DINING AREA | D
HQ | VAV0498 | ARCHIVE 10.005 | 10.005 SHEIKHA WING ARCHIVE | D->E
HQ | VAV0499 | EXEC. DIR. ARCH. COORD 10.006 | 10.006 EXEC DIR ARCH COORD | D
HQ | VAV0500 | EXEC. DIR. PROT. ASSIS. 10.007 | 10.007 EXEC DIR PROT ASSIS | D
HQ | VAV0501 | SCHED OFFICER 10.008 | 10.008 PROTOCOL DIR SCHED OFFICER | D->E
HQ | VAV0502 | CEREM. OFFICER 10.009 | 10.009 PROTOCOL DIR CEREMOFF | D->E
HQ | VAV0503 | CEREM. OFFICER 10.010 | 10.010 PROTOCOL DIR CEREMOFF | D->E
HQ | VAV0504 | CEREM. OFFICER 10.011 | 10.011 PROTOCOL DIR CEREMOFF | D->E
HQ | VAV0505 | TR. & VIS. OFFICER 10.012 | 10.012 PROTOCOL DIR TR AND VIS OFF | D->E
HQ | VAV0506 | TR. & VIS. OFFICER 10.013 | 10.013 PROTOCOL DIR TR AND VIS OFF | D->E
HQ | VAV0507 | SCHED OFFICER 10.015 | 10.015 PROTOCOL DIR SCHED OFFICER | D->E
HQ | VAV0508 | PLANNING ANALYST 10.016 | 10.016 PLANNING DIR PLANNING ANALYST | D->E
HQ | VAV0509 | STRAT. PLANNER 10.017 | 10.017 PLANNING DIR STRAT PLANNER | D->E
HQ | VAV0510 | PLANNING DIR. EXT. COORD 10.018 | 10.018 PLANNING DIR EXT COORD | D
HQ | VAV0511 | SEN. POLICY ANALYST 10.019 | 10.019 POLICY DIRSENPOLANALYST | D->E
HQ | VAV0512 | SEN. RESEARCH ANALYST 10.020 | 10.020 POLICY DIR SEN RESEARCH ANALYST | D->E
HQ | VAV0513 | RESEARCH ANALYST 10.021 | 10.021 POLICY DIRRESANALYST | D->E
HQ | VAV0514 | RESEARCH ANALYST 10.022 | 10.022 POLICY DIRRESANALYST | D->E
HQ | VAV0515 | HR OFFICER 10.023 | 10.023 SHSERVDIR HR OFFICER | D->E
HQ | VAV0516 | HR ASSISTANT 10.024 | 10.024 SHSERVDIR HR ASSISTANT | D->E
HQ | VAV0517 | PROCUR. REPRESENT 10.025 | 10.025 SHSERVDIR PROCUR REPRESENT | D->E
HQ | VAV0518 | SERVICE COORD 10.026 | 10.026 SHSERVDIR SERVICE COORD | D->E
HQ | VAV0519 | SERV. SUPERVISOR 10.027 | 10.027 SHSERVDIRGENSERVSUPERV | D->E
HQ | VAV0520 | FINANCE CONTROL 10.028 | 10.028 SHSERVDIR FINANCE CONTROL | D->E
HQ | VAV0521 | SERV. DIR. TR. & GU. SERV. 10.029 | 10.029 SERV DIR TR AND GU SERV | D
HQ | VAV0522 | HH-WING CORRIDOR 10.601 | 10.601 HH WING CORRIDOR | J
HQ | VAV0523 | COMM. DIR. DESIG. 10.031 | 10.031 COMMUNICDIRCOMM DESIGR | D->E
HQ | VAV0524 | COMM. DIR. EDITOR 10.032 | 10.032 COMMUNICDIRSPEECH EDITOR | D->E
HQ | VAV0525 | COMM. DIR. TRANSLTOR 10.033 | 10.033 COMMUNICDIR TRANSLATOR | D->E
HQ | VAV0526 | COMM. DIR. COORD 10.034 | 10.034 COMMUNICDIRPUBCOMMCOORD | D->E
HQ | VAV0527 | SUPP. OFFICER 10.035 | 10.035 SHSERVDIR IT SUPPORT OFFICER | D->E
HQ | VAV0528 | SH. SERV. DIR. ACCOUNUT. 10.036 | 10.036 SH SERV DIR ACCOUNUT | D
HQ | VAV0529 | SH. SERV. DIR. SR. ACCOUNT. 10.037 | 10.037 SHSERVDIRSENACCOUNTANT | D->E
HQ | VAV0530 | SHEIKHA WING STORAGE 10.001 | 10.001 SHEIKHA WING STORAGE | J
HQ | VAV0531 | SHEIKHA WING STORAGE 10.001 | 10.001 SHEIKHA WING STORAGE | J
HQ | VAV0532 | SHEIKHA WING STORAGE 10.001 | 10.001 SHEIKHA WING STORAGE | J
HQ | VAV0533 | BOARD ROOM WAITING 10.003 | 10.003 BOARD ROOM WAITING AREA | D->E
HQ | VAV0534 | BOARD ROOM WAITING 10.003 | 10.003 BOARD ROOM WAITING AREA | J->E
HQ | VAV0535 | ARCHIVE COORD 10.004 | 10.004 EXECDIRARCH COORD | D->E
HQ | VAV0536 | LOUNGE 10.106 | 10.106 LOUNGE | J
HQ | VAV0537 | NW LOUNGE 10.106 | 10.106 LOUNGE | J->E
HQ | VAV0538 | BOARD PREP. ROOM 10.109 | 10.109 BOARD PREP ROOM | D
HQ | VAV0539 | CONSULTANT SPACE 10.101 | 10.101 CONSULTANT SPACE | J
HQ | VAV0540 | CONSULTANT SPACE 10.101 | 10.101 CONSULTANT SPACE | J
HQ | VAV0541 | AV ROOM 10.112 | 10.112 TRANSLATOR ROOM | D->E
HQ | VAV0542 | HH-WING CORRIDOR 10.601 | 10.601 HH WING CORRIDOR | D
HQ | VAV0543 | HH-WING CORRIDOR 10.601 | 10.601 HH WING CORRIDOR | D
HQ | VAV0544 | HH-WING CORRIDOR 10.601 | 10.601 HH WING CORRIDOR | D
HQ | VAV0545 | HH-WING CORRIDOR 10.601 | 10.601 HH WING CORRIDOR | D
HQ | VAV0546 | HH-WING CORRIDOR 10.601 | 10.601 HH WING CORRIDOR | D
HQ | VAV0547 | SHEIKHA WING MULTIPURPOSE ROOM 10.102 | 10.102 SHEIKHA WING MULTI PURPOSE ROOM | D
HQ | VAV0548 | OFFICE SPACE 10.002E | 10.002E OFFICE SPACE | D
HQ | VAV0549 | OFFICE SPACE 10.002D | 10.002D OFFICE SPACE | D
HQ | VAV0550 | OFFICE SPACE 10.002C | 10.002C OFFICE SPACE | D
HQ | VAV0551 | OFFICE SPACE 10.002A | 10.002A OFFICE SPACE | D
HQ | VAV0552 | PLANNING DIR. 11.012 | 11.012 PLANNING DIR DIR PLANNING | D->E
HQ | VAV0553 | EXEC. DIR. CORR. 11.013 | 11.013 EXECDIRCORRF UP | D->E
HQ | VAV0554 | EXEC. DIR. CORR. MANAGER 11.014 | 11.014 EXEC DIR CORR MANAGER | D
HQ | VAV0555 | EXEC. DIR. CORR. 11.015 | 11.015 EXECDIRCORRF UP | D->E
HQ | VAV0556 | LEGAL ASSIST. 11.016 | 11.016 EXECDIR LEGAL ASSIST | D->E
HQ | VAV0557 | LEGAL ADVISOR 11.017 | 11.017 EXECDIR LEGAL ADVISOR | D->E
HQ | VAV0559 | LEGAL ADVISOR 11.018 | 11.018 EXECDIREXECASSIST | D->E
HQ | VAV0560 | DEP. EXEC. DIRECTOR 11.019 | 11.019 EXECDIR DEP EXEC DIRECTOR | D->E
HQ | VAV0561 | EXEC. ASSI. 11.020 | 11.020 EXECDIREXECASSIST | D->E
HQ | VAV0562 | EXEC. DIRECTOR 11.021 | 11.021 EXECDIR EXEC DIRECTOR | D->E
HQ | VAV0564 | SHEIKHA WING WAITING ROOM 11.022 | 11.022 SHEIKHA WING WAITING ROOM | D
HQ | VAV0565 | SHEIKHA WING WAITING ROOM 11.022 | 11.022 SHEIKHA WING WAITING ROOM | J
HQ | VAV0567 | SECURITY ROOM 11.023 | 11.023 SHEIKHA WING SECURITY ROOM | D->E
HQ | VAV0568 | COMMUNICATION DIR. 11.001 | 11.001 COMMUNICDIR COMMUNICATION DIRECTOR | D->E
HQ | VAV0570 | MED. REL. OFFICER 11.002 | 11.002 COMMUNICDIR MED REL OFFICER | D->E
HQ | VAV0571 | DIR. SHARED SERVICES 11.003 | 11.003 SHSERVDIR DIR SHARED SERVICES | D->E
HQ | VAV0573 | ADM. ASSI. 11.004 | 11.004 EXECDIRECTOR ADMASSIST | D->E
HQ | VAV0574 | PROTOCOL DIR. 11.005 | 11.005 PROTOCOL DIRPROTOCOL DIRECTOR | D->E
HQ | VAV0575 | GIFT DIR. 11.006 | 11.006 PROTOCOL DIRGIFTS DIRECTOR | D->E
HQ | VAV0576 | EXEC. DIR. CONSULTANT 11.008 | 11.008 EXEC DIR CONSULTANT | D
HQ | VAV0577 | SEC. 11.009 | 11.009 SECRETARY | D->E
HQ | VAV0578 | DIR. OF POL. & RES. 11.010 | 11.010 POLICY DIR OF POL AND RES | D->E
HQ | VAV0579 | SECRETARY 11.011 | 11.011 SECRETARY | J
HQ | VAV0580 | SHEIKHA WING BUSINESS LOUNGE 11.103 | 11.103 SHEIKHA WING BUSINESS LOUNGE | D
HQ | VAV0581 | SHEIKHA WING BUSINESS LOUNGE 11.103 | 11.103 SHEIKHA WING BUSINESS LOUNGE | D
HQ | VAV0582 | SHEIKHA WING LOBBY 11.201 | 11.201 SHEIKHA WING LOBBY | D
HQ | VAV0583 | SHEIKHA WING LOBBY 11.201 | 11.201 SHEIKHA WING LOBBY | J
HQ | VAV0584 | SHEIKHA WING SHEIKHA ENSUIT 11.202 | 11.208 SHEIKHA WING SHEIKHA ENSUIT | J
HQ | VAV0585 | SHEIKHA WING SHEIKHA ENSUIT 11.202 | 11.208 SHEIKHA WING SHEIKHA ENSUIT | J
HQ | VAV0586 | SHEIKHA WING SHEIKHA ENSUIT 11.202 | 11.208 SHEIKHA WING SHEIKHA ENSUIT | J
HQ | VAV0587 | SHEIKHA WING SHEIKHA ENSUIT 11.202 | 11.208 SHEIKHA WING SHEIKHA ENSUIT | J
HQ | VAV0588 | SHEIKHA WING RELAX AREA 11.203 | 11.203 SHEIKHA WING RELAX AREA | J
HQ | VAV0589 | SHEIKHA WING RELAX AREA 11.203 | 11.203 SHEIKHA WING RELAX AREA | J
HQ | VAV0590 | SHEIKHA WING MEETING ROOM 11.204 | 11.204 SHEIKHA WING MEETING ROOM | J
HQ | VAV0591 | SHEIKHA WING MEETING ROOM 11.204 | 11.204 SHEIKHA WING MEETING ROOM | J
HQ | VAV0592 | VISITORS CENTER 08 | 8.400 VISITORS CENTER | D->E
HQ | VAV0593 | VISITORS CENTER 08 | 8.400 VISITORS CENTER | D->E
HQ | VAV0594 | VISITORS CENTER 08 | 8.400 VISITORS CENTER | D->E
HQ | VAV0595 | ROOM B.109 | B1.116 SHEIKHA LOBBY | J
HQ | VAV0596 | OFFICE SPACE 04.015B | 4.015B OFFICE SPACE | D
HQ | VAV0597 | OFFICE SPACE 04.001A | 4.001A OFFICE SPACE | D
HQ | VAV0598 | OFFICE SPACE 04.001E | 4.001E OFFICE SPACE | D
HQ | VAV0599 | OFFICE SPACE 04.001C | 4.001C OFFICE SPACE | D
HQ | VAV0600 | OFFICE SPACE 04.001H | 4.001H OFFICE SPACE | D
HQ | VAV0601 | OFFICE SPACE 10.002B | 10.002B OFFICE SPACE | D
HQ | VAV0602 | EXEC. DIR. CONSULTANT 11.007 | 11.007 EXEC DIR CONSULTANT | D
HQ | VAV0603 | SHEIKHA WING CORRIDOR 11.601 | 11.601 SHEIKA WING CORRIDOR NE | J
HQ | VAV0604 | SHEIKHA WING CORRIDOR 11.601 | 11.601 SHEIKA WING CORRIDOR NE | D
HQ | VAV0605 | HH WING BUSINESS LOUNGE 11.102 | 11.102 HH WING BUSINESS LOUNGE | D
HQ | VAV0606 | HH WING BUSINESS LOUNGE 11.102 | 11.102 HH WING BUSINESS LOUNGE | D
HQ | VAV0607 | PR & MARKET STAFF G.013 | G.013 PR AND MARKET STAFF | J
HQ | VAV0608 | TOILET G.405 | G.405 TOILET | D
QNL | AHUB001 | Basement Level Zone 4 Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D->E
QNL | AHUB002 | Basement Level Zone 1 Plant Room 1 B.063 | B.063 PLANT ROOM 01 | D->E
QNL | AHUB003 | Basement Level Zone 1 Plant Room 2 B.070 | B.070 PLANT ROOM 02 | D->E
QNL | AHUB004 | Basement Level Zone 2 Plant Room 3 B.110 | B.110 PLANT ROOM 03 | D->E
QNL | AHUB005 | Basement Level Zone 4 Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D->E
QNL | AHUB006 | Basement Level Zone 4 Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D->E
QNL | AHUB007 | Basement Level Zone 4 Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D->E
QNL | AHUB008 | Basement Level Zone 4 Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D->E
QNL | AHUB009 | Basement Level Zone 2 Plant Room 3 B.110 | B.110 PLANT ROOM 03 | D->E
QNL | AHUB010 | Basement Level Zone 1 Plant Room 2 B.070 | B.070 PLANT ROOM 02 | D->E
QNL | AHUB011 | Basement Level Zone 1 Plant Room 1 B.063 | B.063 PLANT ROOM 01 | D->E
QNL | AHUB012 | Basement Level Zone 1 Plant Room 1 B.063 | B.063 PLANT ROOM 01 | D->E
QNL | AHUB013 | Basement Level Zone 1 Plant Room 2 B.070 | B.070 PLANT ROOM 02 | D->E
QNL | AHUB014 | Basement Level Zone 2 Plant Room 3 B.110 | B.110 PLANT ROOM 03 | D->E
QNL | AHUB015 | Basement Level Zone 2 Plant Room 3 B.110 | B.110 PLANT ROOM 03 | D->E
QNL | FCU_1F_001 | IDF ROOM T1.323 | T1.323 IDF ROOM | D
QNL | FCU_1F_002 | ICT Room 02 L1.030 | L1.030 ICT ROOM 02 | D
QNL | FCU_1F_003 | IDF Room 02 L1.099 | L1.099 IDF ROOM 02 | D
QNL | FCU_1F_004 | BRIDGE CEILING VOID L1.BR6 | BR6 BRIDGE CEILING VOID | D
QNL | FCU_1F_005 | BRIDGE CEILING VOID L1.BR6 | BR6 BRIDGE CEILING VOID | D
QNL | FCU_1F_006 | BRIDGE CEILING VOID L1.BR6 | BR6 BRIDGE CEILING VOID | D
QNL | FCU_1F_007 | BRIDGE CEILING VOID L1.BR6 | BR6 BRIDGE CEILING VOID | D
QNL | FCU_1F_008 | BRIDGE CEILING VOID L1.BR6 | BR6 BRIDGE CEILING VOID | D
QNL | FCU_1F_009 | BRIDGE CEILING VOID L1.BR5 | BR5 BRIDGE CEILING VOID | D
QNL | FCU_1F_010 | BRIDGE CEILING VOID L1.BR5 | BR5 BRIDGE CEILING VOID | D
QNL | FCU_1F_011 | BRIDGE CEILING VOID L1.BR5 | BR5 BRIDGE CEILING VOID | D
QNL | FCU_1F_012 | BRIDGE CEILING VOID L1.BR5 | BR5 BRIDGE CEILING VOID | D
QNL | FCU_1F_013 | BRIDGE CEILING VOID L1.BR6 | BR6 BRIDGE CEILING VOID | D
QNL | FCU_1F_014 | BRIDGE CEILING VOID L1.BR4 | BR4 BRIDGE CEILING VOID | D
QNL | FCU_1F_015 | BRIDGE CEILING VOID L1.BR6 | BR6 BRIDGE CEILING VOID | D
QNL | FCU_1F_016 | BRIDGE CEILING | BC1 BRIDGE CEILING | D
QNL | FCU_1F_017 | VOID L1.BR4 | BR4 BRIDGE CEILING VOID | D->E
QNL | FCU_1F_018 | VOID L1.BR4 | BR4 BRIDGE CEILING VOID | D->E
QNL | FCU_1F_019 | BRIDGE CEILING VOID L1.BR5 | BR5 BRIDGE CEILING VOID | D
QNL | FCU_1F_020 | BRIDGE CEILING VOID L1.BR3 | BR3 BRIDGE CEILING VOID | D
QNL | FCU_1F_021 | BRIDGE CEILING VOID L1.BR5 | BR5 BRIDGE CEILING VOID | D
QNL | FCU_1F_022 | BRIDGE CEILING VOID L1.BR3 | BR3 BRIDGE CEILING VOID | D
QNL | FCU_1F_023 | BRIDGE CEILING VOID L1.BR3 | BR3 BRIDGE CEILING VOID | D
QNL | FCU_1F_024 | BRIDGE CEILING VOID L1.BR3 | BR3 BRIDGE CEILING VOID | D
QNL | FCU_1F_025 | BRIDGE CEILING VOID L1.BR2 | BR2 BRIDGE CEILING VOID | D
QNL | FCU_1F_026 | BRIDGE CEILING VOID L1.BR4 | BR4 BRIDGE CEILING VOID | D
QNL | FCU_1F_027 | BRIDGE CEILING VOID L1.BR2 | BR2 BRIDGE CEILING VOID | D
QNL | FCU_1F_028 | BRIDGE CEILING VOID L1.BR4 | BR4 BRIDGE CEILING VOID | D
QNL | FCU_1F_029 | BRIDGE CEILING VOID L1.BR2 | BR2 BRIDGE CEILING VOID | D
QNL | FCU_1F_030 | BRIDGE CEILING VOID L1.BR2 | BR2 BRIDGE CEILING VOID | D
QNL | FCU_1F_031 | BRIDGE CEILING VOID L1.BR1 | BR1 BRIDGE CEILING VOID | D
QNL | FCU_1F_032 | BRIDGE CEILING VOID L1.BR1 | BR1 BRIDGE CEILING VOID | D
QNL | FCU_1F_033 | BRIDGE CEILING VOID L1.BR1 | BR1 BRIDGE CEILING VOID | D
QNL | FCU_1F_034 | BRIDGE CEILING VOID L1.BR1 | BR1 BRIDGE CEILING VOID | D
QNL | FCU_1F_035 | BRIDGE CEILING VOID L1.BR2 | BR2 BRIDGE CEILING VOID | D
QNL | FCU_1F_036 | BRIDGE CEILING VOID L1.BR2 | BR2 BRIDGE CEILING VOID | D
QNL | FCU_1F_037 | BRIDGE CEILING VOID L1.BR3 | BR3 BRIDGE CEILING VOID | D
QNL | FCU_1F_038 | BRIDGE CEILING VOID L1.BR3 | BR3 BRIDGE CEILING VOID | D
QNL | FCU_1F_039 | BRIDGE CEILING VOID L1.BR4 | BR4 BRIDGE CEILING VOID | D
QNL | FCU_1F_040 | BRIDGE CEILING VOID L1.BR4 | BR4 BRIDGE CEILING VOID | D
QNL | FCU_1F_041 | BRIDGE CEILING | BC2 BRIDGE CEILING | D
QNL | FCU_1F_042 | VOID L1.BR5 | BR5 BRIDGE CEILING VOID | D->E
QNL | FCU_1F_043 | BRIDGE CEILING VOID L1.BR6 | BR6 BRIDGE CEILING VOID | D
QNL | FCU_1F_044 | BRIDGE CEILING VOID L1.BR6 | BR6 BRIDGE CEILING VOID | D
QNL | FCU_1F_045 | BRIDGE CEILING VOID L1.BR6 | BR6 BRIDGE CEILING VOID | D
QNL | FCU_1F_046 | BRIDGE CEILING VOID L1.BR6 | BR6 BRIDGE CEILING VOID | D
QNL | FCU_1F_047 | BRIDGE CEILING VOID L1.BR1 | BR1 BRIDGE CEILING VOID | D
QNL | FCU_1F_048 | BRIDGE CEILING VOID L1.BR1 | BR1 BRIDGE CEILING VOID | D
QNL | FCU_1F_049 | BRIDGE CEILING VOID L1.BR2 | BR2 BRIDGE CEILING VOID | D
QNL | FCU_1F_050 | BRIDGE CEILING VOID L1.BR2 | BR2 BRIDGE CEILING VOID | D
QNL | FCU_1F_051 | BRIDGE CEILING VOID L1.BR4 | BR4 BRIDGE CEILING VOID | D
QNL | FCU_1F_052 | BRIDGE CEILING VOID L1.BR4 | BR4 BRIDGE CEILING VOID | D
QNL | FCU_1F_053 | BRIDGE CEILING VOID L1.BR5 | BR5 BRIDGE CEILING VOID | D
QNL | FCU_1F_054 | BRIDGE CEILING VOID L1.BR5 | BR5 BRIDGE CEILING VOID | D
QNL | FCU_1F_055 | VESTIBULE L1 | L1.990 VESTIBULE | D->E
QNL | FCU_1F_056 | External Book Drop L1 | L1.991 EXTERNAL BOOK DROP | D->E
QNL | FCU_1F_057 | ILL DIRECTOR L1.144 | L1.144 ILL DIRECTOR | D
QNL | FCU_1F_058 | ILL DIRECTOR L1.145 | L1.145 ILL DIRECTOR | D
QNL | FCU_1F_059 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | FCU_1F_060 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | FCU_1F_061 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | FCU_1F_062 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | FCU_1F_063 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | FCU_1F_064 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | FCU_1F_065 | BRIDGE IDF L1.BI | BI BRIDGE IDF | D
QNL | FCU_2F_001 | IDF ROOM T1.275 | T1.275 IDF ROOM | D
QNL | FCU_2F_002 | IDF ROOM T1.276 | T1.276 IDF ROOM | D
QNL | FCU_2F_003 | IDF ROOM T1.171 | T1.171 IDF ROOM | D
QNL | FCU_2F_004 | IDF ROOM T1.1714 | T1.1714 IDF ROOM | D
QNL | FCU_2F_005 | MDF Room L2.009 | L2.009 KDF ROOM | D->E
QNL | FCU_2F_034 | Auditorium High Levlel in Ceiling Void L2.087 | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | D
QNL | FCU_2F_035 | Auditorium High Levlel in Ceiling Void L2.087 | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | D
QNL | FCU_2F_036 | Auditorium High Levlel in Ceiling Void L2.087 | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | D
QNL | FCU_2F_037 | Auditorium High Levlel in Ceiling Void L2.087 | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | D
QNL | FCU_2F_038 | Auditorium Booths L2.087 | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | D->E
QNL | FCU_2F_039 | Auditorium Booths L2.087 | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | D->E
QNL | FCU_2F_040 | Auditorium Booths L2.087 | L2.087 AUDITORIUM HIGH LEVLEL IN CEILING VOID | D->E
QNL | FCU_2F_041 | Bridge Raised Floor L2.088 | L2.088 BRIDGE RAISED FLOOR | D
QNL | FCU_2F_042 | STUDY AREA L2.088 | L2.088 BRIDGE RAISED FLOOR | D->E
QNL | FCU_2F_043 | Bridge L2.088 | L2.088 BRIDGE RAISED FLOOR | D->E
QNL | FCU_2F_044 | Bridge L2.088 | L2.088 BRIDGE RAISED FLOOR | D->E
QNL | FCU_2F_045 | Group Study Room L2.081 | L2.081 GROUP STUDY ROOM | D
QNL | FCU_2F_046 | Group Study Room L2.076 | L2.076 GROUP STUDY ROOM | D
QNL | FCU_2F_047 | Group Study Room L2.076 | L2.076 GROUP STUDY ROOM | D
QNL | FCU_2F_048 | INDIVIDUAL STUDY ROOM L2.070 | L2.070 INDIVISTUDY ROOM | D->E
QNL | FCU_2F_049 | INDIVIDUAL STUDY ROOM L2.070 | L2.070 INDIVISTUDY ROOM | D->E
QNL | FCU_2F_050 | INDIVIDUAL STUDY ROOM L2.070 | L2.070 INDIVISTUDY ROOM | D->E
QNL | FCU_2F_051 | INDIVIDUAL STUDY ROOM L2.073 | L2.073 INDIVISTUDY ROOM | D->E
QNL | FCU_2F_052 | INDIVIDUAL STUDY ROOM L2.073 | L2.073 INDIVISTUDY ROOM | D->E
QNL | FCU_2F_053 | INDIVIDUAL STUDY ROOM L2.073 | L2.073 INDIVISTUDY ROOM | D->E
QNL | FCU_2F_054 | Bridge Raised Floor L2.088 | L2.088 LOUNGE AREA | D
QNL | FCU_2F_055 | Bridge Raised Floor L2.088 | L2.088 LOUNGE AREA | D
QNL | FCU_2F_056 | North East Core T1.021 | T1.021 OPEN STUDY TERRACE | D->E
QNL | FCU_2F_057 | North East Core T1.021 | T1.021 OPEN STUDY TERRACE | D->E
QNL | FCU_2F_058 | North East Core T1.021 | T1.021 OPEN STUDY TERRACE | D->E
QNL | FCU_2F_059 | North East Core T1.021 | T1.021 OPEN STUDY TERRACE | D->E
QNL | FCU_2F_060 | North West Core T1.020 | T1.020 OPEN LOUNGE TERRACE | D->E
QNL | FCU_2F_061 | North West Core T1.020 | T1.020 OPEN LOUNGE TERRACE | D->E
QNL | FCU_2F_062 | North West Core T1.020 | T1.020 OPEN LOUNGE TERRACE | D->E
QNL | FCU_B_001 | IDF ROOM B.155 | B.155 FACULTY CARRELS | D->E
QNL | FCU_B_002 | FUMIGATION B.085 | B.085 FUMIGATION ROOM | D->E
QNL | FCU_B_003 | IDF (Corridor) B.062 | B.062 IDF CORRIDOR | D
QNL | FCU_B_004 | IDF FM Storage B.215 | B.215 IDF FM STORAGE | D
QNL | FCU_B_005 | HL Plant Room B.140 | B.140 HL PLANT ROOM | D
QNL | FCU_B_006 | Fire Command ROOM B.071 | B.071 FIRE COMMAND ROOM | D
QNL | FCU_B_007 | Sprinklers Pumps ROOM B.072 | B.072 SPRIMKLERS PUMPS AND ZONES VALVES | D->E
QNL | FCU_B_008 | GAS SUPPRESSION ROOM B.087 | B.087 GAS SUPPRESSION ROOM | D
QNL | FCU_B_009 | PEOPLE MOVER ROOM B.088 | B.088 PEOPLE MOVER PLANT | D->E
QNL | FCU_B_010 | Security Contol Room B.105 | B.105 SECURITY CONTOL ROOM | D
QNL | FCU_B_011 | Plant Room 1 B.063 | B.063 PLANT ROOM 01 | D
QNL | FCU_B_012 | Plant Room 1 B.063 | B.063 PLANT ROOM 01 | D
QNL | FCU_B_013 | Plant Room 2 B.070 | B.070 PLANT ROOM 02 | D
QNL | FCU_B_014 | Plant Room 2 B.070 | B.070 PLANT ROOM 02 | D
QNL | FCU_B_015 | Plant Room 3 B.110 | B.110 PLANT ROOM 03 | D
QNL | FCU_B_016 | Plant Room 3 B.110 | B.110 PLANT ROOM 03 | D
QNL | FCU_B_017 | Plant Room 3 B.110 | B.110 PLANT ROOM 03 | D
QNL | FCU_B_018 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | FCU_B_019 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | FCU_B_020 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | FCU_B_021 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | FCU_B_022 | FM Storage B.210 | B.210 FM STORAGE | D
QNL | FCU_B_023 | FM Storage B.210 | B.210 FM STORAGE | D
QNL | FCU_B_024 | PH Plant ROOM B.211 | B.211 PH PLANT ROOM | D
QNL | FCU_B_025 | MISTING PUMP ROOM B.212 | B.212 MISTING PUMP ROOM | D
QNL | FCU_B_026 | MISTING PUMP ROOM B.212 | B.212 MISTING PUMP ROOM | D
QNL | FCU_B_027 | Sorting Shelving Room B.121 | B.121 SORTING SHELVING ROOM | D
QNL | FCU_B_028 | Sorting Shelving Room B.121 | B.121 SORTING SHELVING ROOM | D
QNL | FCU_B_029 | B.145.05 | B.145 LOBY AND CSECURITY | D->E
QNL | FCU_B_030 | WATER FEATURE ROOM B.226 | B.226 PUMP RM 4 | J
QNL | FCU_B_031 | IDF ROOM B.215A | B.215A IDF | D->E
QNL | FCU_B_032 | Shell Space-Special Collection B.132 | B.132 SHELL SPACE SPECIAL COLLECTION | D
QNL | FCU_B_033 | Shell Space-Special Collection B.132 | B.132 SHELL SPACE SPECIAL COLLECTION | D
QNL | FCU_B_034 | Shell Space-Special Collection B.132 | B.132 SHELL SPACE SPECIAL COLLECTION | D
QNL | FCU_B_035 | Shell Space-Special Collection B.132 | B.132 SHELL SPACE SPECIAL COLLECTION | D
QNL | FCU_B_036 | IT Office B.122 | B.122 IT OFFICE | D
QNL | FCU_B_037 | DIGITALIZATION SERVER SPACE B.215A | B.215A IDF | D->E
QNL | FCU_B_038 | ELEC. B.145 | B.145 LOBY AND CSECURITY | D->E
QNL | VAV_1F_S11_001 | Group Study Room1 L1.026 | L1.026 GROUP STUDY ROOM1 | D
QNL | VAV_1F_S11_002 | Group Study Room2 L1.027 | L1.027 GROUP STUDY ROOM2 | D
QNL | VAV_1F_S11_003 | Group Study Room3 L1.028 | L1.028 GROUP STUDY ROOM3 | D
QNL | VAV_1F_S11_004 | Information Literacy Instr 1 L1.020 | L1.020 INFO LITERACY INSTR1 | D->E
QNL | VAV_1F_S11_005 | Information Literacy Instr 1 L1.020 | L1.020 INFO LITERACY INSTR1 | D->E
QNL | VAV_1F_S11_006 | Infor. Lteracy Instr.2 L1.021 | L1.021 INFOR LTERACY INSTR 2 | D
QNL | VAV_1F_S11_007 | Infor. Lteracy Instr.2 L1.021 | L1.021 INFOR LTERACY INSTR 2 | D
QNL | VAV_1F_S11_008 | Infor. Lteracy Instr.2 L1.021 | L1.021 INFOR LTERACY INSTR 2 | D
QNL | VAV_1F_S11_009 | Infor. Lteracy Instr.2 L1.021 | L1.021 INFOR LTERACY INSTR 2 | D
QNL | VAV_1F_S11_010 | Infor. Lteracy Instr.2 L1.021 | L1.021 INFOR LTERACY INSTR 2 | D
QNL | VAV_1F_S11_011 | Infor. Lteracy Instr.2 L1.021 | L1.021 INFOR LTERACY INSTR 2 | D
QNL | VAV_1F_S11_012 | Infor. Lteracy Instr.2 L1.021 | L1.021 INFOR LTERACY INSTR 2 | D
QNL | VAV_1F_S11_013 | Infor. Lteracy Instr.2 L1.021 | L1.021 INFOR LTERACY INSTR 2 | D
QNL | VAV_1F_S11_014 | Computer Classroom L1.022 | L1.022 COMPUTER CLASS RM | D
QNL | VAV_1F_S11_015 | Computer Classroom L1.022 | L1.022 COMPUTER CLASS RM | D
QNL | VAV_1F_S11_016 | Computer Classroom L1.022 | L1.022 COMPUTER CLASS RM | D
QNL | VAV_1F_S11_017 | Computer Classroom L1.022 | L1.022 COMPUTER CLASS RM | D
QNL | VAV_1F_S11_018 | Computer Classroom L1.022 | L1.022 COMPUTER CLASS RM | D
QNL | VAV_1F_S11_019 | Computer Classroom L1.022 | L1.022 COMPUTER CLASS RM | J
QNL | VAV_1F_S11_020 | Computer Classroom L1.022 | L1.022 COMPUTER CLASS RM | D
QNL | VAV_1F_S11_021 | Computer Classroom L1.022 | L1.022 COMPUTER CLASS RM | D
QNL | VAV_1F_S11_022 | Group Study Room 4 L1.029 | L1.029 GROUP STUDY ROOM 4 | D
QNL | VAV_1F_S11_087 | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 | L1.023 CORRIDOR | D->E
QNL | VAV_1F_S11_088 | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 | L1.023 CORRIDOR | D->E
QNL | VAV_1F_S11_089 | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 | L1.023 CORRIDOR | D->E
QNL | VAV_1F_S11_090 | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 | L1.023 CORRIDOR | D->E
QNL | VAV_1F_S15_001 | Media Studio1 L1.063 | L1.063 MEDIA STUDIO 1 | D
QNL | VAV_1F_S15_002 | Media Studio1 L1.063 | L1.063 MEDIA STUDIO 1 | D
QNL | VAV_1F_S15_003 | Media Studio2 L1.065 | L1.065 MEDIA STUDIO 1 | D->E
QNL | VAV_1F_S15_004 | Media Studio2 L1.065 | L1.065 MEDIA STUDIO 1 | D->E
QNL | VAV_1F_S15_005 | Head Librarian Office L1.040 | L1.040 HEAD LIBRARIAN OFFICE | D
QNL | VAV_1F_S15_006 | Children Library - Pre School Reading & Playing L1.047 | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | D
QNL | VAV_1F_S15_007 | Children Library - Pre School Reading & Playing L1.047 | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | D
QNL | VAV_1F_S15_008 | Children Library - Pre School Reading & Playing L1.047 | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | D
QNL | VAV_1F_S15_009 | CHILDRENS LIBRARY-PRE SCHOOL COLLECTION L1.047 | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | D->E
QNL | VAV_1F_S15_010 | CHILDRENS LIBRARY-PRE SCHOOL COLLECTION L1.047 | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | D->E
QNL | VAV_1F_S15_011 | CHILDRENS LIBRARY-PRE SCHOOL COLLECTION L1.047 | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | D->E
QNL | VAV_1F_S15_012 | Staff Office L1.048 | L1.048 STAFF OFFICE | D
QNL | VAV_1F_S15_021 | Prayer Room (Female) L1.104 | L1.104 PRAYER ROOM FEMALE | D
QNL | VAV_1F_S15_022 | Prayer Room (Female) L1.104 | L1.104 PRAYER ROOM FEMALE | D
QNL | VAV_1F_S15_023 | Prayer Room (Male) L1.104 | L1.104 PRAYER ROOM FEMALE | D
QNL | VAV_1F_S15_024 | Prayer Room (Male) L1.104 | L1.104 PRAYER ROOM FEMALE | D
QNL | VAV_1F_S15_025 | Ablution (Women) L1.106 | L1.106 ABLUTION WOMEN | D
QNL | VAV_1F_S15_038 | Ablution (Men) L1.105 | L1.105 ABLUTION MEN | D
QNL | VAV_1F_S15_039 | Green Room L1.002A | L1.002A GREEM ROOM | D->E
QNL | VAV_1F_S15_039S | Staff Office L1.048 | L1.048 STAFF OFFICE | D
QNL | VAV_1F_S15_040 | Green Room L1.002A | L1.002A GREEM ROOM | D->E
QNL | VAV_1F_S15_096 | Multipurpose Room L1.041 | L1.041 MULTIPURPOSE ROOM | D
QNL | VAV_1F_S15_097 | Multipurpose Room L1.041 | L1.041 MULTIPURPOSE ROOM | D
QNL | VAV_1F_S15_098 | Multipurpose Room L1.041 | L1.041 MULTIPURPOSE ROOM | D
QNL | VAV_2F_S10_001 | GULF MATERIAL L2 | L2.992 GULF MATERIAL | D->E
QNL | VAV_2F_S10_002 | GULF MATERIAL L2 | L2.992 GULF MATERIAL | D->E
QNL | VAV_2F_S10_003 | GULF MATERIAL L2 | L2.992 GULF MATERIAL | D->E
QNL | VAV_2F_S10_004 | GULF MATERIAL L2 | L2.992 GULF MATERIAL | D->E
QNL | VAV_2F_S10_005 | GULF MATERIAL L2 | L2.992 GULF MATERIAL | D->E
QNL | VAV_2F_S10_006 | GULF MATERIAL L2 | L2.992 GULF MATERIAL | D->E
QNL | VAV_2F_S12_001 | OPEN READING AREA L1.001 | L1.001 OPEN READING AREA | D
QNL | VAV_2F_S12_002 | OPEN READING AREA L1.001 | L1.001 OPEN READING AREA | D
QNL | VAV_2F_S12_003 | OPEN READING AREA L1.001 | L1.001 OPEN READING AREA | D
QNL | VAV_2F_S12_004 | OPEN READING AREA L1.001 | L1.001 OPEN READING AREA | D
QNL | VAV_2F_S12_005 | OPEN READING AREA L1.001 | L1.001 OPEN READING AREA | D
QNL | VAV_2F_S12_006 | OPEN READING AREA L1.001 | L1.001 OPEN READING AREA | D
QNL | VAV_2F_S12_007 | OPEN READING AREA L1.001 | L1.001 OPEN READING AREA | D
QNL | VAV_2F_S12_008 | OPEN READING AREA L1.001 | L1.001 OPEN READING AREA | D
QNL | VAV_2F_S12_009 | OPEN READING AREA L1.001 | L1.001 OPEN READING AREA | D
QNL | VAV_2F_S12_010 | BRAILLE READER L1.002 | L1.002 BRAILLE READER | D
QNL | VAV_2F_S12_011 | BRAILLE READER L1.002 | L1.002 BRAILLE READER | D
QNL | VAV_2F_S12_012 | TUTORING HEAD L1.003 | L1.003 TUTORING HEAD | D
QNL | VAV_2F_S12_013 | WRITING ROOM 1 L1.004 | L1.004 WRITING ROOM 1 | D
QNL | VAV_2F_S12_014 | WRITING HEAD L1.005 | L1.005 WRITING ROOM 2 | D->E
QNL | VAV_2F_S12_015 | WRITING ROOM 2 L1.005 | L1.005 WRITING ROOM 2 | D
QNL | VAV_2F_S12_016 | STUDENT CARRELS L1.007 | L1.007 STUDENT CARRELS | D
QNL | VAV_2F_S12_017 | STUDENT CARRELS L1.007 | L1.007 STUDENT CARRELS | D
QNL | VAV_2F_S12_018 | STUDENT CARRELS L1.007 | L1.007 STUDENT CARRELS | D
QNL | VAV_2F_S12_019 | STUDENT CARRELS L1.007 | L1.007 STUDENT CARRELS | D
QNL | VAV_2F_S12_020 | STUDENT CARRELS L1.007 | L1.007 STUDENT CARRELS | D
QNL | VAV_2F_S12_021 | Breakout Space L2.010 | L2.010 BREAKOUT SPACE | D
QNL | VAV_2F_S12_022 | Circulation Office L2.011 | L2.011 CIRCULATION OFFICE | D
QNL | VAV_2F_S12_023 | Office SpL Collection L2.012 | L2.012 OFFICE SPEC COL | D->E
QNL | VAV_2F_S12_024 | Office SpL Collection L2.013 | L2.013 OFFICE SPEC COL | D->E
QNL | VAV_2F_S12_025 | CORRIDOR L2 | L2.993 CORRIDOR | D->E
QNL | VAV_2F_S12_026 | Group Study Room 5 L2.015 | L2.011 CIRCULATION OFFICE | D
QNL | VAV_2F_S12_027 | Group Study Room 7 L2.017 | L2.017 40 GROUP STUDY ROOM 7 | D
QNL | VAV_2F_S12_028 | Meeting Room L2.018 | L2.018 GROUP STUDY ROOM 8 | D->E
QNL | VAV_2F_S12_029 | Group Study Room 6 L2.016 | L2.017 40 GROUP STUDY ROOM 7 | D
QNL | VAV_2F_S12_097 | Group Study Room 8 L2.018 | L2.018 GROUP STUDY ROOM 8 | D
QNL | VAV_2F_S13_001 | Lib. Director's Room L2.044 | L2.044 LIB DIRECTOR S ROOM | D
QNL | VAV_2F_S13_002 | Lib. Director's Room L2.044 | L2.044 LIB DIRECTOR S ROOM | D
QNL | VAV_2F_S13_003 | Service & Lounge L2.043 | L2.043 SERVICE AND LOUNGE | D
QNL | VAV_2F_S13_004 | OPEN OFFICE L2.025 | L2.014 TRANS SPC AND SPACE ED | D
QNL | VAV_2F_S13_005 | ACADEMIC PERS. LIBRARIA L2.022 | L2.021 LIBR COM REL SPC AND EVENTS SPC | D
QNL | VAV_2F_S13_006 | ACD PERS LIBRARIAN L2.022 | L2.022 ACADEMIC PERS LIBRARIA | D->E
QNL | VAV_2F_S13_007 | AD ADMIN & PLANNING L2.023 | L2.023 AD ADMIN AND PLANNING | D
QNL | VAV_2F_S13_008 | Office Coord L2.024 | L2.024 OFFICE COORD | D
QNL | VAV_2F_S13_009 | OPEN OFFICE L2.025 | L2.025 OPEN OFFICE | D
QNL | VAV_2F_S13_010 | CORRIDOR L2 | L2.993 CORRIDOR | D->E
QNL | VAV_2F_S13_011 | CORRIDOR L2 | L2.993 CORRIDOR | D->E
QNL | VAV_2F_S13_012 | CORRIDOR L2 | L2.993 CORRIDOR | D->E
QNL | VAV_2F_S13_013 | CORRIDOR L2 | L2.993 CORRIDOR | D->E
QNL | VAV_2F_S13_014 | CORRIDOR L2 | L2.993 CORRIDOR | D->E
QNL | VAV_2F_S13_015 | CORRIDOR L2 | L2.993 CORRIDOR | D->E
QNL | VAV_2F_S13_016 | VIP Waiting ROOM L2.048 | L2.048 VIP WATING | D->E
QNL | VAV_2F_S14_001 | PUBLIC SERVICES L1.080 | L1.080 PUBLIC SERVICES | D
QNL | VAV_2F_S14_002 | PUBLIC SERVICES L1.080 | L1.080 PUBLIC SERVICES | D
QNL | VAV_2F_S14_003 | PUBLIC SERVICES L1.080 | L1.080 PUBLIC SERVICES | D
QNL | VAV_2F_S14_004 | PUBLIC SERVICES L1.080 | L1.080 PUBLIC SERVICES | D
QNL | VAV_2F_S14_005 | BIBLIOGRAPHER 1 L1.081 | L1.081 BIBLIOGRAPHER 1 | D
QNL | VAV_2F_S14_006 | BIBLIOGRAPHER 2 L1.082 | L1.082 BIBLIOGRAPHER 2 | D
QNL | VAV_2F_S14_007 | SPEC COLL & ARCH L1.083 | L1.083 SPEC COLL AND ARCH | D
QNL | VAV_2F_S14_008 | R&L SERVICES L1.084 | L1.084 R AND L SERVICES | D
QNL | VAV_2F_S14_009 | AD. PUBLIC SERVICE L1.085 | L1.085 AD PUBLIC SERVICE | D
QNL | VAV_2F_S14_010 | REF LIBRARIAN L1.086 | L1.086 REF LIBRARIAN 1 | D->E
QNL | VAV_2F_S14_011 | REF LIBRARIAN L1.087 | L1.087 REF LIBRARIAN 2 | D->E
QNL | VAV_2F_S14_012 | REF LIBRARIAN L1.088 | L1.088 REF LIBRARIAN 3 | D->E
QNL | VAV_2F_S14_013 | REF LIBRARIAN L1.089 | L1.089 REF LIBRARIAN 4 | D->E
QNL | VAV_2F_S14_014 | REF LIBRARIAN L1.090 | L1.090 REF LIBRARIAN 5 | D->E
QNL | VAV_2F_S14_015 | REF LIBRARIAN L1.091 | L1.091 REF LIBRARIAN 6 | D->E
QNL | VAV_2F_S14_016 | REF LIBRARIAN L1.092 | L1.092 REF LIBRARIAN 7 | D->E
QNL | VAV_2F_S14_017 | REF LIBRARIAN L1.093 | L1.093 REF LIBRARIAN 8 | D->E
QNL | VAV_2F_S14_018 | REF LIBRARIAN L1.094 | L1.094 REF LIBRARIAN 9 | D->E
QNL | VAV_2F_S14_019 | REF LIBRARIAN L1.095 | L1.095 REF LIBRARIAN 10 | D->E
QNL | VAV_2F_S14_020 | REF LIBRARIAN L1.096 | L1.096 REF LIBRARIAN 11 | D->E
QNL | VAV_2F_S14_021 | REF LIBRARIAN L1.097 | L1.097 REF LIBRARIAN 12 | D->E
QNL | VAV_2F_S15_001 | VIP Room L2.051 | L2.051 VIP ROOM | D
QNL | VAV_2F_S15_002 | VIP Room L2.051 | L2.051 VIP ROOM | D
QNL | VAV_2F_S15_003 | VIP Room L2.051 | L2.051 VIP ROOM | D
QNL | VAV_2F_S15_004 | VIP Room L2.051 | L2.051 VIP ROOM | D
QNL | VAV_2F_S15_005 | MAJLIS-VIP Meeting L2.046 | L2.046 VIP MEETING | D->E
QNL | VAV_B_S10_001 | DIGITISATION AREA B.200 | B.200 DIGITIZATION | D->E
QNL | VAV_B_S10_002 | DIGITISATION AREA B.200 | B.200 DIGITIZATION | D->E
QNL | VAV_B_S10_003 | DIGITISATION AREA B.200 | B.200 DIGITIZATION | D->E
QNL | VAV_B_S10_004 | DIGITISATION AREA B.200 | B.200 DIGITIZATION | D->E
QNL | VAV_B_S10_005 | DIGITISATION AREA B.200 | B.200 DIGITIZATION | D->E
QNL | VAV_B_S10_006 | DIGITISATION AREA B.200 | B.200 DIGITIZATION | D->E
QNL | VAV_B_S10_007 | DIGITISATION AREA B.200 | B.200 DIGITIZATION | D->E
QNL | VAV_B_S10_008 | DIGITISATION AREA B.200 | B.200 DIGITIZATION | D->E
QNL | VAV_B_S10_009 | TECHNICAL SERVICES B.203 | B.203 TECHNICAL SERVICES | D
QNL | VAV_B_S10_010 | TECHNICAL SERVICES B.204 | B.204 TECHNICAL SERVICES | D
QNL | VAV_B_S10_011 | TECHNICAL SERVICES B.204 | B.204 TECHNICAL SERVICES | D
QNL | VAV_B_S10_012 | CR6 CONVERSATION WORK AREA B.209 | B.209 CONSERVATION WORK AREA | D->E
QNL | VAV_B_S10_013 | CR6 CONVERSATION WORK AREA B.209 | B.209 CONSERVATION WORK AREA | D->E
QNL | VAV_B_S10_014 | CR6 CONVERSATION WORK AREA B.209 | B.209 CONSERVATION WORK AREA | D->E
QNL | VAV_B_S10_015 | INSTRUCTION OUTREACH B.206 | B.206 INSTRUCTION OUTREACH | D
QNL | VAV_B_S10_016 | MULTIMEDIA PRESENTATION B.205 | B.205 INSTRUCTION PRESENTATION | D->E
QNL | VAV_B_S10_017 | MULTIMEDIA PRESENTATION B.205 | B.205 INSTRUCTION PRESENTATION | D->E
QNL | VAV_B_S10_018 | MULTIMEDIA PRESENTATION B.205 | B.205 INSTRUCTION PRESENTATION | D->E
QNL | VAV_B_S10_019 | CR6 PROF LIBRARIAN B.208 | B.208 PROF LIBRARIAN | D->E
QNL | VAV_B_S10_020 | Reserchers Reading Area B.207 | B.207 RESERCHERS READING AREA | D
QNL | VAV_B_S10_021 | Reserchers Reading Area B.207 | B.207 RESERCHERS READING AREA | D
QNL | VAV_B_S10_022 | Reserchers Reading Area B.207 | B.207 RESERCHERS READING AREA | D
QNL | VAV_B_S10_023 | Reserchers Reading Area B.207 | B.207 RESERCHERS READING AREA | D
QNL | VAV_B_S10_024 | DIGITISATION AREA B.200 | B.200 DIGITIZATION | D->E
QNL | VAV_B_S11_001 | Break Out Area B.001A | B.001A BREAK OUT AREA | D
QNL | VAV_B_S11_002 | Break Out Area B.001A | B.001A BREAK OUT AREA | D
QNL | VAV_B_S11_003 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_004 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_005 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_006 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_007 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_008 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_009 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_010 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_011 | Break Out Area B.001A | B.001A BREAK OUT AREA | D
QNL | VAV_B_S11_012 | Break Out Area B.001A | B.001A BREAK OUT AREA | D
QNL | VAV_B_S11_013 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_014 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_015 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_016 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_017 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_018 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_019 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_020 | Tech, Services & Collections Office B.001 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | D
QNL | VAV_B_S11_021 | Reception & Lounge B.009 | B.001 TECH SERVICES AND COLLECTIONS OFFICE | J
QNL | VAV_B_S11_022 | Corridor Leading To Reception & Lounge B.009 | B.009 RECEPTION AND LOUNGE | D->E
QNL | VAV_B_S11_023 | Corridor Leading To Reception & Lounge B.009 | B.009 RECEPTION AND LOUNGE | D->E
QNL | VAV_B_S11_024 | Kitchen B.002 | B.002 KITCHEN | D
QNL | VAV_B_S11_025 | Storage B.028 | B.028 STORAGE | D
QNL | VAV_B_S11_026 | AD TECH SERVICES DIRECTOR B.003 | B.003 FINANCE COORDINATOR AND BUSINESS SUPPORT OFCR | D
QNL | VAV_B_S11_027 | AD TECH SERVICES DIRECTOR B.003 | B.003 FINANCE COORDINATOR AND BUSINESS SUPPORT OFCR | D->E
QNL | VAV_B_S11_028 | Analogue Resources B.004 | B.004 ANALOGUE RESOURCES | D
QNL | VAV_B_S11_029 | Digital Resources B.005 | B.005 DIGITAL RESOURCES | D
QNL | VAV_B_S11_030 | Budget & Payment 1 B.006 | B.006 BUDGET AND PAYMENT 1 | D
QNL | VAV_B_S11_031 | Budget & Payment 2 B.007 | B.007 BUDGET AND PAYMENT 2 | D
QNL | VAV_B_S11_032 | Ad Collection B.024 | B.024 AD COLLECTION | D
QNL | VAV_B_S11_033 | Ad Collection B.024 | B.024 AD COLLECTION | D
QNL | VAV_B_S11_034 | Engineering B.020 | B.020 ENGINEERING | D
QNL | VAV_B_S11_035 | Arabic Sudies B.021 | B.021 ARABIC SUDIES | D
QNL | VAV_B_S11_036 | Licensing Expert B.022 | B.022 LICENSING EXPERT | D
QNL | VAV_B_S11_037 | Art & Humanities B.023 | B.023 ART AND HUMANITIES | D
QNL | VAV_B_S11_038 | HARD & HEALTH SCIENCES B.027 | B.027 PROCUREMENT SPC PROCUREMENT OFCR | D->E
QNL | VAV_B_S11_039 | Business Computing B.026 | B.026 BUSINESS AND COMPUTING | D->E
QNL | VAV_B_S11_040 | Social Sciences B.025 | B.025 SOCIAL SCIENCES | D
QNL | VAV_B_S11_041 | Literature Language B.029 | B.029 LITERATURE AND ANGUAGE | D->E
QNL | VAV_B_S11_042 | GENERAL B.030 | B.030 SNR P COORDINATOR AND P COORDINATOR | D->E
QNL | VAV_B_S11_043 | Receiving Area B.008 | B.008 RECEIVING AREA | D
QNL | VAV_B_S11_044 | Receiving Area B.008 | B.008 RECEIVING AREA | D
QNL | VAV_B_S11_045 | Receiving Area B.008 | B.008 RECEIVING AREA | D
QNL | VAV_B_S11_046 | Receiving Area B.008 | B.008 RECEIVING AREA | D
QNL | VAV_B_S13_001 | Meeting Room B.034 | B.034 MEETING ROOM | D
QNL | VAV_B_S13_002 | Meeting Room B.034 | B.034 MEETING ROOM | D
QNL | VAV_B_S13_003 | Processing Room B.103 | B.103 PROCESSING ROOM | D
QNL | VAV_B_S13_004 | Processing Room B.103 | B.103 PROCESSING ROOM | D
QNL | VAV_B_S13_006 | Fumigation Room B.085 | B.085 FUMIGATION ROOM | D
QNL | VAV_B_S13_007 | Shipping CLIRK B.101 | B.101 SHIPPING CLIRK | D
QNL | VAV_B_S13_008 | SECURITY CONTROL ROOM B.105 | B.105 SECURITY CONTOL ROOM | J
QNL | VAV_B_S14_001 | Office B.040 | B.040 OFFICE | D
QNL | VAV_B_S14_002 | Office Dig Init B.056 | B.056 OFFICE DIG INIT | D
QNL | VAV_B_S14_003 | Office AD For LIT B.057 | B.057 OFFICE AD FOR LIT | D
QNL | VAV_B_S14_004 | Digitization Room B.041 | B.041 DIGITIZATION ROOM | D
QNL | VAV_B_S14_005 | Digitization Room B.041 | B.041 DIGITIZATION ROOM | D
QNL | VAV_B_S14_006 | Digitization Room B.041 | B.041 DIGITIZATION ROOM | D
QNL | VAV_B_S14_007 | Shell Space B.58 | B.058 SHELL SPACE | D
QNL | VAV_B_S14_008 | Shell Space B.59 | B.041 DIGITIZATION ROOM | D
QNL | VAV_B_S14_009 | Digitization Room B.041 | B.057 OFFICE AD FOR LIT | D
QNL | VAV_B_S14_010 | Digitization Room B.041 | B.041 DIGITIZATION ROOM | D
QNL | VAV_B_S14_011 | Digitization Room B.041 | B.041 DIGITIZATION ROOM | D
QNL | VAV_B_S14_012 | Digitization Room B.041 | B.041 DIGITIZATION ROOM | D
QNL | VAV_B_S14_013 | Shell Space B.58 | B.058 SHELL SPACE | D
QNL | VAV_B_S14_014 | Shell Space B.59 | B.059 SHELL SPACE | D
QNL | VAV_B_S14_015 | Digitization Room B.041 | B.041 DIGITIZATION ROOM | D
QNL | VAV_B_S14_016 | Digitization Room B.041 | B.041 DIGITIZATION ROOM | D
QNL | VAV_B_S14_040 | BOH Kitchen B.044 | B.044 BOH KITCHEN | D
QNL | VAV_B_S14_041 | Fine Binding B.044 | B.044 BOH KITCHEN | D->E
QNL | VAV_B_S14_042 | Binding & Preservation B.043 | B.043 BINDING AND PRESERVATION SPACE | D->E
QNL | VAV_B_S14_043 | Binding & Preservation B.043 | B.043 BINDING AND PRESERVATION SPACE | D->E
QNL | VAV_B_S14_044 | Binding & Preservation B.043 | B.043 BINDING AND PRESERVATION SPACE | D->E
QNL | VAV_B_S14_045 | Binding & Preservation B.043 | B.043 BINDING AND PRESERVATION SPACE | D->E
QNL | VAV_B_S14_046 | Binding & Preservation B.043 | B.043 BINDING AND PRESERVATION SPACE | D->E
QNL | VAV_B_S14_047 | Fine Binding B.044 | B.044 BOH KITCHEN | D->E
QNL | VAV_B_S14_048 | Binding & Preservation B.043 | B.043 BINDING AND PRESERVATION SPACE | D->E
QNL | VAV_B_S14_049 | Binding & Preservation B.043 | B.043 BINDING AND PRESERVATION SPACE | D->E
QNL | VAV_B_S14_050 | Binding & Preservation B.043 | B.043 BINDING AND PRESERVATION SPACE | D->E
QNL | VAV_B_S14_051 | Binding & Preservation B.043 | B.043 BINDING AND PRESERVATION SPACE | D->E
QNL | VAV_B_S15_001 | Prof. Librarian B.153 | B.153 PROF LIBRARIAN | D
QNL | VAV_B_S15_002 | Lobby and Security B.145 | B.145 LOBY AND CSECURITY | D
QNL | VAV_B_S15_003 | Lobby and Security B.145 | B.145 LOBY AND CSECURITY | D
QNL | VAV_B_S15_004 | Lobby and Security B.145 | B.145 LOBY AND CSECURITY | D
QNL | VAV_B_S15_005 | Prof. Librarian B.153 | B.153 PROF LIBRARIAN | D
QNL | VAV_B_S15_006 | Prof. Librarian B.153 | B.153 PROF LIBRARIAN | D
QNL | VAV_B_S15_007 | HC SECURITY ROOM B.152 | B.152 HC SECURITY ROOM | D
QNL | VAV_B_S15_008 | RESEARCH & DOC RECORD MGMT B.151 | B.151 RESEARCH AND DOC RECORD MGMT | D
QNL | VAV_B_S15_009 | HC DIRECTOR HEAD B.149 | B.149 HC DIRECTOR HEAD | D
QNL | VAV_B_S15_010 | HC DIRECTOR HEAD B.149 | B.149 HC DIRECTOR HEAD | D
QNL | VAV_B_S15_011 | VIP Majlis B.149 | B.149 HC DIRECTOR HEAD | D->E
QNL | VAV_B_S15_012 | VIP Majlis B.149 | B.149 HC DIRECTOR HEAD | D->E
QNL | VAV_B_S15_013 | RESEARCH & DOC RECORD MGMT B.151 | B.151 RESEARCH AND DOC RECORD MGMT | D
QNL | CAV_1F_S11_001 | CORRIDOR L1.023 | L1.023 CORRIDOR | D
QNL | CAV_1F_S11_002 | CORRIDOR L1.023 | L1.023 CORRIDOR | D
QNL | CAV_1F_S11_006 | CHILDRENS LIBRRY CIRCULATION NW GLAZED L1.047 | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | D->E
QNL | CAV_1F_S11_007 | CORRIDOR L1.023 | L1.023 CORRIDOR | D
QNL | CAV_1F_S11_008 | CHILDRENS LIBRRY CIRCULATION NW GLAZED L1.047 | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | D->E
QNL | CAV_1F_S11_009 | CHILDRENS LIBRRY CIRCULATION NW GLAZED L1.047 | L1.047 CHILDREN LIBRARY PRE SCHOOL READING AND PLAYING | D->E
QNL | CAV_1F_S15_002 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | CAV_1F_S15_004 | AERIAL PLATFORM PARKING L1.100 | L1.100 AERIAL PLATFORM PARKING | D
QNL | CAV_1F_S15_005 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | CAV_1F_S15_006 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | CAV_1F_S15_010 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | CAV_1F_S15_011 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | CAV_1F_S15_012 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | CAV_1F_S15_013 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | CAV_1F_S15_014 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | CAV_1F_S15_015 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | CAV_1F_S15_016 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | CAV_1F_S15_017 | Restaurant L1.150 | L1.150 RESTAURANT | D
QNL | CAV_1F_S15_018 | AREAL PLATFORM PARK L1.100 | L1.100 AERIAL PLATFORM PARKING | D->E
QNL | CAV_1F_S15_019 | FURNITURE STORE L1.153 | L1.153 FURNITURE STORE | D
QNL | CAV_B_S12_001 | CORRIDOR B.061 | B.063 PLANT ROOM 01 | D
QNL | CAV_B_S12_002 | Plant Room 1 B.063 | B.063 PLANT ROOM 01 | D
QNL | CAV_B_S12_003 | Plant Room 1 B.063 | B.063 PLANT ROOM 01 | D
QNL | CAV_B_S13_001 | Corridor 2 B.064 | B.064 CORRIDOR 2 | D
QNL | CAV_B_S13_002 | Corridor 2 B.064 | B.064 CORRIDOR 2 | D
QNL | CAV_B_S13_003 | Corridor 2 B.064 | B.064 CORRIDOR 2 | D
QNL | CAV_B_S13_004 | Corridor 2 B.064 | B.064 CORRIDOR 2 | D
QNL | CAV_B_S13_005 | Corridor 2 B.064 | B.064 CORRIDOR 2 | D
QNL | CAV_B_S13_006 | CORRIDOR 4 B.035 | B.035 CORRIDOR 4 | D
QNL | CAV_B_S13_007 | CORRIDOR 4 B.035 | B.035 CORRIDOR 4 | D
QNL | CAV_B_S13_008 | CORRIDOR 4 B.035 | B.035 CORRIDOR 4 | D
QNL | CAV_B_S13_009 | IT STORAGE B.104 | B.104 STORAGE | D->E
QNL | CAV_B_S13_010 | Plant Room 2 B.070 | B.070 PLANT ROOM 02 | D
QNL | CAV_B_S13_011 | Plant Room 2 B.070 | B.070 PLANT ROOM 02 | D
QNL | CAV_B_S13_012 | Fire Command B.071 | B.070 PLANT ROOM 02 | D
QNL | CAV_B_S13_013 | GAS SUPPRESSION B.087 | B.087 GAS SUPPRESSION ROOM | D->E
QNL | CAV_B_S13_014 | PEOPLE MOVER B.088 | B.064 CORRIDOR 2 | D
QNL | CAV_B_S13_015 | Server Room B.089 | B.089 SERVER ROOM | D
QNL | CAV_B_S13_020 | UPS BATTERY ROOM B.084 | B.084 UPS BATTERY ROOM | D
QNL | CAV_B_S13_021 | Sprinklers Pumps & Zones Valves B.072 | B.072 SPRIMKLERS PUMPS AND ZONES VALVES | D
QNL | CAV_B_S13_050 | PLANT ROOM B.104A | B.104A PLANT ROOM | D
QNL | CAV_B_S14_001 | CORRIDOR 3 B.051 | B.040 OFFICE | D
QNL | CAV_B_S14_002 | CORRIDOR 3 B.052 | B.052 CORRIDOR 3 | D
QNL | CAV_B_S14_003 | PLANT ROOM 3 B.110 | B.110 PLANT ROOM 03 | D
QNL | CAV_B_S14_004 | PLANT ROOM 3 B.110 | B.110 PLANT ROOM 03 | D
QNL | CAV_B_S14_005 | PLANT ROOM 3 B.110 | B.110 PLANT ROOM 03 | D
QNL | CAV_B_S14_006 | Referigerate Store Kitchen Lobby B.044 | B.044 BOH KITCHEN | D->E
QNL | CAV_B_S14_007 | Washing Area & Fine Binding B.044 | B.044 BOH KITCHEN | D->E
QNL | CAV_B_S15_001 | Corridor 5 B.063 | B.063 PLANT ROOM 01 | D->E
QNL | CAV_B_S15_002 | Corridor 5 B.063 | B.063 PLANT ROOM 01 | D->E
QNL | CAV_B_S15_003 | Corridor 5 B.063 | B.063 PLANT ROOM 01 | D->E
QNL | DX_B01 | MV ROOM B.081 | B.035 CORRIDOR 4 | J
QNL | DX_B02 | MV ROOM B.081 | B.035 CORRIDOR 4 | J
QNL | DX_B03 | TRANSFORMER ROOM B.082 | B.095 EMERGENCY LIGHTING BATTERY ROOM | J
QNL | DX_B04 | TRANSFORMER ROOM B.082 | B.082 TRANSFORMER ROOM | D
QNL | DX_B05 | HV ROOM B.083 | B.083 HV ROOM | D
QNL | DX_B06 | HV ROOM B.083 | B.083 HV ROOM | J
QNL | DX_B07 | EMERGENCY LIGHTING BATTERY ROOM B.095 | B.095 EMERGENCY LIGHTING BATTERY ROOM | D
QNL | DX_B08 | UPS BATTERY ROOM B.084 | B.095 EMERGENCY LIGHTING BATTERY ROOM | J
QNL | DX_B09 | UPS BATTERY ROOM B.084 | B.084 UPS BATTERY ROOM | D
QNL | DX_B10 | SECURITY & BMS B.102 | B.103 PROCESSING ROOM | J
QNL | DX_B11 | ITTIGATION CONTROL ROOM B.046_ITT | B.107 SECURITY EQUIPMENT ROOM | J
QNL | DX_B12 | SECURITY EQUIPMENT ROOM B.107 | B.107 SECURITY EQUIPMENT ROOM | D
QNL | DX_B13 | TRASH CHAMBER B.093 | B.093 TRANSH CHAMBER | D
QNL | DX_B14 | TRANSFORMER ROOM B.082 | B.095 EMERGENCY LIGHTING BATTERY ROOM | J
QNL | DX_B15 | TRASH CHAMBER B.093 | B.093 TRANSH CHAMBER | D
QNL | DX_B16 | EMERGENCY LIGHTING BATTERY ROOM B.095 | B.095 EMERGENCY LIGHTING BATTERY ROOM | D
QNL | DX_B17 | REFRIGERATE STORE B.045A | B.045A REFRIGERATE STORE | D
QNL | DX_B18 | REFRIGERATE STORE B.045A | B.045A REFRIGERATE STORE | D
QNL | DX_B19 | REFRIGERATE STORE B.045A | B.045A REFRIGERATE STORE | D
QNL | DX_B20 | STORAGE B.092 | B.092 STORAGE | D
QNL | DX_B21 | IDF Roof RP.001 | P.004 PLANT ZONE | D->E
QNL | DX_B22 | REST ROOM SECURITY B.106_RES | B.106 REST ROOM SECURITY | D->E
QNL | DX_B23 | SECURITY EQUIPMENT ROOM B.107 | B.107 SECURITY EQUIPMENT ROOM | D
QNL | DX_B24 | IDF Roof RP.001 | P.004 PLANT ZONE | D->E
QNL | HEX01 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | HEX02 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | HEX03 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | HEX04 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | HEX05 | PH PLANT B.211 | B.211 PH PLANT ROOM | D->E
QNL | EF_201 | L-3 L1.L-3 | L-3 L 3 | D
QNL | EF_B05 | FUMIGATION B.085 | B.085 FUMIGATION ROOM | D->E
QNL | EF_B06 | DIGITIZATION CENTER B.055 | B.055 DIGITIZATION CENTER | D
QNL | EF_B07 | Loading Room B.109 | B.109 LOADING AREA | D->E
QNL | EF_B08 | Loading Room B.109 | B.109 LOADING AREA | D->E
QNL | EF_B09 | Generator B.080 | B.080 GENERATOR | D
QNL | EF_B10 | Trash room B.093 | B.093 TRANSH CHAMBER | D->E
QNL | EF_B11 | Fuel pump room B.091 | B.091 FUEL ROOM | D->E
QNL | EF_B12 | IDF ROOM B.214 | B.214 IDF ROOM | D
QNL | EF_B13 | Sprinklers Pumps B.072 | B.072 SPRIMKLERS PUMPS AND ZONES VALVES | J
QNL | EF_B14 | Fire Command B.071 | B.064 CORRIDOR 2 | J
QNL | EF_B15 | Loading Room B.109 | B.109 LOADING AREA | D->E
QNL | EF_B16 | Loading Room B.109 | B.109 LOADING AREA | D->E
QNL | EF_BBV01 | Plant Room 2 B.070 | B.070 PLANT ROOM 02 | D
QNL | EF_BBV02 | Plant Room 2 B.070 | B.070 PLANT ROOM 02 | D
QNL | EF_RP01 | Plant Zone P.002 | P.002 PLANT ZONE | D
QNL | EF_RP02 | Plant Zone P.004 | P.004 PLANT ZONE | D
QNL | EF_RP03 | Plant Zone P.007 | P.007 PLANT ZONE | D
QNL | KEF_101 | RESTAURANT L1.067 | L1.067 RESTAURANT | D
QNL | KEF_B019 | MEP KITCHEN B.049 | B.049 MEP KITCHEN | D
QNL | KEF_B020 | CORRIDOR 3 B.052 | B.052 CORRIDOR 3 | D
QNL | KEF_B04 | BREAKOUT AREA B.001A | B.001A BREAK OUT AREA | D
QNL | SEF_RP04 | Plant Zone P.002 | P.002 PLANT ZONE | D
QNL | SEF_RP05 | Plant Zone P.002 | P.002 PLANT ZONE | D
QNL | SEF_RP06 | Plant Zone P.002 | P.002 PLANT ZONE | D
QNL | SEF_RP07 | Plant Zone P.004 | P.004 PLANT ZONE | D
QNL | SEF_RP08 | Plant Zone P.004 | P.004 PLANT ZONE | D
QNL | SEF_RP09 | Plant Zone P.004 | P.004 PLANT ZONE | D
QNL | SEF_RP10 | Plant Zone P.007 | P.007 PLANT ZONE | D
QNL | SEF_RP11 | Plant Zone P.006 | P.006 PLANT ZONE | D
QNL | SEF_RP12 | Plant Zone P.006 | P.006 PLANT ZONE | D
QNL | SEF_ZoneA | Plant Zone P.002 | P.002 PLANT ZONE | D
QNL | SEF_ZoneB | Plant Zone P.004 | P.004 PLANT ZONE | D
QNL | SEF_ZoneC | Plant Zone P.007 | P.007 PLANT ZONE | D
QNL | TEF_101C | ELEC SHAFT L1.E2 | E2 SHAFT | D->E
QNL | TEF_102C | ELEC SHAFT L1.E1 | E1 SHAFT | D->E
QNL | TEF_B01A | PLANT ROOM 3 B.110 | B.110 PLANT ROOM 03 | D
QNL | TEF_B01B | PLANT ROOM 3 B.110 | B.110 PLANT ROOM 03 | D
QNL | TEF_B02A | PLANT ROOM 2 B.070 | B.070 PLANT ROOM 02 | D
QNL | TEF_B02B | PLANT ROOM 2 B.070 | B.070 PLANT ROOM 02 | D
QNL | TEF_B03A | COMPACT SHELVING-MAIN COLLECTION B.120 | B.120 COMPACT SHELVING MAIN COLLECTION | D
QNL | TEF_B03B | COMPACT SHELVING-MAIN COLLECTION B.120 | B.120 COMPACT SHELVING MAIN COLLECTION | D
QNL | CCU_B01 | QTEL ROOM B.048 | B.048 QTEL ROOM | D
QNL | CCU_B02 | QTEL ROOM B.048 | B.048 QTEL ROOM | D
QNL | CCU_B03 | TELECOM ROOM B.050 | B.050 TELECOM ROOM | D
QNL | CCU_B04 | TELECOM ROOM B.050 | B.050 TELECOM ROOM | D
QNL | CCU_B05 | SERVER ROOM B.089 | B.089 SERVER ROOM | D
QNL | CCU_B06 | SERVER ROOM B.089 | B.089 SERVER ROOM | D
QNL | CCU_B07 | SERVER ROOM B.089 | B.089 SERVER ROOM | D
QNL | CCU_B08 | VAULT_B.141_VAU | B.141 VAULT | D->E
QNL | CCU_B09 | VAULT_B.141_VAU | B.141 VAULT | D->E
QNL | CCU_B10 | IDF B.222 | B.222 IDF | D
QNL | CCU_B11 | IDF B.222 | B.222 IDF | D
QNL | CHW_P01 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | CHW_P02 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | CHW_P03 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | CHW_P04 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | CHWPU_P01 | Plant Room 4 B.220 | B.220 PLANT ROOM 04 | D
QNL | ELEC_Gen | Generator B.080 | B.080 GENERATOR | D
SSC | AHUB_0001 | CHILLED WATER B.013 | B.013 CHILLED WATER | J
SSC | AHUB_0002 | VENT PLANT B.014 | B.014 VENT PLANT | J
SSC | AHUB_0003 | VENT PLANT B.014 | B.014 VENT PLANT | J
SSC | AHUB_0004 | VENT PLANT B.008 | B.008 VENT PLANT | J
SSC | AHUB_0005 | CHILLED WATER B.013 | B.014 VENT PLANT | J
SSC | FCU0001 | SPRINKLER AND WATER B.016 | B.016 SPRINKLER AND WATER | D
SSC | FCU0002 | MAIN SEC. CONTROL ROOM B.025 | B.025 MAIN SEC CONTROL ROOM | J
SSC | FCU0003 | B.M.S B.039 | B.030 CORRIDOR | J
SSC | FCU0004 | AV ROOM 1.008 | 1.008 AV ROOM | D
SSC | FCU0005 | IDF-1 1.027 | 1.027 IDF 1 | J
SSC | FCU0006 | IDF-1 1.027 | 1.027 IDF 1 | J
SSC | FCU0007 | IDF-2 1.039 | 1.039 IDF 2 | J
SSC | FCU0008 | IDF-2 1.039 | 1.039 IDF 2 | D
SSC | FCU0009 | CORRIDOR 1.028 | 1.029 SHELL SPACE | J
SSC | FCU0010 | CORRIDOR 1.010 | 1.013 CORRIDOR | J
SSC | FCU0011 | PRINTING 03.033 | 3.033 PRINTING | D
SSC | VAV0001 | ENTRANCE B.015 | B.015 ENTRANCE | J
SSC | VAV0002 | SHARED OFFICE 01.014 | 1.014 SHELL SPACE | D->E
SSC | VAV0003 | SHARED OFFICE 01.014 | 1.014 SHELL SPACE | J
SSC | VAV0004 | SHARED OFFICE 01.014 | 1.014 SHELL SPACE | J
SSC | VAV0005 | SHARED OFFICE 01.015 | 1.015 SHELL SPACE | D->E
SSC | VAV0006 | SHARED OFFICE 01.015 | 1.015 SHELL SPACE | J
SSC | VAV0007 | SHARED OFFICE 01.015 | 1.015 SHELL SPACE | J
SSC | VAV0008 | CORRIDOR 01.024 | 1.024 CORRIDOR | D
SSC | VAV0009 | PRAYER ROOM 01.019 | 1.001 CORRIDOR | J
SSC | VAV0010 | PRAYER ROOM 01.019 | 1.019 PRAYER ROOM | J
SSC | VAV0011 | PRAYER ROOM 01.019 | 1.019 PRAYER ROOM | J
SSC | VAV0012 | PRAYER ROOM 01.019 | 1.019 PRAYER ROOM | J
SSC | VAV0013 | PRAYER ROOM 01.019 | 1.019 PRAYER ROOM | J
SSC | VAV0014 | PRAYER ROOM 01.019 | 1.019 PRAYER ROOM | J
SSC | VAV0015 | ROOM NO 42 | 1.029 ROOM NO 42 | D
SSC | VAV0016 | ROOM NO 43 | 1.029 ROOM NO 43 | D
SSC | VAV0017 | ROOM NO 44 | 1.029 ROOM NO 44 | D
SSC | VAV0018 | SHARED OFFICE 01.029 | 1.029 SHELL SPACE | J
SSC | VAV0019 | SHARED OFFICE 01.029 | 1.029 SHELL SPACE | J
SSC | VAV0020 | SHARED OFFICE 01.029 | 1.029 SHELL SPACE | J
SSC | VAV0021 | CORRIDOR 01.013 | 1.013 CORRIDOR | D
SSC | VAV0022 | OPEN SPACE 01.003 | 1.003 OPEN SPACE | D
SSC | VAV0023 | OPEN SPACE 01.003 | 1.003 OPEN SPACE | J
SSC | VAV0024 | CORRIDOR 01.001 | 1.003 OPEN SPACE | J
SSC | VAV0025 | TEAM SPACE 01.002 | 1.002 SHELL SPACE | J
SSC | VAV0026 | TEAM SPACE 01.002 | 1.002 SHELL SPACE | D->E
SSC | VAV0027 | TEAM SPACE 01.002 | 1.002 SHELL SPACE | J
SSC | VAV0028 | TEAM SPACE 01.002 | 1.002 SHELL SPACE | J
SSC | VAV0029 | CORRIDOR 01.001 | 1.003 OPEN SPACE | J
SSC | VAV0030 | PRINT COPY 01.016 | 1.016 SHELL SPACE | D->E
SSC | VAV0031 | CORRIDOR 01.001 | 1.003 OPEN SPACE | J
SSC | VAV0032 | CORRIDOR 01.018 | 1.018 CORRIDOR | D
SSC | VAV0033 | CORRIDOR 01.028 | 1.039 IDF 2 | J
SSC | VAV0034 | OPEN SPACE 01.003 | 1.003 OPEN SPACE | J
SSC | VAV0035 | CORRIDOR 01.010 | 1.028 CORRIDOR | J
SSC | VAV0036 | ABLUTION ROOM 01.022 | 1.019 PRAYER ROOM | J
SSC | VAV0037 | AV ROOM 1.008 | 1.008 AV ROOM | D
SSC | VAV0039 | OPEN SPACE 01.003 | 1.003 OPEN SPACE | J
SSC | VAV0040 | CONFERENCE ROOM 02.006 | 2.006 CONFERENCE ROOM | J
SSC | VAV0041 | EXECUTIVE CONFERENCE ROOM 02.005 | 2.005 EXECUTIVE CONFERENCE ROOM | J
SSC | VAV0042 | EXECUTIVE CONFERENCE ROOM 02.005 | 2.005 EXECUTIVE CONFERENCE ROOM | J
SSC | VAV0043 | CORRIDOR 02.004 | 2.004 CORRIDOR | D
SSC | VAV0044 | FOYER 02.001 | 2.001 FOYER | D
SSC | VAV0045 | FOYER 02.001 | 2.001 FOYER | D
SSC | VAV0046 | LOBBY 02.002 | 2.002 LOBBY | J
SSC | VAV0047 | LOBBY 02.002 | 2.002 LOBBY | J
SSC | VAV0048 | LOBBY 02.002 | 2.002 LOBBY | J
SSC | VAV0049 | LOBBY 02.002 | 2.003 CORRIDOR | J
SSC | VAV0050 | CORRIDOR 02.003 | 2.002 LOBBY | J
SSC | VAV0051 | EXECUTIVE CONFERENCE ROOM 02.005 | 2.005 EXECUTIVE CONFERENCE ROOM | J
SSC | VAV0052 | CONFERENCE ROOM 02.006 | 2.006 CONFERENCE ROOM | J
SSC | VAV0053 | RESEARCHER OFFICE 03.015 | 3.015 RESEARCHER OFFICE | J
SSC | VAV0054 | VISITOR'S CUBICLE 03.014 | 3.014 VISITOR S CUBICLE | D
SSC | VAV0055 | RESEARCHER OFFICE 03.013 | 3.013 RESEARCHER OFFICE | J
SSC | VAV0056 | RESEARCHER OFFICE 03.012 | 3.012 RESEARCHER OFFICE | J
SSC | VAV0057 | VISITOR'S CUBICLE 03.011 | 3.011 VISITOR S CUBICLE | D
SSC | VAV0058 | RESEARCHER OFFICE 03.010 | 3.010 RESEARCHER OFFICE | J
SSC | VAV0059 | RESEARCHER OFFICE 03.009 | 3.009 RESEARCHER OFFICE | J
SSC | VAV0060 | VISITOR'S CUBICLE 03.008 | 3.008 VISITOR S CUBICLE | D
SSC | VAV0061 | OPERATION MANAGERS 03.007 | 3.007 OPERATIONS MANAGERS | J
SSC | VAV0062 | ROOM 03.006B | 3.006A ROOM | J
SSC | VAV0064 | ROOM 03.006A | 3.006B ROOM | J
SSC | VAV0065 | RESEARCHER OFFICE 03.005 | 3.005 RESEARCHER OFFICE | D
SSC | VAV0066 | VISITOR'S CUBICLE 03.004 | 3.004 VISITOR S CUBICLE | D
SSC | VAV0067 | RESEARCHER OFFICE 03.003 | 3.003 RESEARCHER OFFICE | D
SSC | VAV0068 | DIRECTOR MEETING ROOM 03.002 | 3.002 DIRECTOR MEETING ROOM | D
SSC | VAV0069 | DIRECTOR MEETING ROOM 03.002 | 3.002 DIRECTOR MEETING ROOM | D
SSC | VAV0070 | DIRECTOR'S OFFICE 03.001 | 3.001 DIRECTOR S OFFICE | D
SSC | VAV0071 | GENERAL OFFICE AREA 03.002 | 3.032 GENERAL OFFICE AREA | J
SSC | VAV0072 | GENERAL OFFICE AREA 03.002 | 3.032 GENERAL OFFICE AREA | J
SSC | VAV0073 | GENERAL OFFICE AREA 03.002 | 3.032 GENERAL OFFICE AREA | J
SSC | VAV0074 | GENERAL OFFICE AREA 03.002 | 3.032 GENERAL OFFICE AREA | J
SSC | VAV0075 | GENERAL OFFICE AREA 03.002 | 3.032 GENERAL OFFICE AREA | J
SSC | VAV0076 | GENERAL OFFICE AREA 03.002 | 3.031 ASSOC DIRECTORS OFFICE | J
SSC | VAV0077 | GENERAL OFFICE AREA 03.002 | 3.032 GENERAL OFFICE AREA | J
SSC | VAV0078 | ASSOC. DOR. OFFICE 03.031 | 3.031 ASSOC DIRECTORS OFFICE | J->E
SSC | VAV0079 | ASSOC. DIR. MEETING ROOM 03.030 | 3.030 ASSOC DIRECTORS MEETING ROOM | D->E
SSC | VAV0080 | ASSOC. DIR. MEETING ROOM 03.030 | 3.030 ASSOC DIRECTORS MEETING ROOM | J->E
SSC | VAV0081 | RESEARCHER OFFICE 03.029 | 3.029 RESEARCHER OFFICE | J
SSC | VAV0082 | VISITOR'S CUBICLE 03.028 | 3.028 VISITOR S CUBICLE | D
SSC | VAV0083 | RESEARCHER OFFICE 03.027 | 3.027 RESEARCHER OFFICE | J
SSC | VAV0084 | MEETING ROOM 03.026 | 3.026 MEETING ROOM | J
SSC | VAV0085 | MEETING ROOM 03.026 | 3.026 MEETING ROOM | J
SSC | VAV0086 | MEETING ROOM 03.026 | 3.026 MEETING ROOM | J
SSC | VAV0087 | SECRETARIAL AREA 03.025 | 3.025 SECRETARIAL AREA | J
SSC | VAV0088 | VISITOR'S CUBICLE 03.024 | 3.024 VISITOR S CUBICLE | D
SSC | VAV0089 | RESEARCHER OFFICE 03.023 | 3.023 RESEARCHER OFFICE | J
SSC | VAV0090 | RESEARCHER OFFICE 03.022 | 3.022 RESEARCHER OFFICE | J
SSC | VAV0091 | VISITOR'S CUBICLE 03.021 | 3.021 VISITOR S CUBICLE | D
SSC | VAV0092 | RESEARCHER OFFICE 03.020 | 3.020 RESEARCHER OFFICE | J
SSC | VAV0093 | IT MANAGERS'S OFFICE 03.019 | 3.019 IT MANAGERS OFFICE | J
SSC | VAV0094 | VISITOR'S CUBICLE 03.018 | 3.018 VISITOR S CUBICLE | D
SSC | VAV0095 | RESEARCHER OFFICE 03.017 | 3.017 RESEARCHER OFFICE | J
SSC | VAV0096 | LOUNGE 03.016 | 3.016 LOUNGE | J
SSC | VAV0097 | LOUNGE 03.016 | 3.016 LOUNGE | J
SSC | VAV0098 | IT OFFICE 03.049 | 3.016 LOUNGE | J
SSC | VAV0099 | CORRIDOR 03.042 | 3.034 CORRIDOR | J
SSC | VAV0100 | CORRIDOR 03.041 | 3.041 CORRIDOR | D
SSC | VAV0101 | CORRIDOR 03.044 | 3.042 CORRIDOR | J
SSC | VAV0102 | CORRIDOR 03.034 | 3.041 CORRIDOR | J
SSC | VAV0103 | CORRIDOR 03.034 | 3.034 CORRIDOR | J
SSC | VAV0104 | CORRIDOR 03.034 | 3.034 CORRIDOR | J
SSC | VAV0105 | CORRIDOR 03.034 | 3.034 CORRIDOR | J
SSC | VAV0106 | CORRIDOR 03.042 | 3.042 CORRIDOR | J
SSC | VAV0107 | GENERAL OFFICE AREA 03.002 | 3.032 GENERAL OFFICE AREA | J
SSC | VAV0108 | GENERAL OFFICE AREA 03.002 | 3.032 GENERAL OFFICE AREA | J
RDC | RDC_SB_GF_AHU8031 | COMPUTER RESEARCH LAB S-1112 | Mech S-0136 | BMS screen, kept green by the client
RDC | RDC_SB_GF_AHU8032 | COMPUTER RESEARCH LAB S-1112 | Mech S-0136 | BMS screen, kept green by the client
RDC | RDC_SB_GF_AHU8033 | COMPUTER RESEARCH LAB S-1112 | Mech S-0136 | BMS screen, kept green by the client
RDC | RDC_SB_GF_AHU8034 | COMPUTER RESEARCH LAB S-1112 | Mech S-0136 | BMS screen, kept green by the client
RDC | RDC_SB_GF_AHU8035 | COMPUTER RESEARCH LAB S-1112 | MECH S-0136 | BMS screen, kept green by the client
RDC | RDC_SB_GF_AHU8037 | COMPUTER RESEARCH LAB S-1112 | Cyber Server S-0138 | BMS screen, kept green by the client
RDC | RDC_SB_GF_AHU8042 | UPS ROOM S-0145 | Corridor S-0143 | BMS screen, kept green by the client
RDC | RDC_NB_GF_VAV5165_EV5166 | Corridor N-0134 | Serv Core N-0136 | BMS screen, kept green by the client
RDC | RDC_NB_GF_VAV7175 | Office 05-15-WS N-0431 | Corridor N-0432 | BMS screen, kept green by the client
RDC | RDC_NB_GF_VAV7460 | Office 05-8-WKS N-0457 | Workstation N-0457 | BMS screen, kept green by the client
RDC | RDC_SB_1F_VAV0514 | NCIR Office S-1119 | Sc.Comp.Office3 S-1119 | BMS screen, kept green by the client
RDC | RDC_SB_1F_VAV2536 | Normal Elec. S-1251 | Mech. Chasing S-1249 | BMS screen, kept green by the client
RDC | RDC_SB_1F_VAV2552 | Vestibule S-1273 | FPC S-1277 | BMS screen, kept green by the client
RDC | RDC_SB_GF_VAV1004 | Corridor S-0137 / S-0143 | Dedicated Cyber SOC/NOC Lab S-0141 | BMS screen, kept green by the client
RDC | RDC_NB_1F_VAV4565_EV4566 | Conference N-1213 | Storage Room N-1215 | BMS screen, kept green by the client
RDC | RDC_NB_1F_VAV4910P | Emergency Electr N-2103 | Emer. Elec. N-2104 | BMS screen, kept green by the client
RDC | RDC_NB_1F_VAV5610_VEV5611 | Robotics N-1115J | Cold Room N-1115F | BMS screen, kept green by the client
RDC | RDC_NB_1F_VAV6980P | Emer. Elec. N-2108 | IDF N-2110 | BMS screen, kept green by the client
RDC | RDC_NB_1F_VAV7660 | Office 05 - 2 WKS- N-1401 | Workstation N-1423 | BMS screen, kept green by the client
RDC | RDC_NB_GF_FCU6982 | Mech/FPC N-0128 | IDF N-0133 | BMS screen, kept green by the client
RDC | RDC_SB_2F_FCU0206 | Normal Elec. S-2103 | South Penthouse S-2101 | BMS screen, kept green by the client
RDC | RDC_SB_2F_FCU0208 | Emerg. Elec. S-2104 | South Penthouse S-2101 | BMS screen, kept green by the client
RDC | RDC_SB_2F_FCU2205 | Emerg. Elec. S-2105 | South Penthouse S-2101 | BMS screen, kept green by the client
RDC | RDC_UB_GF_FCU8514 | WET/MECH/FIRE ROOM U-0120 | Pump Room U-0121 | BMS screen, kept green by the client
RDC | RDC_NB_GF_CAV5280 | Store N-0146 | Serv Core N-0136 | BMS screen, kept green by the client
RDC | RDC_NB_GF_VEV-5211 | Sputter Room N-0140D | MBE EVAP Room N-0140E | BMS screen, kept green by the client
RDC | RDC_NB_1F_FEV-5624 | Sequence Lab N-1115K | Robotics N-1115J | BMS screen, kept green by the client
RDC | RDC_NB_1F_FEV-5574 | Met/Prot Lab N-1115C | PRe-PCR N-1115B | BMS screen, kept green by the client
RDC | RDC_NB_1F_FEV-5575 | Met/Prot Lab N-1115C | Cell Culture N-1115E | BMS screen, kept green by the client
RDC | RDC_NB_1F_VEV-5791 | Shafallah N-1144C | Culture & Gel Rm N-1144B | BMS screen, kept green by the client
RDC | RDC_NB_1F_VEV-5795B | Storage and Archives N-1144C2 | PRE-PCR N-1144D | BMS screen, kept green by the client
RDC | RDC_NB_1F_FEV-5796 | Shafallah N-1144C | PRE-PCR N-1144D | BMS screen, kept green by the client

## Removed from RDC
RDC ROWS THE HISTORIAN PASS REMOVED OR RENAMED
What happened to it | Tag No. | Equipment type | Room it carried | Why
removed - not in historian | RDC_NB_GF_EV-5035 | EV | Confr Room N-0112 | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0115 | AT | Office S-0233A | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0116 | AT | Office S-0232A | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0117 | AT | Open Plan S-0228 | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0118 | AT | Open Plan S-0228B | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0120 | AT | Open Plan S-0228A | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0122 | AT | Office S-0211A | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0123 | AT | Office S-0211B | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0124 | AT | Technical Open Plan S-0211 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_GF_VEV-6053 | VEV | Open Lab 1 N-0310C | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_GF_VEV-6061 | VEV | Lab Support 3 N-0310D | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_GF_VEV-6071 | VEV | Lab Support 4 N-0310E | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_GF_VEV-6081 | VEV | Lab Support 5 N-0310F | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_GF_VEV-6091 | VEV | Lab Support 6 N-0310G | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_GF_VAV-6080 | VAV | Lab Support 5 N-0310F | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_GF_FCU6997 | FCU | Lab Sup 2 N-0310B | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0101 | AT | Office S-0244A | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0102 | AT | Office S-0244B | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0103 | AT | Office S-0244C | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0104 | AT | Office S-0244D | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0105 | AT | Office S-0244E | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0107 | AT | Office S-0262A | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0108 | AT | Office S-0262B | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0109 | AT | Office S-0262C | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0110 | AT | Office S-0262H | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0111 | AT | Office S-0262E | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0112 | AT | Office S-0262F | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0113 | AT | Office S-0262G | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_L0_AT-0114 | AT | Office S-0262D | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_GF_FCU7993 | FCU | Stair 5 N-0ST05 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_1F_FCU2004 | FCU | Corridor N-1202 | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_1F_AT-4260 | AT | Office 05 -8WS- N-0255 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_1F_AT-6372 | AT | Office N-1374 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_1F_AT-6374 | AT | Office N-1375 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_1F_AT-6376 | AT | Office N-1376 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_1F_AT-6378 | AT | Office N-1377 | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_1F_AT-0207 | AT | Open Plan S-1293A | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_1F_AT-0208 | AT | Open Plan S-1293 | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_1F_AT-0201A | AT | Policy Executive Director Office S-1240 | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_1F_AT-0201B | AT | Open Plan S-1229 | neither - nothing in the historian knows this number
removed - not in historian | RDC_SB_1F_AT-0206 | AT | Policy Executive Director Office S-1240 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_2F_AT-4900 | AT | Normal Electric N-2102 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_2F_AT-4910 | AT | Emergency Electr N-2103 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_2F_AT-6979 | AT | Normal Elec. N-2107 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_2F_AT-6980 | AT | Emer. Elec. N-2108 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_2F_AT-7975 | AT | Normal Elec. N-2111 | neither - nothing in the historian knows this number
removed - not in historian | RDC_NB_2F_AT-7980 | AT | Emer. Elec. N-2112 | neither - nothing in the historian knows this number
removed - part | RDC_SB_L0_AT-1002 | AT | Computer Lab S-0139 | part of RDC_SB_GF_CAV1002 / RDC_SB_GF_VAV1003_VEV1002
removed - part | RDC_SB_L0_EV-1001 | EV | Computer Lab S-0139 | part of RDC_SB_GF_CAV1001
removed - part | RDC_SB_L0_AT-1003 | AT | NOC S-0140A | part of RDC_SB_GF_VAV1003_VEV1002
removed - part | RDC_SB_L0_EV-1002 | EV | NOC S-0140A | part of RDC_SB_GF_CAV1002 / RDC_SB_GF_VAV1003_VEV1002
removed - part | RDC_SB_L0_AT-1004 | AT | Dedicated Cyber SOC/NOC Lab S-0141 | part of RDC_SB_GF_VAV1004
removed - part | RDC_SB_L0_EV-1003 | EV | UPS S-0145 | part of RDC_SB_GF_VAV1003_VEV1002
removed - part | RDC_SB_L0_AT-1008 | AT | Cyber/Embedded/Dist System Electrical Lab S-0146 | part of RDC_SB_GF_VAV1008
removed - part | RDC_NB_GF_AT-4005 | AT | Electrical N-0202 | part of RDC_NB_GF_VAV4005_EV4006
removed - part | RDC_NB_GF_AT-4100 | AT | Emergency Elec. Room N-0225 | part of RDC_NB_GF_VAV4100_EV4101
removed - part | RDC_NB_GF_AT-4105 | AT | Normal Electrical Room N-0225 | part of RDC_NB_GF_VAV4105_EV4106
removed - part | RDC_NB_GF_AT-4110 | AT | Conference Room N-0227 | part of RDC_NB_GF_VAV4110_EV4111
removed - part | RDC_NB_GF_AT-4115 | AT | Office N-0228 | part of RDC_NB_GF_VAV4115_EV4116
removed - part | RDC_NB_GF_AT-4120 | AT | Office N-0229 | part of RDC_NB_GF_VAV4120_EV4121
removed - part | RDC_NB_GF_AT-4125 | AT | Office N-0230 | part of RDC_NB_GF_VAV4125_EV4126
removed - part | RDC_NB_GF_AT-4130 | AT | Office N-0231 | part of RDC_NB_GF_VAV4130_EV4131
removed - part | RDC_NB_GF_AT-4135 | AT | Office N-0232 | part of RDC_NB_GF_VAV4135_EV4136
removed - part | RDC_NB_GF_AT-4140 | AT | Conference Room N-0233 | part of RDC_NB_GF_VAV4140_EV4141
removed - part | RDC_NB_GF_AT-4145 | AT | Office N-0234 | part of RDC_NB_GF_VAV4145_EV4146
removed - part | RDC_NB_GF_AT-4165 | AT | Office N-0236 | part of RDC_NB_GF_VAV4165_EV4166
removed - part | RDC_NB_GF_AT-4225 | AT | Office N-0247 | part of RDC_NB_GF_VAV4225
removed - part | RDC_NB_GF_AT-4230 | AT | Office N-0248 | part of RDC_NB_GF_VAV4230
removed - part | RDC_NB_GF_AT-4235 | AT | Workstation N-0250 | part of RDC_NB_GF_VAV4235
removed - part | RDC_NB_GF_AT-4240 | AT | Office N-0251 | part of RDC_NB_GF_VAV4240
removed - part | RDC_NB_GF_AT-4245 | AT | Office N-0252 | part of RDC_NB_GF_VAV4245
removed - part | RDC_NB_GF_AT-4250 | AT | Office N-0253 | part of RDC_NB_GF_VAV4250
removed - part | RDC_NB_GF_AT-4255 | AT | Office N-0254 | part of RDC_NB_GF_VAV4255
removed - part | RDC_NB_GF_AT-4260 | AT | Workstation N-0255 | part of RDC_NB_GF_VAV4260
removed - part | RDC_NB_GF_AT-4265 | AT | Office N-0256 | part of RDC_NB_GF_VAV4265
removed - part | RDC_NB_GF_AT-4270 | AT | Office N-0257 | part of RDC_NB_GF_VAV4270
removed - part | RDC_NB_GF_AT-4275 | AT | Office N-0258 | part of RDC_NB_GF_VAV4275
removed - part | RDC_NB_GF_AT-4280 | AT | Office N-0259 | part of RDC_NB_GF_VAV4280
removed - part | RDC_NB_GF_AT-4285 | AT | Workstation N-0260 | part of RDC_NB_GF_VAV4285
removed - part | RDC_NB_GF_AT-4290 | AT | Office N-0261 | part of RDC_NB_GF_VAV4290
removed - part | RDC_NB_GF_AT-4295 | AT | Office N-0262 | part of RDC_NB_GF_VAV4295
removed - part | RDC_NB_GF_AT-4300 | AT | Office N-0263 | part of RDC_NB_GF_VAV4300
removed - part | RDC_NB_GF_AT-4305 | AT | Office N-0264 | part of RDC_NB_GF_VAV4305
removed - part | RDC_NB_GF_AT-4310 | AT | Workstation N-0265 | part of RDC_NB_GF_VAV4310
removed - part | RDC_SB_L0_AT-0003 | AT | Entrance Lobby S-0102 | part of RDC_SB_GF_VAV0003
removed - part | RDC_SB_L0_AT-0007 | AT | Conf S-0109 | part of RDC_SB_GF_VAV0007
removed - part | RDC_SB_L0_AT-0008 | AT | Computer Research Lab 3 S-0110 | part of RDC_SB_GF_VAV0008
removed - part | RDC_SB_L0_AT-0009 | AT | Phone Booth S-0111 | part of RDC_SB_GF_VAV0009
removed - part | RDC_SB_L0_AT-0010 | AT | Phone Booth S-0112 | part of RDC_SB_GF_VAV0010
removed - part | RDC_SB_L0_AT-0011 | AT | Conference Room S-0113 | part of RDC_SB_GF_VAV0011
removed - part | RDC_SB_L0_AT-0012 | AT | Computer Research Lab 2 S-0114 | part of RDC_SB_GF_VAV0012
removed - part | RDC_SB_L0_AT-0013 | AT | Phone Booth S-0115 | part of RDC_SB_GF_VAV0013
removed - part | RDC_SB_L0_AT-0014 | AT | Phone Booth S-0116 | part of RDC_SB_GF_VAV0014
removed - part | RDC_SB_L0_AT-0016 | AT | Conf S-0118 | part of RDC_SB_GF_VAV0016
removed - part | RDC_SB_L0_AT-0017 | AT | Computer Research Lab 1 S-0119 | part of RDC_SB_GF_VAV0017
removed - part | RDC_SB_L0_AT-0018 | AT | Restaurant S-0123 | part of RDC_SB_GF_VAV0018
removed - part | RDC_SB_L0_AT-0019 | AT | Restaurant S-0123 | part of RDC_SB_GF_VAV0019
removed - part | RDC_SB_L0_AT-0025 | AT | Alt Recording/Sound S-0135 | part of RDC_SB_GF_VAV0025
removed - part | RDC_NB_GF_AT-4001 | AT | Store N-0201 | part of RDC_NB_GF_VAV4001
removed - part | RDC_NB_GF_AT-4312 | AT | Breakout N-0265B | part of RDC_NB_GF_VAV4312
removed - part | RDC_NB_GF_AT-5025 | AT | Corridor N-0110 | part of RDC_NB_GF_VAV5025
removed - part | RDC_NB_GF_AT-5100 | AT | Office N-0115 | part of RDC_NB_GF_VAV5100_EV5101
removed - part | RDC_NB_GF_AT-5105 | AT | Office N-0116 | part of RDC_NB_GF_VAV5105
removed - part | RDC_NB_GF_AT-5110 | AT | Office N-0117 | part of RDC_NB_GF_VAV5110
removed - part | RDC_NB_GF_AT-5115 | AT | Office N-0118 | part of RDC_NB_GF_VAV5115
removed - part | RDC_NB_GF_AT-5120 | AT | Office N-0119 | part of RDC_NB_GF_VAV5120
removed - part | RDC_NB_GF_AT-5125 | AT | Office N-0120 | part of RDC_NB_GF_VAV5125
removed - part | RDC_NB_GF_AT-5130 | AT | Office N-0121 | part of RDC_NB_GF_VAV5130
removed - part | RDC_NB_GF_AT-5135 | AT | Office N-0122 | part of RDC_NB_GF_VAV5135
removed - part | RDC_NB_GF_AT-5140 | AT | Office N-0123 | part of RDC_NB_GF_VAV5140
removed - part | RDC_NB_GF_AT-5145 | AT | Office N-0124 | part of RDC_NB_GF_VAV5145
removed - part | RDC_NB_GF_AT-5150 | AT | Office N-0125 | part of RDC_NB_GF_VAV5150
removed - part | RDC_NB_GF_AT-5152 | AT | Office N-0126 | part of RDC_NB_GF_VAV5152
removed - part | RDC_NB_GF_AT-5155 | AT | Office N-0127 | part of RDC_NB_GF_VAV5155
removed - part | RDC_NB_GF_AT-5156 | AT | Office 04 N-0129 | part of RDC_NB_GF_VAV5156
removed - part | RDC_NB_GF_AT-5165 | AT | Corridor N-0134 | part of RDC_NB_GF_VAV5165_EV5166
removed - part | RDC_NB_GF_AT-5295 | AT | Conference Room N-0149 | part of RDC_NB_GF_VAV5295_EV5296
removed - part | RDC_NB_GF_AT-5300 | AT | Corridor N-0150 | part of RDC_NB_GF_VAV5300
removed - part | RDC_NB_GF_AT-5305 | AT | Office N-0151 | part of RDC_NB_GF_VAV5305
removed - part | RDC_NB_GF_AT-5310 | AT | Office N-0152 | part of RDC_NB_GF_VAV5310
removed - part | RDC_NB_GF_AT-5315 | AT | Open Office N-0153 | part of RDC_NB_GF_VAV5315
removed - part | RDC_NB_GF_AT-5325 | AT | Office N-0155 | part of RDC_NB_GF_VAV5325
removed - part | RDC_NB_GF_AT-5330 | AT | Office N-0156 | part of RDC_NB_GF_VAV5330
removed - part | RDC_NB_GF_AT-5335 | AT | Office N-0157 | part of RDC_NB_GF_VAV5335
removed - part | RDC_NB_GF_AT-5340 | AT | Office N-0158 | part of RDC_NB_GF_VAV5340
removed - part | RDC_NB_GF_AT-5345 | AT | Office N-0159 | part of RDC_NB_GF_VAV5345
removed - part | RDC_NB_GF_AT-5355 | AT | Office N-0161 | part of RDC_NB_GF_VAV5355
removed - part | RDC_NB_GF_AT-5360 | AT | Office N-0162 | part of RDC_NB_GF_VAV5360
removed - part | RDC_NB_GF_AT-5365 | AT | Office N-0163 | part of RDC_NB_GF_VAV5365
removed - part | RDC_NB_GF_AT-5370 | AT | Office N-0164 | part of RDC_NB_GF_VAV5370
removed - part | RDC_NB_GF_AT-5380 | AT | Office N-0166 | part of RDC_NB_GF_VAV5380
removed - part | RDC_NB_GF_AT-5385 | AT | Office N-0167A | part of RDC_NB_GF_VAV5385
removed - part | RDC_NB_GF_AT-5390 | AT | Office 04 N-0168 | part of RDC_NB_GF_VAV5390
removed - part | RDC_NB_GF_AT-5415 | AT | Office 04 N-0174 | part of RDC_NB_GF_VAV5415
removed - part | RDC_NB_GF_EV-4316 | EV | Vestibule N-0270A | part of RDC_NB_GF_CAV4315_EV4316
removed - part | RDC_NB_GF_EV-5161 | EV | Womens+N-0130A+N-0132 JC N-0130 | part of RDC_NB_GF_CAV5160_EV5161
removed - part | RDC_NB_GF_EV-5291 | EV | Pantry N-0148 | part of RDC_NB_GF_CAV5290_EV5291
removed - part | RDC_SB_L0_AT-0001 | AT | Vestibule S-0101 | part of RDC_SB_GF_VAV0001
removed - part | RDC_SB_L0_AT-0002 | AT | Employee Entry Lobby S-0102 | part of RDC_SB_GF_VAV0002
removed - part | RDC_SB_L0_A1.3_AT-2001 | AT | WOMEN S-0205 | part of RDC_SB_GF_CAV2001
removed - part | RDC_NB_GF_AT-5010 | AT | Conf N-0106 | part of RDC_NB_GF_VAV5010_EV5011
removed - part | RDC_NB_GF_AT-5015 | AT | Conference N-0107 | part of RDC_NB_GF_VAV5015_EV5016
removed - part | RDC_NB_GF_AT-5030 | AT | Confr Room N-0112 | part of RDC_NB_GF_VAV5030_EV5031
removed - part | RDC_NB_GF_AT-5040 | AT | Normal Elec. N-0113 | part of RDC_NB_GF_VAV5040_EV5041
removed - part | RDC_NB_GF_AT-5045 | AT | Emergency Elec. N-0114 | part of RDC_NB_GF_VAV5045_EV5046
removed - part | RDC_NB_GF_AT-5395 | AT | Exp. Office N-0169 | part of RDC_NB_GF_VAV5395
removed - part | RDC_NB_GF_AT-5400 | AT | Reception Area N-0170 | part of RDC_NB_GF_VAV5400
removed - part | RDC_NB_GF_AT-5405 | AT | Exp. Office N-0172 | part of RDC_NB_GF_VAV5405
removed - part | RDC_NB_GF_AT-5410 | AT | Conf Room N-0173 | part of RDC_NB_GF_VAV5410_EV5411
removed - part | RDC_NB_GF_AT-5000 | AT | Lobby North N-0101 | part of RDC_NB_GF_VAV5000_EV5002
removed - part | RDC_NB_GF_AT-5001 | AT | Lobby North N-0101 | part of RDC_NB_GF_VAV5001_EV5003
removed - part | RDC_NB_GF_AT-6000 | AT | Conf Room N-0301 | part of RDC_NB_GF_VAV6000_EV6001
removed - part | RDC_NB_GF_AT-6010 | AT | Conf N-0304 | part of RDC_NB_GF_VAV6010_EV6011
removed - part | RDC_NB_GF_AT-6025 | AT | Normal Elec. N-0310 | part of RDC_NB_GF_VAV6025_EV6026
removed - part | RDC_NB_GF_AT-6240 | AT | Emergency Electrical N-0350A | part of RDC_NB_GF_VAV6240_EV6241
removed - part | RDC_NB_GF_AT-6300 | AT | Store N-0362B | part of RDC_NB_GF_VAV6300
removed - part | RDC_NB_GF_AT-6305 | AT | Office N-0363 | part of RDC_NB_GF_VAV6305
removed - part | RDC_NB_GF_AT-6310 | AT | Office N-0364 | part of RDC_NB_GF_VAV6310
removed - part | RDC_NB_GF_AT-6315 | AT | Conf Room N-0364A | part of RDC_NB_GF_VAV6315_EV6316
removed - part | RDC_NB_GF_EV-6316 | EV | Conf Room N-0364A | part of RDC_NB_GF_VAV6315_EV6316
removed - part | RDC_NB_GF_EV-5021 | EV | Mens + Vestibule + N-0109 N-0108 | part of RDC_NB_GF_CAV5020_EV5021
removed - part | RDC_NB_GF_EV-6016 | EV | Men N-0306 | part of RDC_NB_GF_CAV6015_EV6016
removed - part | RDC_SB_L0_AT-2002 | AT | Conference Room S-0207 | part of RDC_SB_GF_VAV2002
removed - part | RDC_SB_L0_AT-2003 | AT | Multi Purpose Hall S-0208 | part of RDC_SB_GF_VAV2003
removed - part | RDC_SB_L0_AT-2004 | AT | Multi Purpose Hall S-0208 | part of RDC_SB_GF_VAV2004
removed - part | RDC_SB_L0_AT-2006 | AT | Meeting Room S-0212 | part of RDC_SB_GF_VAV2006
removed - part | RDC_SB_L0_AT-2007 | AT | Office S-0213 | part of RDC_SB_GF_VAV2007
removed - part | RDC_SB_L0_AT-2008 | AT | Office S-0214 | part of RDC_SB_GF_VAV2008
removed - part | RDC_SB_L0_AT-2009 | AT | Office S-0215 | part of RDC_SB_GF_VAV2009
removed - part | RDC_SB_L0_AT-2010 | AT | Office S-0216 | part of RDC_SB_GF_VAV2010
removed - part | RDC_SB_L0_AT-2011 | AT | Office S-0217 | part of RDC_SB_GF_VAV2011
removed - part | RDC_SB_L0_AT-2012 | AT | Director Office S-0218 | part of RDC_SB_GF_VAV2012
removed - part | RDC_SB_L0_AT-2013 | AT | Office S-0219 | part of RDC_SB_GF_VAV2013
removed - part | RDC_SB_L0_AT-2014 | AT | Office S-0220 | part of RDC_SB_GF_VAV2014
removed - part | RDC_SB_L0_AT-2015 | AT | Director Office S-0221 | part of RDC_SB_GF_VAV2015
removed - part | RDC_SB_L0_AT-2016 | AT | Director Office S-0222 | part of RDC_SB_GF_VAV2016
removed - part | RDC_SB_L0_AT-2017 | AT | Meeting Room S-0223 | part of RDC_SB_GF_VAV2017
removed - part | RDC_SB_L0_AT-2018 | AT | PANTRY S-0226 | part of RDC_SB_GF_VAV2018
removed - part | RDC_SB_L0_AT-2019 | AT | Office S-0227 | part of RDC_SB_GF_VAV2019
removed - part | RDC_SB_L0_AT-2020 | AT | Informal Meeting S-0231 | part of RDC_SB_GF_VAV2020
removed - part | RDC_SB_L0_AT-2021 | AT | Open Plan S-0228 | part of RDC_SB_GF_VAV2021
removed - part | RDC_SB_L0_AT-2022 | AT | Director Office S-0229 | part of RDC_SB_GF_VAV2022
removed - part | RDC_SB_L0_AT-2023 | AT | Office S-0230 | part of RDC_SB_GF_VAV2023
removed - part | RDC_SB_L0_AT-2024 | AT | Executive Director Office S-0232 | part of RDC_SB_GF_VAV2024
removed - part | RDC_SB_L0_AT-2025 | AT | Executive Director Office S-0233 | part of RDC_SB_GF_VAV2025
removed - part | RDC_SB_L0_AT-2026 | AT | Office S-0234 | part of RDC_SB_GF_VAV2026
removed - part | RDC_SB_L0_AT-2027 | AT | Office S-0235 | part of RDC_SB_GF_VAV2027
removed - part | RDC_SB_L0_AT-2028 | AT | Office S-0236 | part of RDC_SB_GF_VAV2028
removed - part | RDC_SB_L0_AT-2029 | AT | Waiting Area S-0251 | part of RDC_SB_GF_VAV2029
removed - part | RDC_SB_L0_AT-2030 | AT | Office S-0259 | part of RDC_SB_GF_VAV2030
removed - part | RDC_SB_L0_AT-2031 | AT | Office S-0260 | part of RDC_SB_GF_VAV2031
removed - part | RDC_SB_L0_AT-2032 | AT | Open Plan S-0269 | part of RDC_SB_GF_VAV2032
removed - part | RDC_SB_L0_AT-2033 | AT | CORRIDOR S-0273 | part of RDC_SB_GF_VAV2033
removed - part | RDC_SB_L0_AT-2034 | AT | Meeting Room S-0274 | part of RDC_SB_GF_VAV2034
removed - part | RDC_SB_L0_AT-2035 | AT | MECH S-0272 | part of RDC_SB_GF_VAV2035
removed - part | RDC_SB_L0_AT-2036 | AT | Emergency Elec. Room S-0278 | part of RDC_SB_GF_VAV2036
removed - part | RDC_SB_L0_AT-2037 | AT | Men S-0284 | part of RDC_SB_GF_VAV2037
removed - part | RDC_SB_L0_AT-2038 | AT | Informal Meeting S-0285 | part of RDC_SB_GF_VAV2038
removed - part | RDC_SB_L0_AT-2039 | AT | Meeting Room S-0286 | part of RDC_SB_GF_VAV2039
removed - part | RDC_SB_L0_AT-2040 | AT | Open Plan S-0289 | part of RDC_SB_GF_VAV2040
removed - part | RDC_SB_L0_AT-2041 | AT | Open Plan S-0289 | part of RDC_SB_GF_VAV2041
removed - part | RDC_SB_L0_AT-2042 | AT | Lobby S-0294 | part of RDC_SB_GF_VAV2042
removed - part | RDC_SB_L0_AT-2043 | AT | Lobby S-0294 | part of RDC_SB_GF_VAV2043
removed - part | RDC_SB_L0_AT-2044 | AT | Lobby S-0294 | part of RDC_SB_GF_VAV2044
removed - part | RDC_SB_L0_AT-2045 | AT | Lobby S-0294 | part of RDC_SB_GF_VAV2045
removed - part | RDC_SB_L0_AT-2046 | AT | Lobby S-0294 | part of RDC_SB_GF_VAV2046
removed - part | RDC_SB_L0_AT-2047 | AT | Lobby S-0294 | part of RDC_SB_GF_VAV2047
removed - part | RDC_NB_GF_AT-6130 | AT | Store N-0315 | part of RDC_NB_GF_VAV6130_EV6131
removed - part | RDC_NB_GF_AT-6135 | AT | Store N-0316 | part of RDC_NB_GF_VAV6135
removed - part | RDC_NB_GF_AT-6140 | AT | Workstation N-0317 | part of RDC_NB_GF_VAV6140
removed - part | RDC_NB_GF_AT-6145 | AT | Office N-0318 | part of RDC_NB_GF_VAV6145
removed - part | RDC_NB_GF_AT-6150 | AT | Office N-0319 | part of RDC_NB_GF_VAV6150
removed - part | RDC_NB_GF_AT-6155 | AT | Workstation N-0320 | part of RDC_NB_GF_VAV6155
removed - part | RDC_NB_GF_AT-6160 | AT | Office N-0321 | part of RDC_NB_GF_VAV6160
removed - part | RDC_NB_GF_AT-6170 | AT | Office N-0323 | part of RDC_NB_GF_VAV6170
removed - part | RDC_NB_GF_AT-6175 | AT | Workstation N-0324 | part of RDC_NB_GF_VAV6175
removed - part | RDC_NB_GF_AT-6180 | AT | Office N-0325 | part of RDC_NB_GF_VAV6180
removed - part | RDC_NB_GF_AT-6185 | AT | Office N-0326 | part of RDC_NB_GF_VAV6185_EV6186
removed - part | RDC_NB_GF_AT-7000 | AT | Vestibule / Staging N-0401 | part of RDC_NB_GF_VAV7000
removed - part | RDC_NB_GF_AT-6195 | AT | Store N-0329 | part of RDC_NB_GF_VAV6195
removed - part | RDC_NB_GF_AT-6190 | AT | Normal Elec. N-0328 | part of RDC_NB_GF_VAV6190_EV6191
removed - part | RDC_NB_GF_AT-6200 | AT | Conf N-0330 | part of RDC_NB_GF_VAV6200_EV6201
removed - part | RDC_NB_GF_AT-6220 | AT | Emergency Elec. N-0333 | part of RDC_NB_GF_VAV6220_EV6221
removed - part | RDC_NB_GF_AT-6205 | AT | Conference N-0331 | part of RDC_NB_GF_VAV6205_EV6206
removed - part | RDC_NB_GF_AT-6285 | AT | Conference N-0358 | part of RDC_NB_GF_VAV6285_EV6286
removed - part | RDC_NB_GF_AT-6210 | AT | Corridor N-0332C | part of RDC_NB_GF_VAV6210
removed - part | RDC_NB_GF_AT-6295 | AT | Conference N-0360 | part of RDC_NB_GF_VAV6295_EV6296
removed - part | RDC_NB_GF_AT-6320 | AT | Corridor N-0365 | part of RDC_NB_GF_VAV6320
removed - part | RDC_NB_GF_AT-6325 | AT | Office N-0366 | part of RDC_NB_GF_VAV6325
removed - part | RDC_NB_GF_AT-6330 | AT | Office 04 N-0367 | part of RDC_NB_GF_VAV6330
removed - part | RDC_NB_GF_AT-6335 | AT | Office N-0368 | part of RDC_NB_GF_VAV6335
removed - part | RDC_NB_GF_AT-6340 | AT | Office N-0369 | part of RDC_NB_GF_VAV6340
removed - part | RDC_NB_GF_AT-6345 | AT | Office N-0370 | part of RDC_NB_GF_VAV6345
removed - part | RDC_NB_GF_AT-6350 | AT | Office N-0371 | part of RDC_NB_GF_VAV6350
removed - part | RDC_NB_GF_AT-6355 | AT | Workstation N-0372 | part of RDC_NB_GF_VAV6355
removed - part | RDC_NB_GF_AT-6360 | AT | Office N-0374 | part of RDC_NB_GF_VAV6360
removed - part | RDC_NB_GF_AT-6365 | AT | Office N-0375 | part of RDC_NB_GF_VAV6365
removed - part | RDC_NB_GF_AT-6370 | AT | Office N-0376 | part of RDC_NB_GF_VAV6370
removed - part | RDC_NB_GF_AT-6375 | AT | Office N-0377 | part of RDC_NB_GF_VAV6375
removed - part | RDC_NB_GF_AT-6380 | AT | Workstation N-0378 | part of RDC_NB_GF_VAV6380
removed - part | RDC_NB_GF_AT-6390 | AT | Office N-0379 | part of RDC_NB_GF_VAV6390
removed - part | RDC_NB_GF_AT-6395 | AT | Office N-0380 | part of RDC_NB_GF_VAV6395
removed - part | RDC_NB_GF_AT-6400 | AT | Workstation N-0381 | part of RDC_NB_GF_VAV6400
removed - part | RDC_NB_GF_AT-6405 | AT | Office N-0382 | part of RDC_NB_GF_VAV6405
removed - part | RDC_NB_GF_AT-6410 | AT | Office N-0383 | part of RDC_NB_GF_VAV6410
removed - part | RDC_NB_GF_AT-7385 | AT | Office N-0444 | part of RDC_NB_GF_VAV7385
removed - part | RDC_NB_GF_AT-7390 | AT | Office 04 N-0445 | part of RDC_NB_GF_VAV7390
removed - part | RDC_NB_GF_EV-6281 | EV | Pantry N-0356 | part of RDC_NB_GF_CAV6280_EV6281
removed - part | RDC_NB_GF_EV-7006 | EV | WOMEN N-0402 | part of RDC_NB_GF_CAV7005_EV7006
removed - part | RDC_NB_GF_EV-7381 | EV | Pipe Chase N-0443B | part of RDC_NB_GF_CAV7380_EV7381
removed - part | RDC_SB_L0_AT-3001 | AT | Director Office S-0237 | part of RDC_SB_GF_VAV3001
removed - part | RDC_SB_L0_AT-3002 | AT | Office S-0238 | part of RDC_SB_GF_VAV3002
removed - part | RDC_SB_L0_AT-3003 | AT | Office S-0239 | part of RDC_SB_GF_VAV3003
removed - part | RDC_SB_L0_AT-3004 | AT | Office S-0240 | part of RDC_SB_GF_VAV3004
removed - part | RDC_SB_L0_AT-3005 | AT | Office S-0241 | part of RDC_SB_GF_VAV3005
removed - part | RDC_SB_L0_AT-3006 | AT | Office S-0242 | part of RDC_SB_GF_VAV3006
removed - part | RDC_SB_L0_AT-3007 | AT | Director Office S-0243 | part of RDC_SB_GF_VAV3007
removed - part | RDC_SB_L0_AT-3010 | AT | Open Plan S-0244 | part of RDC_SB_GF_VAV3010
removed - part | RDC_SB_L0_AT-3011 | AT | Meeting Room S-0245 | part of RDC_SB_GF_VAV3011
removed - part | RDC_SB_L0_AT-3012 | AT | Office S-0246 | part of RDC_SB_GF_VAV3012
removed - part | RDC_SB_L0_AT-3013 | AT | Office S-0247 | part of RDC_SB_GF_VAV3013
removed - part | RDC_SB_L0_AT-3014 | AT | Office S-0248 | part of RDC_SB_GF_VAV3014
removed - part | RDC_SB_L0_AT-3015 | AT | Security S-0249 | part of RDC_SB_GF_VAV3015
removed - part | RDC_SB_L0_AT-3016 | AT | Corridor S-0250 | part of RDC_SB_GF_VAV3016
removed - part | RDC_SB_L0_AT-3017 | AT | Office S-0251 | part of RDC_SB_GF_VAV3017
removed - part | RDC_SB_L0_AT-3018 | AT | Corridor S-0251B | part of RDC_SB_GF_VAV3018
removed - part | RDC_SB_L0_AT-3019 | AT | Corridor S-0251B | part of RDC_SB_GF_VAV3019
removed - part | RDC_SB_L0_AT-3020 | AT | Office S-0252 | part of RDC_SB_GF_VAV3020
removed - part | RDC_SB_L0_AT-3021 | AT | Office S-0252 | part of RDC_SB_GF_VAV3021
removed - part | RDC_SB_L0_AT-3022 | AT | Office S-0253 | part of RDC_SB_GF_VAV3022
removed - part | RDC_SB_L0_AT-3023 | AT | Office S-0253 | part of RDC_SB_GF_VAV3023
removed - part | RDC_SB_L0_AT-3024 | AT | Office S-0254 | part of RDC_SB_GF_VAV3024
removed - part | RDC_SB_L0_AT-3025 | AT | Office S-0255 | part of RDC_SB_GF_VAV3025
removed - part | RDC_SB_L0_AT-3026 | AT | Office S-0256 | part of RDC_SB_GF_VAV3026
removed - part | RDC_SB_L0_AT-3027 | AT | Office S-0257 | part of RDC_SB_GF_VAV3027
removed - part | RDC_SB_L0_AT-3028 | AT | Office S-0258 | part of RDC_SB_GF_VAV3028
removed - part | RDC_SB_L0_AT-3031 | AT | IT Server S-0264 | part of RDC_SB_GF_VAV3031
removed - part | RDC_SB_L0_AT-3032 | AT | Open Plan S-0265 | part of RDC_SB_GF_VAV3032
removed - part | RDC_SB_L0_AT-3033 | AT | Emergency Elec. S-0266 | part of RDC_SB_GF_VAV3033
removed - part | RDC_SB_L0_AT-3034 | AT | Reception / Vestibule S-0293 | part of RDC_SB_GF_VAV3034
removed - part | RDC_SB_L0_AT-3035 | AT | Lobby S-0294 | part of RDC_SB_GF_VAV3035
removed - part | RDC_SB_L0_AT-3036 | AT | Lobby S-0294 | part of RDC_SB_GF_VAV3036
removed - part | RDC_NB_GF_AT-7080 | AT | Exp. Office N-0410 | part of RDC_NB_GF_VAV7080
removed - part | RDC_NB_GF_AT-7085 | AT | Office N-0411 | part of RDC_NB_GF_VAV7085
removed - part | RDC_NB_GF_AT-7095 | AT | Office N-0413 | part of RDC_NB_GF_VAV7095
removed - part | RDC_NB_GF_AT-7100 | AT | Office N-0414 | part of RDC_NB_GF_VAV7100
removed - part | RDC_NB_GF_AT-7110 | AT | Office N-0416 | part of RDC_NB_GF_VAV7110
removed - part | RDC_NB_GF_AT-7115 | AT | Office N-0417 | part of RDC_NB_GF_VAV7115
removed - part | RDC_NB_GF_AT-7125 | AT | NORMAL ELEC. ROOM N-0420 | part of RDC_NB_GF_VAV7125_EV7126
removed - part | RDC_NB_GF_AT-7130 | AT | Office N-0421 | part of RDC_NB_GF_VAV7130
removed - part | RDC_NB_GF_AT-7135 | AT | Office N-0422 | part of RDC_NB_GF_VAV7135
removed - part | RDC_NB_GF_AT-7140 | AT | Conference N-0423 | part of RDC_NB_GF_VAV7140_EV7141
removed - part | RDC_NB_GF_AT-7145 | AT | Office N-0425 | part of RDC_NB_GF_VAV7145
removed - part | RDC_NB_GF_AT-7155 | AT | Office N-0427 | part of RDC_NB_GF_VAV7155
removed - part | RDC_NB_GF_AT-7165 | AT | Office N-0429 | part of RDC_NB_GF_VAV7165
removed - part | RDC_NB_GF_AT-7180 | AT | Corridor N-0432 | part of RDC_NB_GF_VAV7180
removed - part | RDC_NB_GF_AT-7185 | AT | Emer. Elec. Room N-0433 | part of RDC_NB_GF_VAV7185_EV7186
removed - part | RDC_NB_GF_AT-7195 | AT | OFFICE N-0436 | part of RDC_NB_GF_VAV7195
removed - part | RDC_NB_GF_AT-7205 | AT | Office 04 N-0438 | part of RDC_NB_GF_VAV7205
removed - part | RDC_NB_GF_AT-7215 | AT | CONFERENCE ROOM N-0440 | part of RDC_NB_GF_VAV7215_EV7216
removed - part | RDC_NB_GF_AT-7395 | AT | Workstation N-0446 | part of RDC_NB_GF_VAV7395
removed - part | RDC_NB_GF_AT-7400 | AT | Office N-0447 | part of RDC_NB_GF_VAV7400
removed - part | RDC_NB_GF_AT-7405 | AT | Office N-0448 | part of RDC_NB_GF_VAV7405
removed - part | RDC_NB_GF_AT-7410 | AT | Office N-0449 | part of RDC_NB_GF_VAV7410
removed - part | RDC_NB_GF_AT-7415 | AT | Office N-0450 | part of RDC_NB_GF_VAV7415
removed - part | RDC_NB_GF_AT-7425 | AT | Workstation N-0452 | part of RDC_NB_GF_VAV7425
removed - part | RDC_NB_GF_AT-7430 | AT | Office N-0453 | part of RDC_NB_GF_VAV7430
removed - part | RDC_NB_GF_AT-7435 | AT | Office N-0454 | part of RDC_NB_GF_VAV7435
removed - part | RDC_NB_GF_AT-7440 | AT | Office N-0455 | part of RDC_NB_GF_VAV7440
removed - part | RDC_NB_GF_AT-7445 | AT | Office N-0456 | part of RDC_NB_GF_VAV7445
removed - part | RDC_NB_GF_AT-7460 | AT | Workstation N-0457 | part of RDC_NB_GF_VAV7460
removed - part | RDC_NB_GF_AT-7465 | AT | Office N-0458 | part of RDC_NB_GF_VAV7465
removed - part | RDC_NB_GF_AT-7470 | AT | Office N-0459 | part of RDC_NB_GF_VAV7470
removed - part | RDC_NB_GF_AT-7475 | AT | Office N-0460 | part of RDC_NB_GF_VAV7475
removed - part | RDC_NB_GF_AT-7480 | AT | Office N-0461 | part of RDC_NB_GF_VAV7480
removed - part | RDC_NB_GF_AT-7485 | AT | WORKSTATION N-0462 | part of RDC_NB_GF_VAV7485
removed - part | RDC_NB_GF_AT-7490 | AT | Confer N-0463 | part of RDC_NB_GF_VAV7490_EV7495
removed - part | RDC_NB_GF_AT-7496 | AT | Office N-0464 | part of RDC_NB_GF_VAV7496
removed - part | RDC_NB_GF_AT-7498 | AT | Office N-0465 | part of RDC_NB_GF_VAV7498
removed - part | RDC_NB_GF_AT-7499 | AT | Office N-0466 | part of RDC_NB_GF_VAV7499
removed - part | RDC_NB_GF_AT-7090-N1 | AT | Office N-0412 | part of RDC_NB_GF_VAV7090
removed - part | RDC_NB_GF_AT-7090-N2 | AT | Office N-0412A | part of RDC_NB_GF_VAV7090
removed - part | RDC_NB_GF_AT-7105-N1 | AT | Office N-0415 | part of RDC_NB_GF_VAV7105
removed - part | RDC_NB_GF_AT-7105-N2 | AT | Office N-0415A | part of RDC_NB_GF_VAV7105
removed - part | RDC_NB_GF_AT-7120-N1 | AT | Office N-0418 | part of RDC_NB_GF_VAV7120
removed - part | RDC_NB_GF_AT-7120-N2 | AT | Office N-0418A | part of RDC_NB_GF_VAV7120
removed - part | RDC_NB_GF_AT-7120-N3 | AT | Office N-0430A | part of RDC_NB_GF_VAV7120
removed - part | RDC_NB_GF_AT-7120-N4 | AT | Office N-0430B | part of RDC_NB_GF_VAV7120
removed - part | RDC_NB_GF_AT-7120-N5 | AT | Office N-0430C | part of RDC_NB_GF_VAV7120
removed - part | RDC_NB_GF_AT-7120-N6 | AT | Office N-0430D | part of RDC_NB_GF_VAV7120
removed - part | RDC_NB_GF_AT-7120-N7 | AT | Office N-0430E | part of RDC_NB_GF_VAV7120
removed - part | RDC_NB_GF_AT-7120-N8 | AT | Office N-0430F | part of RDC_NB_GF_VAV7120
removed - part | RDC_NB_GF_AT-7120-N9 | AT | Corridor N-0418A | part of RDC_NB_GF_VAV7120
removed - part | RDC_SB_1F_AT-1507 | AT | Workstation S-1124A | part of RDC_SB_1F_VAV1507
removed - part | RDC_SB_1F_AT-1508 | AT | Scientific Comp. Office 1 S-1125 | part of RDC_SB_1F_VAV1508
removed - part | RDC_SB_1F_AT-1509 | AT | Scientific Comp. Office S-1126 | part of RDC_SB_1F_VAV1509
removed - part | RDC_SB_1F_AT-1510 | AT | ALT Office 2 S-1127 | part of RDC_SB_1F_VAV1510
removed - part | RDC_SB_1F_AT-1511 | AT | ALT Office 3 S-1128 | part of RDC_SB_1F_VAV1511
removed - part | RDC_SB_1F_AT-1512 | AT | Workstation S-1128A | part of RDC_SB_1F_VAV1512
removed - part | RDC_SB_1F_AT-1513 | AT | ALT Office 1 S-1129 | part of RDC_SB_1F_VAV1513
removed - part | RDC_SB_1F_AT-1514 | AT | ALT Office S-1130 | part of RDC_SB_1F_VAV1514
removed - part | RDC_SB_1F_AT-1515 | AT | Distub. Syst Office 1 S-1131 | part of RDC_SB_1F_VAV1515
removed - part | RDC_SB_1F_AT-1516 | AT | Distub. Syst Office S-1132 | part of RDC_SB_1F_VAV1516
removed - part | RDC_SB_1F_AT-1517 | AT | Workstation S-1132A | part of RDC_SB_1F_VAV1517
removed - part | RDC_SB_1F_AT-1518 | AT | Distub. Syst Office S-1133 | part of RDC_SB_1F_VAV1518
removed - part | RDC_SB_1F_AT-1519 | AT | Distub. Syst Office S-1134 | part of RDC_SB_1F_VAV1519
removed - part | RDC_SB_1F_AT-1520 | AT | Data Analytic Office S-1135 | part of RDC_SB_1F_VAV1520
removed - part | RDC_SB_1F_AT-1521 | AT | Data Analytic Office S-1136 | part of RDC_SB_1F_VAV1521
removed - part | RDC_SB_1F_AT-1522 | AT | Workstation S-1136A | part of RDC_SB_1F_VAV1522
removed - part | RDC_SB_1F_AT-1523 | AT | Data Analytic Office S-1137 | part of RDC_SB_1F_VAV1523
removed - part | RDC_SB_1F_AT-1524 | AT | Data Analytic Office S-1138 | part of RDC_SB_1F_VAV1524
removed - part | RDC_SB_1F_AT-1525 | AT | Office S-1139 | part of RDC_SB_1F_VAV1525
removed - part | RDC_SB_1F_AT-1526 | AT | Office S-1140 | part of RDC_SB_1F_VAV1526
removed - part | RDC_SB_1F_AT-1527 | AT | Conference Room S-1141 | part of RDC_SB_1F_VAV1527
removed - part | RDC_SB_1F_AT-1528 | AT | Office S-1142 | part of RDC_SB_1F_VAV1528
removed - part | RDC_SB_1F_AT-1529 | AT | Office S-1144 | part of RDC_SB_1F_VAV1529
removed - part | RDC_SB_1F_AT-1530 | AT | Office S-1145 | part of RDC_SB_1F_VAV1530
removed - part | RDC_SB_1F_AT-1531 | AT | Office S-1146 | part of RDC_SB_1F_VAV1531
removed - part | RDC_SB_1F_AT-1532 | AT | Workstation S-1146A | part of RDC_SB_1F_VAV1532
removed - part | RDC_SB_1F_AT-1533 | AT | Office S-1148 | part of RDC_SB_1F_VAV1533
removed - part | RDC_SB_1F_AT-1534 | AT | Office S-1149 | part of RDC_SB_1F_VAV1534
removed - part | RDC_SB_1F_AT-1536 | AT | Office S-1150 | part of RDC_SB_1F_VAV1536
removed - part | RDC_SB_1F_AT-1542 | AT | Office S-1182 | part of RDC_SB_1F_VAV1542
removed - part | RDC_SB_1F_AT-1546 | AT | Office S-1182E | part of RDC_SB_1F_VAV1546
removed - part | RDC_SB_1F_AT-1548 | AT | Office S-1183 | part of RDC_SB_1F_VAV1548
removed - part | RDC_SB_1F_AT-1549 | AT | Workstation S-1183A | part of RDC_SB_1F_VAV1549
removed - part | RDC_SB_1F_AT-1550 | AT | Office S-1184 | part of RDC_SB_1F_VAV1550
removed - part | RDC_SB_1F_AT-1551 | AT | Social Comp Office S-1185 | part of RDC_SB_1F_VAV1551
removed - part | RDC_SB_1F_AT-1552 | AT | Social Comp Office S-1186 | part of RDC_SB_1F_VAV1552
removed - part | RDC_SB_1F_AT-1553 | AT | Workstation S-1186A | part of RDC_SB_1F_VAV1553
removed - part | RDC_SB_1F_AT-1554 | AT | Social Comp Office S-1187 | part of RDC_SB_1F_VAV1554
removed - part | RDC_SB_1F_AT-1555 | AT | Social Comp Office S-1188 | part of RDC_SB_1F_VAV1555
removed - part | RDC_SB_1F_AT-1556 | AT | Cyber Sec Office S-1189 | part of RDC_SB_1F_VAV1556
removed - part | RDC_SB_1F_AT-1557 | AT | Cyber Sec Office S-1190 | part of RDC_SB_1F_VAV1557
removed - part | RDC_SB_1F_AT-1558 | AT | Workstation S-1190A | part of RDC_SB_1F_VAV1558
removed - part | RDC_SB_1F_AT-1559 | AT | Office S-1191 | part of RDC_SB_1F_VAV1559
removed - part | RDC_SB_1F_AT-1560 | AT | Cyber Sec Office S-1192 | part of RDC_SB_1F_VAV1560
removed - part | RDC_SB_1F_AT-1561 | AT | Cyber Sec Office S-1193 | part of RDC_SB_1F_VAV1561
removed - part | RDC_SB_1F_AT-0538 | AT | Workstation S-1151A | part of RDC_SB_1F_VAV0538
removed - part | RDC_NB_1F_AT-4660 | AT | Expansion Workstation N-1227 | part of RDC_NB_1F_VAV4660
removed - part | RDC_NB_1F_AT-4665 | AT | Office N-1228 | part of RDC_NB_1F_VAV4665
removed - part | RDC_NB_1F_AT-4680 | AT | Office N-1231 | part of RDC_NB_1F_VAV4680
removed - part | RDC_NB_1F_AT-4690 | AT | Office N-1233 | part of RDC_NB_1F_VAV4690
removed - part | RDC_NB_1F_AT-4705 | AT | Office N-1236 | part of RDC_NB_1F_VAV4705
removed - part | RDC_NB_1F_AT-4720 | AT | Office N-1239 | part of RDC_NB_1F_VAV4720
removed - part | RDC_NB_1F_AT-4730 | AT | Office N-1241 | part of RDC_NB_1F_VAV4730
removed - part | RDC_NB_1F_AT-4745 | AT | Office N-1244 | part of RDC_NB_1F_VAV4745
removed - part | RDC_SB_1F_AT-0506 | AT | Conf. S-1110 | part of RDC_SB_1F_VAV0506
removed - part | RDC_SB_1F_AT-0507 | AT | Computer Research Lab-4 S-1112 | part of RDC_SB_1F_VAV0507
removed - part | RDC_SB_1F_AT-0508 | AT | Conf S-1113 | part of RDC_SB_1F_VAV0508
removed - part | RDC_SB_1F_AT-0509 | AT | NCIR OFFICE S-1115 | part of RDC_SB_1F_VAV0509
removed - part | RDC_SB_1F_AT-0510 | AT | Workstation S-1115A | part of RDC_SB_1F_VAV0510
removed - part | RDC_SB_1F_AT-0511 | AT | NCIR Office S-1116 | part of RDC_SB_1F_VAV0511
removed - part | RDC_SB_1F_AT-0512 | AT | NCIR Office S-1117 | part of RDC_SB_1F_VAV0512
removed - part | RDC_SB_1F_AT-0513 | AT | NCIR Office S-1118 | part of RDC_SB_1F_VAV0513
removed - part | RDC_SB_1F_AT-0514 | AT | NCIR Office S-1119 | part of RDC_SB_1F_VAV0514
removed - part | RDC_SB_1F_AT-0518 | AT | Office S-1161 | part of RDC_SB_1F_VAV0518
removed - part | RDC_SB_1F_AT-0519 | AT | Office S-1162 | part of RDC_SB_1F_VAV0519
removed - part | RDC_SB_1F_AT-0520 | AT | Office S-1163 | part of RDC_SB_1F_VAV0520
removed - part | RDC_SB_1F_AT-0521 | AT | Office S-1164 | part of RDC_SB_1F_VAV0521
removed - part | RDC_SB_1F_AT-0522 | AT | Office S-1165 | part of RDC_SB_1F_VAV0522
removed - part | RDC_SB_1F_AT-0523 | AT | Office S-1166 | part of RDC_SB_1F_VAV0523
removed - part | RDC_SB_1F_AT-0526 | AT | Office S-1171 | part of RDC_SB_1F_VAV0526
removed - part | RDC_SB_1F_AT-0527 | AT | Office S-1172 | part of RDC_SB_1F_VAV0527
removed - part | RDC_SB_1F_AT-0528 | AT | Office S-1173 | part of RDC_SB_1F_VAV0528
removed - part | RDC_SB_1F_AT-0529 | AT | Corridor S-1174 | part of RDC_SB_1F_VAV0529
removed - part | RDC_SB_1F_AT-0530 | AT | Situation Room S-1175 | part of RDC_SB_1F_VAV0530
removed - part | RDC_SB_1F_AT-0531 | AT | Immersive Viz Lab S-1176 | part of RDC_SB_1F_VAV0531
removed - part | RDC_SB_1F_AT-0532 | AT | Conference Room S-1177 | part of RDC_SB_1F_VAV0532
removed - part | RDC_SB_1F_AT-0533 | AT | Telepresence S-1179 | part of RDC_SB_1F_VAV0533
removed - part | RDC_SB_1F_AT-1501 | AT | Workstation S-1119A | part of RDC_SB_1F_VAV1501
removed - part | RDC_SB_1F_AT-1502 | AT | NCIR Office S-1120 | part of RDC_SB_1F_VAV1502
removed - part | RDC_SB_1F_AT-1503 | AT | NCIR Office S-1121 | part of RDC_SB_1F_VAV1503
removed - part | RDC_SB_1F_AT-1505 | AT | SC. Comp Office 2 S-1123 | part of RDC_SB_1F_VAV1505
removed - part | RDC_SB_1F_AT-1506 | AT | SC. Comp Office 3 S-1124 | part of RDC_SB_1F_VAV1506
removed - part | RDC_SB_1F_AT-1539 | AT | Video Conf. Room S-1154 | part of RDC_SB_1F_VAV1539
removed - part | RDC_SB_1F_AT-1540 | AT | Conf S-1159 | part of RDC_SB_1F_VAV1540
removed - part | RDC_SB_1F_AT-1543 | AT | Workstation S-1182A | part of RDC_SB_1F_VAV1543
removed - part | RDC_SB_1F_AT-1544 | AT | Office S-1182C | part of RDC_SB_1F_VAV1544
removed - part | RDC_SB_1F_AT-1545 | AT | Office S-1182D | part of RDC_SB_1F_VAV1545
removed - part | RDC_SB_1F_AT-1547 | AT | Office S-1182F | part of RDC_SB_1F_VAV1547
removed - part | RDC_NB_1F_AT-5650 | AT | Office N-1120 | part of RDC_NB_1F_VAV5650
removed - part | RDC_NB_1F_AT-5655 | AT | Store N-1120B | part of RDC_NB_1F_VAV5655_EV5656
removed - part | RDC_NB_1F_AT-5660 | AT | Office N-1121 | part of RDC_NB_1F_VAV5660
removed - part | RDC_NB_1F_AT-5665 | AT | Office N-1122 | part of RDC_NB_1F_VAV5665
removed - part | RDC_NB_1F_AT-5670 | AT | Office N-1123 | part of RDC_NB_1F_VAV5670
removed - part | RDC_NB_1F_AT-5675 | AT | Office N-1124 | part of RDC_NB_1F_VAV5675
removed - part | RDC_NB_1F_AT-5680 | AT | Office N-1125 | part of RDC_NB_1F_VAV5680
removed - part | RDC_NB_1F_AT-5685 | AT | Corridor N-1126 | part of RDC_NB_1F_VAV5685
removed - part | RDC_NB_1F_AT-5690 | AT | Office N-1127 | part of RDC_NB_1F_VAV5690
removed - part | RDC_NB_1F_AT-5695 | AT | Office N-1128 | part of RDC_NB_1F_VAV5695
removed - part | RDC_NB_1F_AT-5700 | AT | Office N-1129 | part of RDC_NB_1F_VAV5700
removed - part | RDC_NB_1F_AT-5705 | AT | Office N-1130 | part of RDC_NB_1F_VAV5705
removed - part | RDC_NB_1F_AT-5710 | AT | Office N-1131 | part of RDC_NB_1F_VAV5710
removed - part | RDC_NB_1F_AT-5715 | AT | Conf Rm N-1132 | part of RDC_NB_1F_VAV5715_EV5716
removed - part | RDC_NB_1F_AT-5730 | AT | Store N-1135 | part of RDC_NB_1F_VAV5730_EV5731
removed - part | RDC_NB_1F_AT-5735 | AT | Normal Elec. N-1136 | part of RDC_NB_1F_VAV5735_EV5736
removed - part | RDC_NB_1F_AT-5740 | AT | Emer. Elec. N-1137 | part of RDC_NB_1F_VAV5740_EV5741
removed - part | RDC_NB_1F_AT-5745 | AT | Corridor N-1138 | part of RDC_NB_1F_VAV5745
removed - part | RDC_NB_1F_AT-5760 | AT | Conf N-1143 | part of RDC_NB_1F_VAV5760_EV5761
removed - part | RDC_NB_1F_AT-5835 | AT | P/C/S Pantry N-1146 | part of RDC_NB_1F_VAV5835_EV5836
removed - part | RDC_NB_1F_AT-5840 | AT | Corridor N-1150 | part of RDC_NB_1F_VAV5840
removed - part | RDC_NB_1F_AT-5860 | AT | Office N-1154 | part of RDC_NB_1F_VAV5860
removed - part | RDC_NB_1F_AT-5865 | AT | Office N-1155 | part of RDC_NB_1F_VAV5865
removed - part | RDC_NB_1F_AT-5870 | AT | Exp Office N-1156 | part of RDC_NB_1F_VAV5870
removed - part | RDC_NB_1F_AT-5875 | AT | Office N-1157 | part of RDC_NB_1F_VAV5875
removed - part | RDC_NB_1F_AT-5880 | AT | Office N-1158 | part of RDC_NB_1F_VAV5880
removed - part | RDC_NB_1F_AT-5885 | AT | Office N-1159 | part of RDC_NB_1F_VAV5885
removed - part | RDC_NB_1F_AT-5890 | AT | Workstation N-1160 | part of RDC_NB_1F_VAV5890
removed - part | RDC_NB_1F_AT-5895 | AT | Office N-1161 | part of RDC_NB_1F_VAV5895
removed - part | RDC_NB_1F_AT-5900 | AT | Office N-1162 | part of RDC_NB_1F_VAV5900
removed - part | RDC_NB_1F_AT-5905 | AT | Office N-1163 | part of RDC_NB_1F_VAV5905
removed - part | RDC_NB_1F_AT-5910 | AT | Office N-1164 | part of RDC_NB_1F_VAV5910
removed - part | RDC_NB_1F_AT-5915 | AT | Office N-1167 | part of RDC_NB_1F_VAV5915
removed - part | RDC_NB_1F_AT-5920 | AT | Workstation N-1168 | part of RDC_NB_1F_VAV5920
removed - part | RDC_NB_1F_AT-5925 | AT | Office N-1169 | part of RDC_NB_1F_VAV5925
removed - part | RDC_NB_1F_AT-5930 | AT | Office N-1170 | part of RDC_NB_1F_VAV5930
removed - part | RDC_NB_1F_AT-5935 | AT | Office N-1166 | part of RDC_NB_1F_VAV5935
removed - part | RDC_NB_1F_AT-5940 | AT | Workstation N-1165 | part of RDC_NB_1F_VAV5940
removed - part | RDC_NB_1F_AT-4650 | AT | Breakout N-1225 | part of RDC_NB_1F_VAV4650
removed - part | RDC_NB_1F_EV-5721 | EV | Men N-1134 | part of RDC_NB_1F_CAV5720_EV5721
removed - part | RDC_NB_1F_EV-4641 | EV | Women N-1221 | part of RDC_NB_1F_CAV4640_EV4641
removed - part | RDC_SB_1F_AT-2501 | AT | Lobby S-1201 | part of RDC_SB_1F_VAV2501
removed - part | RDC_SB_1F_AT-2502 | AT | Lobby S-1202 | part of RDC_SB_1F_VAV2502
removed - part | RDC_SB_1F_AT-2503 | AT | Lobby S-1202 | part of RDC_SB_1F_VAV2503
removed - part | RDC_SB_1F_AT-2504 | AT | Lobby S-1202 | part of RDC_SB_1F_VAV2504
removed - part | RDC_SB_1F_AT-2505 | AT | Lobby S-1202 | part of RDC_SB_1F_VAV2505
removed - part | RDC_SB_1F_AT-2506 | AT | Lobby S-1202 | part of RDC_SB_1F_VAV2506
removed - part | RDC_SB_1F_AT-2508 | AT | Female Prayer S-1207 | part of RDC_SB_1F_VAV2508
removed - part | RDC_SB_1F_AT-2509 | AT | Open Plan S-1210 | part of RDC_SB_1F_VAV2509
removed - part | RDC_SB_1F_AT-2510 | AT | Exc. Dir. Office S-1211 | part of RDC_SB_1F_VAV2510
removed - part | RDC_SB_1F_AT-2511 | AT | Office S-1212 | part of RDC_SB_1F_VAV2511
removed - part | RDC_SB_1F_AT-2512 | AT | Office S-1213 | part of RDC_SB_1F_VAV2512
removed - part | RDC_SB_1F_AT-2513 | AT | Office S-1214 | part of RDC_SB_1F_VAV2513
removed - part | RDC_SB_1F_AT-2514 | AT | Office S-1215 | part of RDC_SB_1F_VAV2514
removed - part | RDC_SB_1F_AT-2515 | AT | Office S-1216 | part of RDC_SB_1F_VAV2515
removed - part | RDC_SB_1F_AT-2516 | AT | Executive Director Office S-1217 | part of RDC_SB_1F_VAV2516
removed - part | RDC_SB_1F_AT-2517 | AT | Executive Director Office S-1218 | part of RDC_SB_1F_VAV2517
removed - part | RDC_SB_1F_AT-2518 | AT | Office S-1219 | part of RDC_SB_1F_VAV2518
removed - part | RDC_SB_1F_AT-2519 | AT | Office S-1220 | part of RDC_SB_1F_VAV2519
removed - part | RDC_SB_1F_AT-2520 | AT | Office S-1221 | part of RDC_SB_1F_VAV2520
removed - part | RDC_SB_1F_AT-2521 | AT | Office S-1222 | part of RDC_SB_1F_VAV2521
removed - part | RDC_SB_1F_AT-2522 | AT | Office S-1223 | part of RDC_SB_1F_VAV2522
removed - part | RDC_SB_1F_AT-2523 | AT | Office S-1224 | part of RDC_SB_1F_VAV2523
removed - part | RDC_SB_1F_AT-2524 | AT | Office S-1225 | part of RDC_SB_1F_VAV2524
removed - part | RDC_SB_1F_AT-2525 | AT | Office S-1226 | part of RDC_SB_1F_VAV2525
removed - part | RDC_SB_1F_AT-2526 | AT | Open Plan S-1227 | part of RDC_SB_1F_VAV2526
removed - part | RDC_SB_1F_AT-2527 | AT | Director Office S-1228 | part of RDC_SB_1F_VAV2527
removed - part | RDC_SB_1F_AT-2528 | AT | Director Office S-1230 | part of RDC_SB_1F_VAV2528
removed - part | RDC_SB_1F_AT-2529 | AT | Office S-1231 | part of RDC_SB_1F_VAV2529
removed - part | RDC_SB_1F_AT-2530 | AT | Office S-1232 | part of RDC_SB_1F_VAV2530
removed - part | RDC_SB_1F_AT-2531 | AT | Director Ofice S-1241 | part of RDC_SB_1F_VAV2531
removed - part | RDC_SB_1F_AT-2532 | AT | Office S-1242 | part of RDC_SB_1F_VAV2532
removed - part | RDC_SB_1F_AT-2533 | AT | Cooridor S-1246 | part of RDC_SB_1F_VAV2533
removed - part | RDC_SB_1F_AT-2534 | AT | Meeting Room S-1247 | part of RDC_SB_1F_VAV2534
removed - part | RDC_SB_1F_AT-2535 | AT | Store S-1248 | part of RDC_SB_1F_VAV2535
removed - part | RDC_SB_1F_AT-2536 | AT | Normal Elec. S-1251 | part of RDC_SB_1F_VAV2536
removed - part | RDC_SB_1F_AT-2538 | AT | Office S-1257 | part of RDC_SB_1F_VAV2538
removed - part | RDC_SB_1F_AT-2539 | AT | Office S-1257B | part of RDC_SB_1F_VAV2539
removed - part | RDC_SB_1F_AT-2540 | AT | Executive Director S-1260 | part of RDC_SB_1F_VAV2540
removed - part | RDC_SB_1F_AT-2541 | AT | Assistant S-1261 | part of RDC_SB_1F_VAV2541
removed - part | RDC_SB_1F_AT-2542 | AT | Open Plan S-1263 | part of RDC_SB_1F_VAV2542
removed - part | RDC_SB_1F_AT-2543 | AT | Office S-1264 | part of RDC_SB_1F_VAV2543
removed - part | RDC_SB_1F_AT-2544 | AT | Office S-1265 | part of RDC_SB_1F_VAV2544
removed - part | RDC_SB_1F_AT-2545 | AT | Office S-1266 | part of RDC_SB_1F_VAV2545
removed - part | RDC_SB_1F_AT-2546 | AT | Office S-1267 | part of RDC_SB_1F_VAV2546
removed - part | RDC_SB_1F_AT-2547 | AT | Office S-1268 | part of RDC_SB_1F_VAV2547
removed - part | RDC_SB_1F_AT-2548 | AT | Office S-1269 | part of RDC_SB_1F_VAV2548
removed - part | RDC_SB_1F_AT-2549 | AT | Office S-1270 | part of RDC_SB_1F_VAV2549
removed - part | RDC_SB_1F_AT-2550 | AT | Office S-1271 | part of RDC_SB_1F_VAV2550
removed - part | RDC_SB_1F_AT-2551 | AT | Meeting Room S-1272 | part of RDC_SB_1F_VAV2551
removed - part | RDC_SB_1F_AT-2552 | AT | Vestibule S-1273 | part of RDC_SB_1F_VAV2552
removed - part | RDC_SB_1F_AT-2553 | AT | Male Prayer S-1278 | part of RDC_SB_1F_VAV2553
removed - part | RDC_NB_1F_AT-6650 | AT | Office N-1319 | part of RDC_NB_1F_VAV6650
removed - part | RDC_NB_1F_AT-6655 | AT | Office N-1320 | part of RDC_NB_1F_VAV6655
removed - part | RDC_NB_1F_AT-6660 | AT | Workstation N-1321 | part of RDC_NB_1F_VAV6660
removed - part | RDC_NB_1F_AT-6665 | AT | Office N-1322 | part of RDC_NB_1F_VAV6665
removed - part | RDC_NB_1F_AT-6670 | AT | Office N-1323 | part of RDC_NB_1F_VAV6670
removed - part | RDC_NB_1F_AT-6675 | AT | Workstation N-1324 | part of RDC_NB_1F_VAV6675
removed - part | RDC_NB_1F_AT-6680 | AT | Office N-1325 | part of RDC_NB_1F_VAV6680
removed - part | RDC_NB_1F_AT-6685 | AT | Office N-1326 | part of RDC_NB_1F_VAV6685
removed - part | RDC_NB_1F_AT-6690 | AT | Exp. Workstation N-1327 | part of RDC_NB_1F_VAV6690
removed - part | RDC_NB_1F_AT-6695 | AT | Office N-1328 | part of RDC_NB_1F_VAV6695
removed - part | RDC_NB_1F_AT-6700 | AT | NORMAL ELEC. N-1329 | part of RDC_NB_1F_VAV6700_EV6701
removed - part | RDC_NB_1F_AT-6705 | AT | Office N-1330 | part of RDC_NB_1F_VAV6705
removed - part | RDC_NB_1F_AT-6710 | AT | Office N-1331 | part of RDC_NB_1F_VAV6710
removed - part | RDC_NB_1F_AT-6715 | AT | Office N-1332 | part of RDC_NB_1F_VAV6715
removed - part | RDC_NB_1F_AT-6720 | AT | Corridor N-1335 | part of RDC_NB_1F_VAV6720
removed - part | RDC_NB_1F_AT-6725 | AT | Emer. Elec. N-1336 | part of RDC_NB_1F_VAV6725_EV6726
removed - part | RDC_NB_1F_AT-6900 | AT | Office N-1357 | part of RDC_NB_1F_VAV6900
removed - part | RDC_NB_1F_AT-6905 | AT | Open Plan N-1358 | part of RDC_NB_1F_VAV6905
removed - part | RDC_NB_1F_AT-6910 | AT | Office N-1359 | part of RDC_NB_1F_VAV6910
removed - part | RDC_NB_1F_AT-6915 | AT | Office N-1360 | part of RDC_NB_1F_VAV6915
removed - part | RDC_NB_1F_AT-6920 | AT | Office N-1360B | part of RDC_NB_1F_VAV6920
removed - part | RDC_NB_1F_AT-6925 | AT | Office N-1361 | part of RDC_NB_1F_VAV6925
removed - part | RDC_NB_1F_AT-6930 | AT | Office N-1362 | part of RDC_NB_1F_VAV6930
removed - part | RDC_NB_1F_AT-6935 | AT | Workstation N-1363 | part of RDC_NB_1F_VAV6935
removed - part | RDC_NB_1F_AT-6940 | AT | Office N-1364 | part of RDC_NB_1F_VAV6940
removed - part | RDC_NB_1F_AT-6945 | AT | Office N-1365 | part of RDC_NB_1F_VAV6945
removed - part | RDC_NB_1F_AT-6950 | AT | Office N-1366 | part of RDC_NB_1F_VAV6950
removed - part | RDC_NB_1F_AT-6955 | AT | Office N-1367 | part of RDC_NB_1F_VAV6955
removed - part | RDC_NB_1F_AT-6960 | AT | Workstation N-1368 | part of RDC_NB_1F_VAV6960
removed - part | RDC_NB_1F_AT-6965 | AT | Office N-1369 | part of RDC_NB_1F_VAV6965
removed - part | RDC_NB_1F_AT-6967 | AT | Office N-1370 | part of RDC_NB_1F_VAV6967
removed - part | RDC_NB_1F_AT-6968 | AT | Workstation N-1371 | part of RDC_NB_1F_VAV6968
removed - part | RDC_NB_1F_AT-6970 | AT | PANTRY N-1372 | part of RDC_NB_1F_VAV6970_EV6971
removed - part | RDC_NB_1F_AT-7865 | AT | Workstation N-1461A | part of RDC_NB_1F_VAV7865
removed - part | RDC_NB_1F_EV-6741 | EV | Men N-1340 | part of RDC_NB_1F_CAV6740_EV6741
removed - part | RDC_NB_1F_EV-7501 | EV | Women N-1403 | part of RDC_NB_1F_CAV7500_EV7501
removed - part | RDC_SB_1F_AT-3501 | AT | Lobby S-0294 | part of RDC_SB_GF_VAV3501
removed - part | RDC_SB_1F_AT-3502 | AT | Lobby S-0294 | part of RDC_SB_GF_VAV3502
removed - part | RDC_SB_1F_AT-3503 | AT | Reception S-0293 | part of RDC_SB_GF_VAV3503
removed - part | RDC_SB_1F_AT-3504 | AT | Open Plan S-1229 | part of RDC_SB_1F_VAV3504
removed - part | RDC_SB_1F_AT-3505 | AT | Open Plan S-1229 | part of RDC_SB_1F_VAV3505
removed - part | RDC_SB_1F_AT-3506 | AT | Office S-1233 | part of RDC_SB_1F_VAV3506
removed - part | RDC_SB_1F_AT-3507 | AT | Office S-1234 | part of RDC_SB_1F_VAV3507
removed - part | RDC_SB_1F_AT-3508 | AT | Office S-1235 | part of RDC_SB_1F_VAV3508
removed - part | RDC_SB_1F_AT-3509 | AT | Policy Director Office S-1237 | part of RDC_SB_1F_VAV3509
removed - part | RDC_SB_1F_AT-3510 | AT | Policy Executive Director Office S-1240 | part of RDC_SB_1F_VAV3510
removed - part | RDC_SB_1F_AT-3511 | AT | CORRIDOR S-1280 | part of RDC_SB_1F_VAV3511
removed - part | RDC_SB_1F_AT-3512 | AT | Pantry S-1282 | part of RDC_SB_1F_VAV3512
removed - part | RDC_SB_1F_AT-3513 | AT | Office S-1283 | part of RDC_SB_1F_VAV3513
removed - part | RDC_SB_1F_AT-3514 | AT | Office S-1284 | part of RDC_SB_1F_VAV3514
removed - part | RDC_SB_1F_AT-3515 | AT | S-1285 VP R&D | part of RDC_SB_1F_VAV3515
removed - part | RDC_SB_1F_AT-3516 | AT | Meeting Room S-1288 | part of RDC_SB_1F_VAV3516
removed - part | RDC_SB_1F_AT-3517 | AT | Dressing Room S-1290 | part of RDC_SB_1F_VAV3517
removed - part | RDC_SB_1F_AT-3518 | AT | Waiting Area S-1292 | part of RDC_SB_1F_VAV3518
removed - part | RDC_SB_1F_AT-3520 | AT | Office S-1294 | part of RDC_SB_1F_VAV3520
removed - part | RDC_SB_1F_AT-3521 | AT | Office S-1295 | part of RDC_SB_1F_VAV3521
removed - part | RDC_SB_1F_AT-3522 | AT | Conference Room S-1296 | part of RDC_SB_1F_VAV3522
removed - part | RDC_SB_1F_AT-3523 | AT | Office S-1299 | part of RDC_SB_1F_VAV3523
removed - part | RDC_SB_1F_AT-3524 | AT | Normal Elec. S-1238 | part of RDC_SB_1F_VAV3524
removed - part | RDC_NB_1F_AT-7620 | AT | Office N-1415 | part of RDC_NB_1F_VAV7620
removed - part | RDC_NB_1F_AT-7625 | AT | Office N-1416 | part of RDC_NB_1F_VAV7625
removed - part | RDC_NB_1F_AT-7630 | AT | Office 05 - 2 WKS- N-1407 | part of RDC_NB_1F_VAV7630
removed - part | RDC_NB_1F_AT-7635 | AT | Office N-1418 | part of RDC_NB_1F_VAV7635
removed - part | RDC_NB_1F_AT-7640 | AT | Office N-1419 | part of RDC_NB_1F_VAV7640
removed - part | RDC_NB_1F_AT-7645 | AT | Exp. Workstation N-1420 | part of RDC_NB_1F_VAV7645
removed - part | RDC_NB_1F_AT-7650 | AT | Office N-1421 | part of RDC_NB_1F_VAV7650
removed - part | RDC_NB_1F_AT-7655 | AT | Office N-1422 | part of RDC_NB_1F_VAV7655
removed - part | RDC_NB_1F_AT-7660 | AT | Office 05 - 2 WKS- N-1401 | part of RDC_NB_1F_VAV7660
removed - part | RDC_NB_1F_AT-7665 | AT | Normal Elec. N-1425 | part of RDC_NB_1F_VAV7665_EV7666
removed - part | RDC_NB_1F_AT-7670 | AT | Office N-1426 | part of RDC_NB_1F_VAV7670
removed - part | RDC_NB_1F_AT-7675 | AT | Office N-1428 | part of RDC_NB_1F_VAV7675
removed - part | RDC_NB_1F_AT-7680 | AT | Conf N-1429 | part of RDC_NB_1F_VAV7680_EV7681
removed - part | RDC_NB_1F_AT-7685 | AT | Office N-1433 | part of RDC_NB_1F_VAV7685
removed - part | RDC_NB_1F_AT-7690 | AT | Office N-1435 | part of RDC_NB_1F_VAV7690
removed - part | RDC_NB_1F_AT-7695 | AT | Office N-1437 | part of RDC_NB_1F_VAV7695
removed - part | RDC_NB_1F_AT-7700 | AT | Emer. Elec. N-1438 | part of RDC_NB_1F_VAV7700_EV7701
removed - part | RDC_NB_1F_AT-7705 | AT | Expansion WORKstation N-1442 | part of RDC_NB_1F_VAV7705
removed - part | RDC_NB_1F_AT-7710 | AT | Office 05 - 24 WKS + N-1441 Room N-1442 | part of RDC_NB_1F_VAV7710
removed - part | RDC_NB_1F_AT-7840 | AT | Conf N-1458 | part of RDC_NB_1F_VAV7840_EV7841
removed - part | RDC_NB_1F_AT-7845 | AT | Conf N-1459 | part of RDC_NB_1F_VAV7845_EV7846
removed - part | RDC_NB_1F_AT-7850 | AT | Office N-1459A | part of RDC_NB_1F_VAV7850
removed - part | RDC_NB_1F_AT-7860 | AT | Exp. Workstation N-1461 | part of RDC_NB_1F_VAV7860
removed - part | RDC_NB_1F_AT-7870 | AT | Office N-1462 | part of RDC_NB_1F_VAV7870
removed - part | RDC_NB_1F_AT-7875 | AT | Office N-1463 | part of RDC_NB_1F_VAV7875
removed - part | RDC_NB_1F_AT-7880 | AT | Office N-1464 | part of RDC_NB_1F_VAV7880
removed - part | RDC_NB_1F_AT-7885 | AT | Office N-1465 | part of RDC_NB_1F_VAV7885
removed - part | RDC_NB_1F_AT-7890 | AT | Workstation N-1466 | part of RDC_NB_1F_VAV7890
removed - part | RDC_NB_1F_AT-7895 | AT | Office N-1467 | part of RDC_NB_1F_VAV7895
removed - part | RDC_NB_1F_AT-7900 | AT | Office N-1468 | part of RDC_NB_1F_VAV7900
removed - part | RDC_NB_1F_AT-7905 | AT | Office N-1469 | part of RDC_NB_1F_VAV7905
removed - part | RDC_NB_1F_AT-7910 | AT | Office N-1470 | part of RDC_NB_1F_VAV7910
removed - part | RDC_NB_1F_AT-7915 | AT | Workstation N-1471 | part of RDC_NB_1F_VAV7915
removed - part | RDC_NB_1F_AT-7920 | AT | Office N-1472 | part of RDC_NB_1F_VAV7920
removed - part | RDC_NB_1F_AT-7925 | AT | Office N-1473 | part of RDC_NB_1F_VAV7925
removed - part | RDC_NB_1F_AT-7930 | AT | Office N-1474 | part of RDC_NB_1F_VAV7930
removed - part | RDC_NB_1F_AT-7935 | AT | Office N-1475 | part of RDC_NB_1F_VAV7935
removed - part | RDC_NB_1F_AT-7940 | AT | Workstation N-1476 | part of RDC_NB_1F_VAV7940
removed - part | RDC_NB_1F_AT-7945 | AT | Office N-1477 | part of RDC_NB_1F_VAV7945
removed - part | RDC_NB_1F_AT-7950 | AT | Office N-1478 | part of RDC_NB_1F_VAV7950
removed - part | RDC_NB_1F_AT-7955 | AT | Office N-1479 | part of RDC_NB_1F_VAV7955
removed - part | RDC_NB_1F_AT-7960 | AT | Office N-1480 | part of RDC_NB_1F_VAV7960
removed - part | RDC_NB_1F_CEV-7581 | CEV | TC3 N-1404H | part of RDC_NB_1F_VAV7580_VEV7581
removed - part | RDC_NB_1F_CEV-6831 | CEV | SHARED COLD LAB N-1345G | part of RDC_NB_1F_VAV6830_VEV6831
removed - part | RDC_NB_2F_AT-5930 | AT | Office 04 N-1170 | part of RDC_NB_1F_VAV5930
removed - part | RDC_NB_2F_AT-5940 | AT | Office 05 - 8 WKS- N-1165 | part of RDC_NB_1F_VAV5940
kept - already the assembly | RDC_NB_1F_VAV7830_VEV7831 | VEV | TC2 N-1450N | the register already names the whole assembly; the historian spells it RDC_NB_1F_VAV7830_7831
renamed in place - unit | RDC_SB_GF_CAV1001 | CAV |  | its parts named 2 different rooms - left blank; was RDC_SB_L0_AT-1001, and takes the place of RDC_SB_L0_AT-1001, RDC_SB_L0_EV-1001
renamed in place - unit | RDC_SB_GF_CAV1005 | CAV | Normal & Emergency Elec. Landing S-0142 | room kept from its 1 part row(s); was RDC_SB_L0_AT-1005, and takes the place of RDC_SB_L0_AT-1005
renamed in place - unit | RDC_SB_GF_CAV1006 | CAV | Corridor S-0137 | room kept from its 1 part row(s); was RDC_SB_L0_AT-1006, and takes the place of RDC_SB_L0_AT-1006
renamed in place - unit | RDC_SB_GF_CAV1007 | CAV | UPS S-0145 | room kept from its 1 part row(s); was RDC_SB_L0_AT-1007, and takes the place of RDC_SB_L0_AT-1007
renamed in place - unit | RDC_SB_GF_CAV1009 | CAV | Service Dock S-0151 | room kept from its 1 part row(s); was RDC_SB_L0_AT-1009, and takes the place of RDC_SB_L0_AT-1009
renamed in place - unit | RDC_NB_GF_CAV4035 | CAV | Corridor N-0207A | room kept from its 1 part row(s); was RDC_NB_GF_AT-4035, and takes the place of RDC_NB_GF_AT-4035
renamed in place - unit | RDC_NB_GF_CAV4170 | CAV | Storage Room N-0237 | room kept from its 1 part row(s); was RDC_NB_GF_AT-4170, and takes the place of RDC_NB_GF_AT-4170
renamed in place - unit | RDC_NB_GF_EAV4028 | EAV | MDF ROOM N-0206A | room kept from its 1 part row(s); was RDC_NB_GF_EV-4028, and takes the place of RDC_NB_GF_EV-4028
renamed in place - unit | RDC_NB_GF_EAV4236 | EAV | Office 05 -8WS- N-0250 | room kept from its 1 part row(s); was RDC_NB_GF_EV-4236, and takes the place of RDC_NB_GF_EV-4236
renamed in place - unit | RDC_NB_GF_EAV4261 | EAV | Office 05 -8WS- N-0255 | room kept from its 1 part row(s); was RDC_NB_GF_EV-4261, and takes the place of RDC_NB_GF_EV-4261
renamed in place - unit | RDC_NB_GF_EAV4286 | EAV | Office 05 -8WS- N-0260 | room kept from its 1 part row(s); was RDC_NB_GF_EV-4286, and takes the place of RDC_NB_GF_EV-4286
renamed in place - unit | RDC_NB_GF_EAV4311 | EAV | WORKSTATION N-0265 | room kept from its 1 part row(s); was RDC_NB_GF_EV-4311, and takes the place of RDC_NB_GF_EV-4311
renamed in place - unit | RDC_SB_GF_CAV0006 | CAV | Normal Elec. S-0107 | room kept from its 1 part row(s); was RDC_SB_L0_AT-0006, and takes the place of RDC_SB_L0_AT-0006
renamed in place - unit | RDC_SB_GF_CAV0015 | CAV | Corridor S-0117 | room kept from its 1 part row(s); was RDC_SB_L0_AT-0015, and takes the place of RDC_SB_L0_AT-0015
renamed in place - unit | RDC_SB_GF_CAV0020 | CAV | Storage S-0120B | room kept from its 1 part row(s); was RDC_SB_L0_AT-0020, and takes the place of RDC_SB_L0_AT-0020
renamed in place - unit | RDC_SB_GF_CAV0021 | CAV | Vestibule S-0125 | room kept from its 1 part row(s); was RDC_SB_L0_AT-0021, and takes the place of RDC_SB_L0_AT-0021
renamed in place - unit | RDC_SB_GF_CAV0022 | CAV | Men S-0126 | room kept from its 1 part row(s); was RDC_SB_L0_AT-0022, and takes the place of RDC_SB_L0_AT-0022
renamed in place - unit | RDC_SB_GF_CAV0023 | CAV | Women S-0127 | room kept from its 1 part row(s); was RDC_SB_L0_AT-0023, and takes the place of RDC_SB_L0_AT-0023
renamed in place - unit | RDC_SB_GF_CAV0024 | CAV | NORM. ELEC. S-0129 | room kept from its 1 part row(s); was RDC_SB_L0_AT-0024, and takes the place of RDC_SB_L0_AT-0024
renamed in place - unit | RDC_NB_GF_CAV4315_EV4316 | CAV | Vestibule N-0270A | room kept from its 2 part row(s); was RDC_NB_GF_AT-4315, and takes the place of RDC_NB_GF_AT-4315, RDC_NB_GF_EV-4316
renamed in place - unit | RDC_NB_GF_CAV5160_EV5161 | CAV |  | its parts named 2 different rooms - left blank; was RDC_NB_GF_AT-5160, and takes the place of RDC_NB_GF_AT-5160, RDC_NB_GF_EV-5161
renamed in place - unit | RDC_NB_GF_CAV5280 | CAV | Store N-0146 | room kept from its 1 part row(s); was RDC_NB_GF_AT-5280, and takes the place of RDC_NB_GF_AT-5280
renamed in place - unit | RDC_NB_GF_CAV5290_EV5291 | CAV | Pantry N-0148 | room kept from its 2 part row(s); was RDC_NB_GF_AT-5290, and takes the place of RDC_NB_GF_AT-5290, RDC_NB_GF_EV-5291
renamed in place - unit | RDC_NB_GF_CAV5320 | CAV | Office N-0154 | room kept from its 1 part row(s); was RDC_NB_GF_AT-5320, and takes the place of RDC_NB_GF_AT-5320
renamed in place - unit | RDC_NB_GF_CAV5350 | CAV | Open Office N-0160 | room kept from its 1 part row(s); was RDC_NB_GF_AT-5350, and takes the place of RDC_NB_GF_AT-5350
renamed in place - unit | RDC_NB_GF_CAV5375 | CAV | Open Office N-0165 | room kept from its 1 part row(s); was RDC_NB_GF_AT-5375, and takes the place of RDC_NB_GF_AT-5375
renamed in place - unit | RDC_NB_GF_EAV5026 | EAV | Corridor N-0110 | room kept from its 1 part row(s); was RDC_NB_GF_EV-5026, and takes the place of RDC_NB_GF_EV-5026
renamed in place - unit | RDC_NB_GF_EAV5163 | EAV | IDF N-0133 | room kept from its 1 part row(s); was RDC_NB_GF_EV-5163, and takes the place of RDC_NB_GF_EV-5163
renamed in place - unit | RDC_NB_GF_FEV5192A | FEV | Furnace Room N-0140B | room kept from its 1 part row(s); was RDC_NB_GF_VEV-5192a, and takes the place of RDC_NB_GF_VEV-5192a
renamed in place - unit | RDC_NB_GF_FEV5192B | FEV | Furnace Room N-0140B | room kept from its 1 part row(s); was RDC_NB_GF_VEV-5192b, and takes the place of RDC_NB_GF_VEV-5192b
renamed in place - unit | RDC_NB_GF_CAV5240_CEV5241 | CAV | Air Lock N-0140G | room kept from its 1 part row(s); was RDC_NB_GF_CEV-5241, and takes the place of RDC_NB_GF_CEV-5241
renamed in place - unit | RDC_SB_GF_CAV0004 | CAV | Corridor S-0104 | room kept from its 1 part row(s); was RDC_SB_L0_AT-0004, and takes the place of RDC_SB_L0_AT-0004
renamed in place - unit | RDC_SB_GF_CAV0005 | CAV | Men S-0105 | room kept from its 1 part row(s); was RDC_SB_L0_AT-0005, and takes the place of RDC_SB_L0_AT-0005
renamed in place - unit | RDC_SB_GF_CAV2001 | CAV |  | its parts named 2 different rooms - left blank; was RDC_SB_L0_A1.2_AT-2001, and takes the place of RDC_SB_L0_A1.2_AT-2001, RDC_SB_L0_A1.3_AT-2001
renamed in place - unit | RDC_NB_GF_CAV5005 | CAV | Vestibule N-0105 | room kept from its 1 part row(s); was RDC_NB_GF_AT-5005, and takes the place of RDC_NB_GF_AT-5005
renamed in place - unit | RDC_NB_GF_CAV5020_EV5021 | CAV | Mens + Vestibule + N-0109 N-0108 | room kept from its 2 part row(s); was RDC_NB_GF_AT-5020, and takes the place of RDC_NB_GF_AT-5020, RDC_NB_GF_EV-5021
renamed in place - unit | RDC_NB_GF_CAV6005 | CAV | Vestibule N-0302 | room kept from its 1 part row(s); was RDC_NB_GF_AT-6005, and takes the place of RDC_NB_GF_AT-6005
renamed in place - unit | RDC_NB_GF_CAV6015_EV6016 | CAV | Men N-0306 | room kept from its 2 part row(s); was RDC_NB_GF_AT-6015, and takes the place of RDC_NB_GF_AT-6015, RDC_NB_GF_EV-6016
renamed in place - unit | RDC_NB_GF_CAV6020 | CAV | Vestibule N-0308 | room kept from its 1 part row(s); was RDC_NB_GF_AT-6020, and takes the place of RDC_NB_GF_AT-6020
renamed in place - unit | RDC_NB_GF_EAV6127 | EAV | IDF N-0311 | room kept from its 1 part row(s); was RDC_NB_GF_EV-6127, and takes the place of RDC_NB_GF_EV-6127
renamed in place - unit | RDC_NB_GF_CAV7005_EV7006 | CAV | WOMEN N-0402 | room kept from its 2 part row(s); was RDC_NB_GF_AT-7005, and takes the place of RDC_NB_GF_AT-7005, RDC_NB_GF_EV-7006
renamed in place - unit | RDC_NB_GF_CAV7380_EV7381 | CAV | Pipe Chase N-0443B | room kept from its 2 part row(s); was RDC_NB_GF_AT-7380, and takes the place of RDC_NB_GF_AT-7380, RDC_NB_GF_EV-7381
renamed in place - unit | RDC_NB_GF_CAV6280_EV6281 | CAV | Pantry N-0356 | room kept from its 2 part row(s); was RDC_NB_GF_AT-6280, and takes the place of RDC_NB_GF_AT-6280, RDC_NB_GF_EV-6281
renamed in place - unit | RDC_NB_GF_EAV6141 | EAV | Workstation N-0317 | room kept from its 1 part row(s); was RDC_NB_GF_EV-6141, and takes the place of RDC_NB_GF_EV-6141
renamed in place - unit | RDC_NB_GF_EAV6156 | EAV | Workstation N-0320 | room kept from its 1 part row(s); was RDC_NB_GF_EV-6156, and takes the place of RDC_NB_GF_EV-6156
renamed in place - unit | RDC_NB_GF_EAV6176 | EAV | Workstation N-0324 | room kept from its 1 part row(s); was RDC_NB_GF_EV-6176, and takes the place of RDC_NB_GF_EV-6176
renamed in place - unit | RDC_NB_GF_EAV6356 | EAV | Office 05-8-WKS N-0372 | room kept from its 1 part row(s); was RDC_NB_GF_EV-6356, and takes the place of RDC_NB_GF_EV-6356
renamed in place - unit | RDC_NB_GF_EAV6381 | EAV | Office 05-8-WKS N-0378 | room kept from its 1 part row(s); was RDC_NB_GF_EV-6381, and takes the place of RDC_NB_GF_EV-6381
renamed in place - unit | RDC_NB_GF_EAV6401 | EAV | Office 05-8-WKS N-0381 | room kept from its 1 part row(s); was RDC_NB_GF_EV-6401, and takes the place of RDC_NB_GF_EV-6401
renamed in place - unit | RDC_NB_GF_EAV7091 | EAV | Office N-0412A | room kept from its 1 part row(s); was RDC_NB_GF_EV-7091, and takes the place of RDC_NB_GF_EV-7091
renamed in place - unit | RDC_NB_GF_EAV7106 | EAV | Office N-0415A | room kept from its 1 part row(s); was RDC_NB_GF_EV-7106, and takes the place of RDC_NB_GF_EV-7106
renamed in place - unit | RDC_NB_GF_EAV7121 | EAV | Office 05-4-WS N-0418 | room kept from its 1 part row(s); was RDC_NB_GF_EV-7121, and takes the place of RDC_NB_GF_EV-7121
renamed in place - unit | RDC_NB_GF_EAV7122 | EAV | IDF Room N-0419 | room kept from its 1 part row(s); was RDC_NB_GF_EV-7122, and takes the place of RDC_NB_GF_EV-7122
renamed in place - unit | RDC_NB_GF_EAV7396 | EAV | Office 05-8-WKS N-0446 | room kept from its 1 part row(s); was RDC_NB_GF_EV-7396, and takes the place of RDC_NB_GF_EV-7396
renamed in place - unit | RDC_NB_GF_EAV7426 | EAV | Office 05-8-WKS N-0452 | room kept from its 1 part row(s); was RDC_NB_GF_EV-7426, and takes the place of RDC_NB_GF_EV-7426
renamed in place - unit | RDC_NB_GF_EAV7461 | EAV | Office 05-8-WKS N-0457 | room kept from its 1 part row(s); was RDC_NB_GF_EV-7461, and takes the place of RDC_NB_GF_EV-7461
renamed in place - unit | RDC_NB_GF_EAV7486 | EAV | Office 05-8-WKS N-0462 | room kept from its 1 part row(s); was RDC_NB_GF_EV-7486, and takes the place of RDC_NB_GF_EV-7486
renamed in place - unit | RDC_SB_1F_CAV1504 | CAV | Corridor S-1122 | room kept from its 1 part row(s); was RDC_SB_1F_AT-1504, and takes the place of RDC_SB_1F_AT-1504
renamed in place - unit | RDC_SB_1F_CAV1535 | CAV | Pantry S-1149A | room kept from its 1 part row(s); was RDC_SB_1F_AT-1535, and takes the place of RDC_SB_1F_AT-1535
renamed in place - unit | RDC_SB_1F_CAV1537 | CAV | Normal Elec. S-1147 | room kept from its 1 part row(s); was RDC_SB_1F_AT-1537, and takes the place of RDC_SB_1F_AT-1537
renamed in place - unit | RDC_NB_1F_EAV4500 | EAV | MDF N-1201 | room kept from its 1 part row(s); was RDC_NB_1F_EV-4500, and takes the place of RDC_NB_1F_EV-4500
renamed in place - unit | RDC_NB_1F_EAV4661 | EAV | Office 05 - 8 WKS- N-1227 | room kept from its 1 part row(s); was RDC_NB_1F_EV-4661, and takes the place of RDC_NB_1F_EV-4661
renamed in place - unit | RDC_NB_1F_EAV4686 | EAV | Office 05 - 8 WKS- N-1232 | room kept from its 1 part row(s); was RDC_NB_1F_EV-4686, and takes the place of RDC_NB_1F_EV-4686
renamed in place - unit | RDC_NB_1F_EAV4711 | EAV | Office 05 - 8 WKS- N-1237 | room kept from its 1 part row(s); was RDC_NB_1F_EV-4711, and takes the place of RDC_NB_1F_EV-4711
renamed in place - unit | RDC_NB_1F_EAV4736 | EAV | Office 05 - 8 WKS- N-1242 | room kept from its 1 part row(s); was RDC_NB_1F_EV-4736, and takes the place of RDC_NB_1F_EV-4736
renamed in place - unit | RDC_SB_1F_CAV0501 | CAV | Lobby S-1102 | room kept from its 1 part row(s); was RDC_SB_1F_AT-0501, and takes the place of RDC_SB_1F_AT-0501
renamed in place - unit | RDC_SB_1F_CAV0502 | CAV | Vestibule S-1105 | room kept from its 1 part row(s); was RDC_SB_1F_AT-0502, and takes the place of RDC_SB_1F_AT-0502
renamed in place - unit | RDC_SB_1F_CAV0503 | CAV | Women S-1106B | room kept from its 1 part row(s); was RDC_SB_1F_AT-0503, and takes the place of RDC_SB_1F_AT-0503
renamed in place - unit | RDC_SB_1F_CAV0504 | CAV | Vestibule S-1107 | room kept from its 1 part row(s); was RDC_SB_1F_AT-0504, and takes the place of RDC_SB_1F_AT-0504
renamed in place - unit | RDC_SB_1F_CAV0505 | CAV | EMERGENCY Elec. S-1107B | room kept from its 1 part row(s); was RDC_SB_1F_AT-0505, and takes the place of RDC_SB_1F_AT-0505
renamed in place - unit | RDC_SB_1F_CAV0515 | CAV | Corridor S-1122 | room kept from its 1 part row(s); was RDC_SB_1F_AT-0515, and takes the place of RDC_SB_1F_AT-0515
renamed in place - unit | RDC_SB_1F_CAV0516 | CAV | Pantry S-1158 | room kept from its 1 part row(s); was RDC_SB_1F_AT-0516, and takes the place of RDC_SB_1F_AT-0516
renamed in place - unit | RDC_SB_1F_CAV0517 | CAV | Normal Elec. S-1160 | room kept from its 1 part row(s); was RDC_SB_1F_AT-0517, and takes the place of RDC_SB_1F_AT-0517
renamed in place - unit | RDC_SB_1F_CAV0524 | CAV | Women S-1169 | room kept from its 1 part row(s); was RDC_SB_1F_AT-0524, and takes the place of RDC_SB_1F_AT-0524
renamed in place - unit | RDC_SB_1F_CAV0525 | CAV | Men S-1170 | room kept from its 1 part row(s); was RDC_SB_1F_AT-0525, and takes the place of RDC_SB_1F_AT-0525
renamed in place - unit | RDC_SB_1F_CAV0534 | CAV | CORRIDOR S-1180 | room kept from its 1 part row(s); was RDC_SB_1F_AT-0534, and takes the place of RDC_SB_1F_AT-0534
renamed in place - unit | RDC_SB_1F_CAV0535 | CAV | Cooridor S-1180 | room kept from its 1 part row(s); was RDC_SB_1F_AT-0535, and takes the place of RDC_SB_1F_AT-0535
renamed in place - unit | RDC_SB_1F_CAV1541 | CAV | Cooridor S-1181 | room kept from its 1 part row(s); was RDC_SB_1F_AT-1541, and takes the place of RDC_SB_1F_AT-1541
renamed in place - unit | RDC_NB_1F_CAV5720_EV5721 | CAV | Men N-1134 | room kept from its 2 part row(s); was RDC_NB_1F_AT-5720, and takes the place of RDC_NB_1F_AT-5720, RDC_NB_1F_EV-5721
renamed in place - unit | RDC_NB_1F_CAV5750 | CAV | Store N-1141 | room kept from its 1 part row(s); was RDC_NB_1F_AT-5750, and takes the place of RDC_NB_1F_AT-5750
renamed in place - unit | RDC_NB_1F_CAV4640_EV4641 | CAV | Women N-1221 | room kept from its 2 part row(s); was RDC_NB_1F_AT-4640, and takes the place of RDC_NB_1F_AT-4640, RDC_NB_1F_EV-4641
renamed in place - unit | RDC_NB_1F_EAV5686 | EAV | Corridor N-1126 | room kept from its 1 part row(s); was RDC_NB_1F_EV-5686, and takes the place of RDC_NB_1F_EV-5686
renamed in place - unit | RDC_NB_1F_EAV5747 | EAV | IDF N-1140 | room kept from its 1 part row(s); was RDC_NB_1F_EV-5747, and takes the place of RDC_NB_1F_EV-5747
renamed in place - unit | RDC_NB_1F_EAV5891 | EAV | Office 05 - 8 WKS- North N-1160 | room kept from its 1 part row(s); was RDC_NB_1F_EV-5891, and takes the place of RDC_NB_1F_EV-5891
renamed in place - unit | RDC_NB_1F_EAV5921 | EAV | Office 05 - 8 WKS- N-1168 | room kept from its 1 part row(s); was RDC_NB_1F_EV-5921, and takes the place of RDC_NB_1F_EV-5921
renamed in place - unit | RDC_NB_1F_EAV5941 | EAV | Office 05 - 8 WKS- N-1165 | room kept from its 1 part row(s); was RDC_NB_1F_EV-5941, and takes the place of RDC_NB_1F_EV-5941
renamed in place - unit | RDC_SB_1F_CAV2507 | CAV | Female S-1204 | room kept from its 1 part row(s); was RDC_SB_1F_AT-2507, and takes the place of RDC_SB_1F_AT-2507
renamed in place - unit | RDC_NB_1F_CAV6740_EV6741 | CAV | Men N-1340 | room kept from its 2 part row(s); was RDC_NB_1F_AT-6740, and takes the place of RDC_NB_1F_AT-6740, RDC_NB_1F_EV-6741
renamed in place - unit | RDC_NB_1F_CAV7500_EV7501 | CAV | Women N-1403 | room kept from its 2 part row(s); was RDC_NB_1F_AT-7500, and takes the place of RDC_NB_1F_AT-7500, RDC_NB_1F_EV-7501
renamed in place - unit | RDC_NB_1F_EAV6661 | EAV | Workstation N-1321 | room kept from its 1 part row(s); was RDC_NB_1F_EV-6661, and takes the place of RDC_NB_1F_EV-6661
renamed in place - unit | RDC_NB_1F_EAV6676 | EAV | Workstation N-1324 | room kept from its 1 part row(s); was RDC_NB_1F_EV-6676, and takes the place of RDC_NB_1F_EV-6676
renamed in place - unit | RDC_NB_1F_EAV6691 | EAV | Exp. Workstation N-1327 | room kept from its 1 part row(s); was RDC_NB_1F_EV-6691, and takes the place of RDC_NB_1F_EV-6691
renamed in place - unit | RDC_NB_1F_EAV6936 | EAV | Workstation N-1363 | room kept from its 1 part row(s); was RDC_NB_1F_EV-6936, and takes the place of RDC_NB_1F_EV-6936
renamed in place - unit | RDC_NB_1F_EAV6961 | EAV | Workstation N-1368 | room kept from its 1 part row(s); was RDC_NB_1F_EV-6961, and takes the place of RDC_NB_1F_EV-6961
renamed in place - unit | RDC_NB_1F_EAV6969 | EAV | Workstation N-1371 | room kept from its 1 part row(s); was RDC_NB_1F_EV-6969, and takes the place of RDC_NB_1F_EV-6969
renamed in place - unit | RDC_NB_1F_CAV6790_CEV6791 | CAV | TC2 N-1345C | room kept from its 1 part row(s); was RDC_NB_1F_CEV-6791, and takes the place of RDC_NB_1F_CEV-6791
renamed in place - unit | RDC_NB_1F_EAV7631 | EAV | Office 05 - 2 WKS- N-1407 | room kept from its 1 part row(s); was RDC_NB_1F_EV-7631, and takes the place of RDC_NB_1F_EV-7631
renamed in place - unit | RDC_NB_1F_EAV7646 | EAV | Exp. Workstation N-1420 | room kept from its 1 part row(s); was RDC_NB_1F_EV-7646, and takes the place of RDC_NB_1F_EV-7646
renamed in place - unit | RDC_NB_1F_EAV7661 | EAV | Office 05 - 2 WKS- N-1401 | room kept from its 1 part row(s); was RDC_NB_1F_EV-7661, and takes the place of RDC_NB_1F_EV-7661
renamed in place - unit | RDC_NB_1F_EAV7663 | EAV | IDF N-1424 | room kept from its 1 part row(s); was RDC_NB_1F_EV-7663, and takes the place of RDC_NB_1F_EV-7663
renamed in place - unit | RDC_NB_1F_EAV7711 | EAV | Workstation N-1442 | room kept from its 1 part row(s); was RDC_NB_1F_EV-7711, and takes the place of RDC_NB_1F_EV-7711
renamed in place - unit | RDC_NB_1F_EAV7712 | EAV | Workstation N-1442 | room kept from its 1 part row(s); was RDC_NB_1F_EV-7712, and takes the place of RDC_NB_1F_EV-7712
renamed in place - unit | RDC_NB_1F_EAV7861 | EAV | Office 05 - 9 WKS N-1461 | room kept from its 1 part row(s); was RDC_NB_1F_EV-7861, and takes the place of RDC_NB_1F_EV-7861
renamed in place - unit | RDC_NB_1F_EAV7916 | EAV | Office 05 - 8 WKS N-1471 | room kept from its 1 part row(s); was RDC_NB_1F_EV-7916, and takes the place of RDC_NB_1F_EV-7916
renamed in place - unit | RDC_NB_1F_CAV7520_CEV7521 | CAV | Isotope N-1404B | room kept from its 1 part row(s); was RDC_NB_1F_CEV-7521, and takes the place of RDC_NB_1F_CEV-7521
renamed in place - unit | RDC_NB_1F_CAV7590_CEV7591 | CAV | HY Room N-1404J | room kept from its 1 part row(s); was RDC_NB_1F_CEV-7591, and takes the place of RDC_NB_1F_CEV-7591
renamed in place - unit | RDC_NB_1F_CAV7610_CEV7611 | CAV | TC1 N-1404L | room kept from its 1 part row(s); was RDC_NB_1F_CEV-7611, and takes the place of RDC_NB_1F_CEV-7611
renamed in place - unit | RDC_NB_1F_CAV7760_CEV7761 | CAV | A/L N-1450D | room kept from its 1 part row(s); was RDC_NB_1F_CEV-7761, and takes the place of RDC_NB_1F_CEV-7761
renamed in place - unit | RDC_NB_1F_CAV7790_CEV7791 | CAV | A/L N-1450G | room kept from its 1 part row(s); was RDC_NB_1F_CEV-7791, and takes the place of RDC_NB_1F_CEV-7791
renamed in place - unit | RDC_NB_2F_EAV4920 | EAV | IDF N-2104 | room kept from its 1 part row(s); was RDC_NB_2F_EV-4920, and takes the place of RDC_NB_2F_EV-4920
renamed in place - unit | RDC_NB_2F_EAV6981 | EAV | IDF N-2110 | room kept from its 1 part row(s); was RDC_NB_2F_EV-6981, and takes the place of RDC_NB_2F_EV-6981

## Read me
WHAT THIS FILE IS
Section | What it says
What this is | The controllable asset register for HQ, QNL, SSC and RDC as one flat table, with the agreed room name written into column D. 2577 rows.
Rows per building | HQ 761, QNL 551, SSC 124, RDC 1141
Room names rewritten | 1446 in total - HQ 755, QNL 537, SSC 122, RDC 32. Every one is listed on the Room name changes tab with the room it replaced and where the new name came from. The cell is shaded on the register so the change can be seen in place.
Where the names came from | HQ, QNL and SSC from Room_Names_4.xlsx column M, the name chosen after checking the drawings against the BMS screens and the delivered ontology. RDC from the BMS screen readings the client kept green in the review workbook - 32 of the 215 that were put forward; the other 183 were rejected and are not applied.
Rows left alone | 18 rows still carry no room name. No source settled the room for them and none has been invented; they are the rows to look at next.
Columns | The working file left two columns empty between the ones it used and two more without a header. Every column here carries data and a header, so ROOM PER BMS SCREEN is column H rather than column J. Column D is unchanged - it is the one the converter reads.
Building column | Column L names the building on every row. The HQ / QNL / SSC / RDC banner rows are gone: a banner row inside a filtered table sorts into the middle of the data. Filter column L instead.
RDC is smaller than it was | The RDC section went from 1,759 rows to 1,141. Air terminals and valves that the historian carries only as part of an assembly are parts, not controllable assets, and belong in the ontology under brick:hasPart. Every removal and rename is on the Removed from RDC tab.
Tags are not unique across buildings | 123 tags appear in two buildings at once - AHUB_0001, FCU0001 and so on. No tag repeats inside its own building, so column L tells them apart here, but only RDC prefixes its tags with the building code. The ontology needs that prefix on all four, or HQ and QNL assets collide the moment the sheets are merged.
Still open | VEV-5192a/b were renamed FEV5192A/B on the historian's word alone; 14 assemblies disagree with their parts on the room number; 47 RDC rows carry a number the historian has never heard of and were removed rather than kept on trust.
Not in this file | The four source equipment registers, the three room-name tabs and the Claude Log stay in the working workbook. They carry live formulas that a rewrite would break, and none of them is the deliverable.