## Claude Log
Turn # | Date | User Request | Action Taken | Details | Outcome
1 | 2026-08-10 | Provided full transcript from previous session (classifying HQ VAV/FCU tags as Included/Not Included in column D by room type across Ground Floor–Level 11). New session; selection at D1174. | Loaded prior context; set up Claude Log sheet; inspected the registry section around D1174. | Row 1170 = AHUB_0005; FCU numbering restarts at FCU0001 on row 1171 — this is a separate building/section where column D holds room descriptions (e.g. 'SPRINKLER AND WATER','B.M.S'), not Included/Not Included marks. AHUs (rows 4-28) still unmarked pending direction. | Awaiting user direction on next step (new floor, AHU handling, or final excluded-room verification).
3 | 2026-08-10 | Clarified: wants room names (rooms served by each equipment tag) filled for the HQ block, rows 3–763, in column E (keeping the Included/Not Included marks in column D). | Confirmed target column E via question; checked E is empty apart from a legend at E3/E4. Explained I cannot view the previous session's drawing images and my prior notes are not a clean per-row room map. | Room names must be exact; prior notes grouped multiple tags per room label. Requested the floor drawings be resent one at a time to fill column E accurately, floor by floor. | Awaiting user to resend the first HQ floor drawing to begin populating column E.
4 | 2026-08-10 | Said they will send the floor drawings later tonight. | Acknowledged; no workbook changes made. Confirmed the floor-by-floor workflow to populate column E with room names once drawings arrive. | No cells written to Controllable Asset Registry this turn. | On hold — awaiting HQ floor drawings from user (expected tonight).
5 | 2026-08-10 | Sent HQ Roof Top (Level 12) drawing; asked me to start filling room names in column E for that floor. | Wrote FCU room names to E155:E160 (FCU0126/0127 → 12.002 MCC Closet; FCU0128/0129 → 12.003 MCC Closet; FCU0130 → 12.004 MCC Closet; FCU0131 → roof plant/walkway near CSRR-0008). Verified by re-reading A155:E160. | Roof VAV/12/01-13 units are NOT in the tag list (all VAV0001-0607 already assigned to Ground-L11; HQ block ends row 763, QNL starts 764). AHU/12/01-10 (rows 4-12) left blank — parked per earlier decision and AHUs don't serve a single room. | Level 12 FCUs done. Flagged: SE 12.001 Electrical Closet sits beside 12.002 MCC Closet — could not confirm if one FCU serves 12.001 instead; FCU0131 has no room number on the drawing.
6 | 2026-08-11 | Sent the 3rd image pair — new: South Building L0 Section A1.3; old: North Building L0 Section A2.3. Asked me to continue the established workflow (map the new floor, extract standalone tags from the old floor). | Filled 3 blank FCU rows (FCU6987 row 2118, SB FCU0001 row 2159, SB FCU2001 row 2168). Appended 33 new rows (2365-2397): 5 A1.3 South Building AT tags, 24 A2.3 North Building AT tags, 4 A2.3 standalone EV valves. Flagged 7 uncertain rows yellow in C:D. | Duplicate avoidance: skipped AT-0006 (already row 2262 from B1.1) and all A2.3 numbers already embedded in existing VAV rows (5000/5002, 5001/5003, 5010/5011, 5015/5016, 5030/5031, 5040/5041, 5045/5046, 5395, 5400, 5405, 5410/5411, 6000/6001, 6010/6011, 6025/6026, 6240/6241, 6300, 6305, 6310, 6315/6316). Appended only valves with no VAV row: EV-5021, EV-5035, EV-6016, EV-6127. Equipment type = each tag's own prefix (AT/EV) per the standing rule. NB FCU5982/5991/5992/6985/6986 were already populated from an earlier session and matched A2.3, so left untouched. | 3rd pair complete and verified (rows 2118, 2159, 2168, 2365-2397 re-read; no gaps). Next append row = 2398. Flagged yellow: AT-0002, AT-0005, AT-2001, AT-5030, AT-5045, EV-5035, EV-6127. Open note: A2.3 right-hand area is labelled RECEPTION AREA N-0169, which duplicates the left-side EXP. OFFICE N-0169 label - no tag sits there so no row was written.
7 | 2026-08-11 | Sent the 4th image pair — new: South Building L0 Section A1.2; old: North Building L0 Section B2.1. Continue the established workflow. | Filled SB FCU2002-2005 (rows 2169-2172). Mapped 45 of 46 blank VAV rows for A1.2 (C/D 1738:1783 = VAV2002-VAV2047). Appended 112 rows (2398-2509): 45 A1.2 AT-20xx, 8 A1.2 standalone 0-series AT, 43 B2.1 AT, 15 B2.1 valves, FCU6997. Corrected AT-2001 (row 2369). Flagged 39 uncertain rows yellow, then fixed 14 misplaced flags. | A1.2 turned out to be a map-the-rooms floor: VAV2002-VAV2047 existed but were blank, and AT numbers correspond 1:1 to VAV numbers. There is no VAV2001 row and no VAV rows for the 0115-0124 series, so those 9 tags were appended only. VAV2005 (row 1741) left blank - AT-2005 does not appear on A1.2. Self-caught error: skipping AT-2005 in the append shifted my flag row offsets by one, so 7 flags landed on confident rows (AT-2010/2014/2017/2018/2026/2034/2036) and 7 uncertain rows were unflagged; cleared and re-applied correctly. AT-2001 moved from Vestibule S-0202 (per A1.3) to High-Density Room S-0206 (per A1.2, box sits inside the room outline) - still flagged. | 4th pair complete and verified (rows 2169-2172, 2369, 1738-1783, 2398-2510 re-read; no gaps; flag colours confirmed on C:D). Next append row = 2510. DEFERRED / NEEDS USER DECISION: (1) 21 blank NB VAV rows discovered - 1468 (VAV6295), 1473-1490 (VAV6320-6410), 1543-1544 (VAV7385/7390) - not filled because two existing rows conflict with the drawing, so a bulk same-number fill is unsafe. (2) Conflict A: registry row 1465 VAV6220 = Conf N-0331 and row 1463 VAV6205 = Emergency Elec. N-0333, but B2.1 shows AT-6220 at Emergency Elec. N-0333 and AT-6205 at Conference N-0331 (appears swapped). (3) Conflict B: registry row 1485 VAV6380 = Office N-0376, but B2.1 shows AT-6370 at Office N-0376 and AT-6380 at Workstation N-0378 (possible off-by-one, same pattern as the A2.2 fix).
8 | 2026-08-11 | Sent the 5th image pair — new: South Building L0 Section A1.1; old: North Building L0 Section B2.2. Continue the established workflow. | A1.1: filled VAV3001-3007 (rows 1784-1790) and FCU3001 (row 2173); appended 45 tags (2510-2554) = 32 AT-30xx plus 13 of the 2301-AT-01xx BACnet points. B2.2: appended 77 rows (2555-2631) = 51 AT (incl. the AT-7090/7105/7120 multi-node sensors), 8 standalone EV, 17 lab valves, FCU7993. Flagged 34 rows yellow across both. | B2.2's VAV rows mostly already existed with rooms, so the AT twins inherited the registry room (consistent with the A2.1/A2.2 approach) rather than my read of the drawing; the five places where the drawing disagrees were flagged instead of overwritten. Multi-node tags (AT-7090-N1/N2, AT-7105-N1/N2, AT-7120-N1..N9) have no VAV rows and were mapped from the drawing to N-0412/0412A, N-0415/0415A, N-0418/0418A and N-0430A..N-0430F - all flagged. Skipped every valve already embedded in a VAV row name (VEV7031, VEV7051, VEV7061, CEV7221, VEV7231, VEV7241A, VEV7251/7261/7271/7281/7291/7311/7321/7331/7341/7351/7361/7371, EV7126/7141/7186/7216/7495). FEV-7232 appears twice on the drawing - appended once and flagged. | 5th pair complete and verified (rows 1784-1790, 2173, 2510-2632 re-read; 122 appended rows with no gaps; flag colours spot-checked against tag names). Next append row = 2632. NEW CONFLICTS FLAGGED, NOT OVERWRITTEN: (1) FCU rows 2119/2120/2121 (FCU7981 = Stair 5 N-0STO5, FCU7982 and FCU7983 = Service Corridor N-0344) disagree with B2.2, which shows FCU-7993 at Stair 5, FCU-7981 at IDF N-0419 and FCU-7982 near Mech/FPC N-0434. (2) Row 2085 FCU7790 is tagged NB_1F but B2.2 (Level 0) shows FCU-7790 at Stair 6 N-0ST06. (3) Registry rows 1517/1518 give both VAV7145 and VAV7155 the same room (Office N-0427) - drawing suggests 7145 = N-0425. (4) Row 1519 VAV7165 = N-0428 vs drawing N-0429. (5) Row 1523 VAV7185 = Office N-0426 vs drawing Emer. Elec. Room N-0433, and row 1526 VAV7215 = Emergency Elec. N-0433 vs drawing Office N-0438. STILL OPEN from turn 7: the 21 blank NB VAV rows (1468, 1473-1490, 1543-1544) and the VAV6205/6220 and VAV6380 conflicts.
9 | 2026-08-11 | Sent the 6th image pair — new: South Building Level 1 Section B1.2; old: North Building Level 01 Section A2.1. First pair on Level 1 rather than Level 0. | B1.2: filled 45 blank VAV rows (C/D across 1595:1645) and FCU1503 (row 2132); appended 49 AT tags (2632-2680). A2.1 L01: appended 28 rows (2681-2708) = 8 AT twins, 19 valves, FCU2004. Flagged 5 rows yellow after correcting 2 that landed one row off. | Both drawings are Level 1, so writes went to the SB_1F and NB_1F blocks (not GF). SB VAV15xx occupies rows 1590-1645 but the series is not contiguous - VAV1504, 1535, 1537, 1538 and 1541 have no rows, so AT-1504/1535/1537 were appended only. NB_1F registry rooms for VAV4660-4745 matched my reading of the drawing exactly (N-1227 through N-1244), so those 8 AT twins needed no flags. NB_1F FCU4910/4915/4916/4917 were already correctly populated and match A2.1, so left untouched. Skipped valves already embedded in VAV row names (VEV4621, VEV4631, VEV4051/4061/4091, the VAV4070-4083 high-bay pairs) and VEV-4041 which was already appended at row 2253. | 6th pair complete and verified (rows 1590-1645, 2132, 2632-2709 re-read; 77 appended rows with no gaps; flag cells checked against tag names). Next append row = 2709. Flagged: AT-1504 (corridor position), AT-1533 and AT-1536 (sit between an electrical room and an office), AT-1537, CEV-4502, FCU2004. Still-blank SB L1 VAV rows with no tag on this drawing: 1590-1594 (VAV1501-1503, 1505, 1506), 1624-1625 (VAV1539/1540), 1627-1629 (VAV1543-1545), 1631 (VAV1547) - likely on the B1.1 half of Level 1. STILL OPEN: the 21 blank NB GF VAV rows (1468, 1473-1490, 1543-1544) and the registry conflicts at rows 1463/1465, 1485, 1517/1518, 1519, 1523/1526, 2085, 2119-2121.
10 | 2026-08-11 | Sent the 7th image pair — new: South Building Level 1 Section B1.1; old: North Building Level 1 Section A2.2. | B1.1: filled 34 blank VAV rows (1566-1594, 1624-1631) + FCU1501/1502 (2130-2131); appended 46 AT tags (2709-2754). A2.2: filled FCU5986 (2076) and VAV4650 (1842); appended 67 rows (2755-2821) = 42 AT, 7 EV, 18 lab valves. Flagged 12 rows yellow. | ERROR MADE AND CORRECTED: I wrote to FCU5983 (row 2073) and FCU5984 (row 2074) without reading them first - they already held 'Not Included / JC N-1139' and 'Included / Corridor N-1138'. I overwrote both with my own reading of the drawing (IDF N-1140 / JC N-1139), then restored the original values from the pre-write snapshot and flagged all three rows instead. Only FCU5986 was genuinely blank and kept a new value. Lesson: read FCU rows before writing, as several were populated in earlier sessions. Otherwise: NB_1F VAV5650-5940 rooms already matched the drawing closely, so those 38 AT twins inherited the registry room. Skipped valves embedded in VAV row names (VEV5601/5611/5622/5623/5631/5771/5781/5793/5795A/5801, EV5656/5716/5731/5736/5741/5761/5836). Unnumbered 'TAG 0.0' boxes on A2.2 could not be appended. | 7th pair complete and verified (rows 1566-1645, 1842, 2073-2076, 2130-2132, 2709-2822 re-read; 113 appended rows with no gaps; all 12 flag cells checked against tag names). Next append row = 2822. South Building Level 1 is now fully mapped except VAV0509 (row 1569) - no AT-0509 appears on either B1.1 or B1.2. Flagged: AT-0504, AT-0505, AT-0515, AT-0534, AT-0529, AT-5685 (registry calls N-1126 an Office, drawing calls it Corridor), AT-5840 and AT-5905 (registry gives both Office N-1163), EV-5686, VEV-5581 (label appears twice on drawing), VEV-5821, FCU1503 (row 2132 - B1.2 shows it at Stair 1, B1.1 shows it near FPC S-1108/UPS S-1107D), FCU5983/5984/5986. STILL OPEN: 21 blank NB GF VAV rows (1468, 1473-1490, 1543-1544) and conflicts at rows 1463/1465, 1485, 1517/1518, 1519, 1523/1526, 2085, 2119-2121.
11 | 2026-08-11 | Sent the 8th image pair — new: South Building Level 1 Section A1.3; old: North Building Level 1 Section A2.3. Both are sparse core/lobby sections. | A1.3: filled VAV2501 (row 1646, Lobby S-1201), FCU0501 (2127, Stair 2 S-1ST02) and FCU2501 (2133, Stair 3 S-1ST03); appended 2 AT tags (2822-2823 = AT-2501 Lobby S-1201, AT-2507 Female S-1204); corrected AT-0503 and AT-0505 rooms. A2.3: NO rows written - see details. Flagged 4 rows. | Pre-read all three fill targets before writing this turn (lesson from turn 10) - all were genuinely blank. AT-0503 changed from NCIR Office S-1115 to Women S-1106B and AT-0505 from UPS S-1107D to Emergency Elec. S-1107B: A1.3 is the section that actually contains the S-1105/S-1106B/S-1107B core, AT-0502 already matched Vestibule S-1105, and 0502/0503/0505 form a clean sequence onto those three rooms. A2.3 yielded nothing appendable: every sensor box on it is an unnumbered 'TAG' with no tag ID, so there is nothing to key a registry row on. Separately, FCU-2004 appears SIX times on A2.3 (Stair 3 N-1ST03, Stair 4 N-1ST04, Normal Elec. N-1310, IDF N-1311, Mech/FPC N-1353A, Reception N-1355) all reading 25.3 C - one BMS point bound to six graphic boxes, so no new rows could be derived; flagged row 2708 instead. | 8th pair complete and verified (rows 1646, 2127, 2133, 2708, 2711-2713, 2822-2824 re-read; flag fills confirmed). Next append row = 2824. OPEN QUESTION raised: moving AT-0503 to Women S-1106B leaves NCIR Office S-1115 with no sensor and VAV0509 (row 1569) still blank - the B1.1 tag I read as AT-0503 in that office may actually be AT-0509. Needs user confirmation before writing. Flagged: AT-0503, AT-0505, AT-2501, FCU2004. STILL OPEN from earlier turns: 21 blank NB GF VAV rows (1468, 1473-1490, 1543-1544) and conflicts at rows 1463/1465, 1485, 1517/1518, 1519, 1523/1526, 2085, 2119-2121, 1889, 1910/1923, 2132, 2073/2074.
12 | 2026-08-11 | Sent the 9th image pair — new: South Building Level 1 Section A1.2; old: North Building Level 1 Section B2.1. | A1.2: filled 50 blank VAV rows (C/D 1647:1696 = VAV2502-VAV2553) and 4 FCU rows (2134-2137); appended 51 AT tags (2824-2874). B2.1: appended 79 rows (2875-2953) = 40 AT, 8 EV, 31 lab valves. 130 appended rows total. Flagged 22 rows yellow. | Pre-read all 54 fill targets before writing - all confirmed blank, no overwrite. Verified fill alignment by spot-checking VAV2511=Office S-1212, VAV2536=Normal Elec. S-1251, VAV2553=Male Prayer S-1278 after the block write. B2.1 registry rooms matched the drawing throughout (VAV6650-6725 = N-1319 to N-1336, VAV6900-6970 = N-1357 to N-1371, VAV7865 = N-1461A), so those 34 AT twins inherited the registry room with no flags. VAV6630B/6631B were checked and already populated (Bio-Med Chem Lab 1 N-1316L) so were skipped, as were FCU6988/6989 which already read Service Corridor N-1337 and match the drawing. Corridor-run valves EV-6936/6961/6969 were assigned by the EV-pairs-with-VAV convention (Workstation N-1363/N-1368/N-1371) and flagged, since the dotted corridor they sit on carries no room number on this drawing. | 9th pair complete and verified (rows 1647-1696, 2080-2081, 2134-2137, 2824-2954 re-read; 130 appended rows with no gaps; all 22 flag cells checked against tag names). Next append row = 2954. Flagged: AT-2502/2503/2505/2506 and VAV2502/2503/2505/2506 (four lobby-band sensors with no room label of their own - all assigned Lobby S-1202), AT-2552/VAV2552 (label appears twice on A1.2), AT-4260 (4000-series tag on a South Building drawing, assigned Men S-1254), FCU2502-2505, AT-7500, EV-7501, EV-6936/6961/6969, CEV-6581, FEV-6731. STILL OPEN: 21 blank NB GF VAV rows (1468, 1473-1490, 1543-1544); conflicts at rows 1463/1465, 1485, 1517/1518, 1519, 1523/1526, 2085, 2119-2121, 1889, 1910/1923, 2132, 2073/2074; and the AT-0503/AT-0509 vs NCIR Office S-1115 question (row 1569 still blank).
13 | 2026-08-11 | Sent the 10th image pair — new: South Building Level 1 Section A1.1; old: North Building Level 1 Section B2.2. | A1.1: filled 20 blank VAV rows (C/D 1697:1717 = VAV3504-VAV3524, leaving VAV3519 blank) and FCU3501 (row 2138, Stair S-1ST104); appended 28 AT tags (2954-2981). B2.2: appended 58 rows (2982-3039) = 42 AT, 8 EV, 8 lab valves. 86 appended rows total. Flagged 15 rows yellow. | Pre-read all 22 fill targets and aborted-on-conflict guard was in the code; all were blank so nothing was overwritten. Verified alignment after the block write (VAV3504=Open Plan S-1229, VAV3514=Office S-1294, VAV3519 blank, VAV3524=Normal Elec. S-1238). VAV3519 left blank - no AT-3519 on the drawing. There are no VAV rows for AT-3501/3502/3503 or for the 2301-AT-02xx BACnet points, so those were appended only. B2.2 registry rooms matched the drawing throughout (VAV7620-7710 = N-1415 to N-1442, VAV7840-7960 = N-1458 to N-1480, and the N-1404x / N-1450x lab series), so all 42 AT twins inherited the registry room. RESOLVED an earlier flag: row 2085 FCU7790 was flagged in turn 8 because it carries the NB_1F tag but appeared on a Level 0 drawing - B2.2 (Level 1) now shows FCU-7790 at Stair 6 N-1ST06, matching the registry, so the NB_1F assignment looks correct and the Level 0 sighting was a graphic repeat. All seven NB_1F FCU rows (2085-2091) were already populated and match B2.2, so none were touched. | 10th pair complete and verified (rows 1697-1717, 2085-2091, 2138, 2954-3040 re-read; 86 appended rows with no gaps; all 15 flag cells checked against tag names). Next append row = 3040. Flagged: AT-3501 (sits under Lobby S-0294 which is a Level 0 room number on a Level 1 drawing), AT-3502, AT-3511/VAV3511, AT-3514/VAV3514 and AT-3520/VAV3520 (drawing carries TWO rooms labelled OFFICE S-1294 - one bottom-centre, one right of the stair), AT-0207/AT-0208, AT-7705 (registry room is just 'Expansion (Office)' with no number), EV-7663, EV-7712, CEV-7761, CEV-7791. NEW pre-existing issue spotted: rows 2034 and 2036 both give Flow Cyto N-1450C (VEV7751 and VEV7781) but the drawing puts VEV-7781 in iPS-TC N-1450F. STILL OPEN: 21 blank NB GF VAV rows (1468, 1473-1490, 1543-1544); conflicts at rows 1463/1465, 1485, 1517/1518, 1519, 1523/1526, 2119-2121, 1889, 1910/1923, 2132, 2073/2074, 2034/2036; and the AT-0503/AT-0509 vs NCIR Office S-1115 question (row 1569 still blank).
14 | 2026-08-11 | Sent the 11th and final image pair — South Building Level 2 and North Building Level 2. Both are plant / penthouse levels. | SB L2: filled all 20 blank FCU rows (C/D 2139:2158 = FCU0201-0208, FCU1201/1202, FCU2201-2210), all Not Included. NB L2: appended 10 rows (3040-3049) = 8 AT and 2 EV tags for the electrical and IDF rooms. NB L2 FCU rows (2092-2102) already populated and matching, so untouched. Flagged 6 rows yellow. | Pre-read the 20 SB targets with an abort-on-conflict guard; all blank. Verified alignment after the write (FCU0201=South Penthouse S-2101, FCU1201=IDF S-2102, FCU2204=Emerg. Elec. S-2105, FCU2210=IDF S-2107). AT-5930 and AT-5940 also exist as NB_1F rows with different rooms (Office N-1170 / Workstation N-1165); the NB_2F prefix keeps them distinct, and the registry's own VAV5930P (row 1929, Normal Elec. N-2105) and VAV5940P (row 1932, Emer. Elec. N-2106) confirm the Level 2 penthouse assignment is right. AHUs (8011-8026, 8512-8521), ERUs (8531-8541) and EFs (8011A, 8012A, 8041-8044, 8551-8554) were NOT written - continuing the decision made early in this project that AHU-class plant does not serve a single room. If those should be registered, they need a separate pass. | Final pair complete and verified (rows 2092-2102, 2139-2158, 3040-3050 re-read; 10 appended rows with no gaps; row 3050 empty; all 6 flag cells checked against tag names). Next append row = 3050. Flagged: FCU0204, FCU2201, FCU2202, FCU2203, FCU2205, FCU2210 - the penthouse FCUs sit in open plant space with no room boundary, so the split between South Penthouse S-2101 and the adjacent Emerg. Elec./IDF rooms is a best-guess. ALL 11 IMAGE PAIRS NOW PROCESSED. OUTSTANDING WORK FOR NEXT SESSION: (1) 21 blank NB GF VAV rows - 1468, 1473-1490, 1543-1544; (2) registry conflicts at rows 1463/1465, 1485, 1517/1518, 1519, 1523/1526, 2119-2121, 1889, 1910/1923, 2132, 2073/2074, 2034/2036; (3) AT-0503 vs AT-0509 and NCIR Office S-1115, row 1569 still blank; (4) SB L1 VAV3519 (row 1712) blank, no AT-3519 on any drawing; (5) unnumbered TAG boxes on NB A2.3, B2.1 and B2.2 that carry no tag ID; (6) AHU/ERU/EF plant equipment unregistered.
15 | 2026-08-11 | Re-sent all 18 drawings and asked me to tackle outstanding items 1 to 3: the blank North Building GF VAV rows, the 12 registry conflicts, and the AT-0503 / AT-0509 / NCIR Office S-1115 question. | Item 1: filled 19 blank NB GF VAV rows (1468, 1473-1484, 1486, 1488-1490, 1543-1544). Item 2: corrected 13 conflicting rows (1463, 1465, 1485, 1517, 1519, 1523, 1526, 1889, 1910, 2036, 2074, 2119, 2120) and synced 9 dependent appended rows (2565, 2567, 2569, 2572, 2711, 2762, 2775, 2797). Item 3: filled VAV0509 (row 1569). Bonus: filled FCU0502/FCU0503 (2128-2129) from B1.1. Cleared 21 resolved flags, set 11 remaining. Added 16 cell notes recording the evidence for each change. | Two swaps were confirmed by temperature, not just position: AT-6220 reads 18.1 C and AT-6205 reads 20.8 C, so VAV6220 is the Emergency Elec. N-0333 unit and VAV6205 the Conference N-0331 unit (rows 1463/1465 were reversed); AT-7185 reads 15.0 C, so VAV7185 is the Emer. Elec. Room N-0433 unit and VAV7215 serves Office N-0438 (rows 1523/1526). Three duplicate-room errors resolved: VAV7145 was sharing N-0427 with VAV7155 (now N-0425); VAV5840 was sharing N-1163 with VAV5905 - A2.2's bottom office band has exactly 17 tags for 17 rooms with AT-5840 left over sitting on the Corridor N-1150 run, so VAV5840 is the corridor unit; VEV7781 was sharing Flow Cyto N-1450C with VEV7751 (now iPS-TC N-1450F). Row 2132 FCU1503 needed no change at all - my turn-10 flag was a misreading of B1.1, which actually shows FCU-0502 and FCU-0503, and filling those two was the bonus. VAV0509 was resolved by elimination rather than read off a drawing, and is flagged with a note saying so. | Items 1-3 complete and verified (all 38 changed rows re-read; NB GF rows 1468-1490 and 1543-1544 now have zero blanks; the entire South Building Level 1 block 1566-1696 now has zero blanks; flag colours spot-checked against tag names). REMAINING OPEN: (a) row 2121 FCU7983 - reads Service Corridor N-0344 but does not appear on any drawing supplied, still flagged; (b) VAV6295 (1468), VAV6320 (1473), VAV6410 (1490) - filled but flagged, positions are best-guess; (c) VAV0509 (1569) and AT-0503 (2711) - flagged, need the BMS point list to settle whether the S-1115 sensor is AT-0503 or AT-0509; (d) FCU0502/0503 (2128-2129) flagged on position; (e) SB L1 VAV3519 (row 1712) still blank, no AT-3519 on any drawing; (f) unnumbered TAG boxes on NB A2.3, B2.1, B2.2 need IDs from the mechanical drawings or point list; (g) AHU / ERU / EF plant equipment still unregistered.
16 | 2026-08-12 | Switched to the QNL section (rows 766-1165). Sent IMG_9606.jpeg (Honeywell HMI, QNL Second Floor Zone-1 Part-1). New rules: use the Key Plan zone name + image name in parentheses when a room number is absent, mark those Included and highlight red; highlight uncertain rows yellow; only technical/executive rooms are Not Included. Follow-up: CAV/FEV/VEV tags found on drawings must be appended above the SSC section. | Filled C/D for VAV_2F_S12_001-029, _097 (rows 975-1004), VAV_2F_S13_004 (row 1008) and FCU_2F_005 (row 850). Applied red fill to the 20 zone-named rows and yellow to the 2 uncertain/technical rows. Located the QNL/SSC boundary for future CAV/FEV/VEV inserts. | Rows 975-994 (VAV_2F_S12_001-020) sit in the unlabelled open library floor, so all 20 got 'Second Floor Zone-1 Part-1 (IMG_9606.jpeg)' per the new Key Plan rule (Current View = Part-1), Included, red fill. Named rooms mapped left-to-right along the top office band: 021 Breakout Space, 022 Circulation Office, 023 + 024 Office Space Col., 025 Transl. Spc & ED Publications Spc.; group study band: 026 Room 5, 029 Room 6, 027 Room 7, 097 Room 8; S13_004 Open Office. FCU_2F_005 = MDF Room, Not Included as a technical room, flagged yellow. VAV_2F_S12_028 sits between the two Office Space Col. cells and Transl. Spc with no clear boundary - given a dual name and flagged yellow. QNL section confirmed as rows 766-1165 with the SSC header at row 1166; QNL currently holds only AHUB, FCU and VAV prefixes (no CAV/FEV/VEV rows exist yet). | Verified by re-reading A970:D1010 and C850:D850 - values and fill colours confirmed. NOT WRITTEN this turn (right edge of the photo is cut off, rooms not fully readable): VAV_2F_S13_005/006/009/011/012/013 and VAV_2F_S10_001/002/004/005 - awaiting a clearer or adjacent view. No CAV/FEV/VEV tags appear on IMG_9606, so no rows were appended; when they do appear they will be inserted at row 1166, immediately above the SSC header.
17 | 2026-08-12 | Second image: IMG_9608.jpeg - QNL Honeywell HMI, 'Second Floor Zone-2-P1' (Key Plan: Second Level, Current View = Part-1). Fill in the QNL section using the same rules as the first image. | Filled C/D for 33 rows: VAV_2F_S10_003 (971), _006 (974); VAV_2F_S13_001/002/003/008/010/015/016 (1005-1020); VAV_2F_S14_001-014 (1021-1034) and _016-020 (1036-1040); VAV_2F_S15_001-005 (1042-1046). Red fill on the 21 zone-named rows, yellow on 2 rows needing review. | Named rooms read left-to-right off the executive/admin band: S13_010 + S13_015 = Ad. Admin & Planning, S13_008 = Office Coord., S13_001 + S13_002 = Lib. Director's Room, S13_003 = Service & Lounge, S13_016 = VIP Waiting, S15_001-004 = VIP Room, S15_005 = VIP Meeting. Applied the executive-room rule: Lib. Director's Room, VIP Room, VIP Waiting and VIP Meeting all set to Not Included (7 rows). Ad. Admin & Planning set to Included but flagged yellow - it sits inside the same executive suite band and may be an executive office rather than a staff office, so it needs your call. The whole right-hand grid (S14_001-014, _016-020) and the two S10 units on the left have no room label on the drawing, so all 21 got 'Second Floor Zone-2 Part-1 (IMG_9608.jpeg)' per the Key Plan rule, Included, red fill. | Verified by re-reading A971:D1046 - tags, values and fill colours all confirmed against the intended mapping. NOT WRITTEN (cropped off the right edge of the photo): VAV_2F_S14_015 (row 1035) and VAV_2F_S14_021 (row 1041) - their tags are cut off mid-label. Also still outstanding from image 1: VAV_2F_S13_005/006/009/011/012/013 and VAV_2F_S10_001/002/004/005. No CAV, FEV or VEV tags on this drawing either, so no rows appended above the SSC header (row 1166).
18 | 2026-08-12 | Third image: IMG_9610.jpeg - QNL Honeywell HMI, 'Second Floor Zone-3-P1' (Key Plan: Second Level, Current View = Part-1). Fill in the QNL section using the same rules. | Filled C/D for 2 rows: FCU_2F_043 (row 860) and FCU_2F_044 (row 861), both set to Included / 'Display Area'. No highlight applied. | This view is almost empty - only two FCU tags and a single blue room label, 'Display Area', are present. Both FCUs sit inside the same wall-bounded open hall as that label (between the vertical wall runs at either side), so the real room name was used rather than the Key Plan zone fallback, meaning no red highlight was needed. Display Area is a public library space, so neither the technical-room nor the executive-room exclusion applies and both are Included. Row positions confirmed by reading A846:A880: the FCU_2F block runs 001-005 at rows 846-850 then jumps to 034-062 at rows 851-879, which puts 043 at 860 and 044 at 861. | Verified by re-reading A860:D861 as rendered text - both rows show the correct tag, Included, and Display Area. Judgement call flagged to the user in chat rather than with a yellow fill: the 'Display Area' label sits a fair distance from the two tags in a sparse drawing, so it is worth a glance on review. Outstanding backlog unchanged: VAV_2F_S14_015 (1035), VAV_2F_S14_021 (1041), VAV_2F_S13_005/006/009/011/012/013, VAV_2F_S10_001/002/004/005. Still no CAV, FEV or VEV tags seen on any drawing so far, so nothing appended above the SSC header at row 1166.
19 | 2026-08-12 | Fourth image: IMG_9611.jpeg - QNL Honeywell HMI, 'Second Floor Zone-3-P2' (Key Plan: Second Level, Zn-3, Current View = Part-2). Fill the QNL section using the established rules. | Filled C/D for 18 FCU rows: FCU_2F_034-040 (851-857), _045-055 (862-872). All set Included. Yellow flag on 2 rows (866, 869). No red/zone-named rows needed - every device on this view sits in a labelled room. | Auditorium is the large room top-centre and holds 7 units: FCU_2F_034-040 (rows 851-857). The middle block carries two 'Group Study Room' labels (one above, one below) with FCU_2F_045, _046, _047 inside - all three named Group Study Room since both labels read identically. The right block is split into a rest-room column and an individual-study column, top and bottom: FCU_2F_048 = Rest Room (Men), _051 = Rest Room (Women), _050 and _053 = Indiv. Study Room. Bottom of view: FCU_2F_054 and _055 = Lounge Area. Rest rooms, lounge, auditorium and study rooms are all public library spaces - none are technical or executive - so nothing on this drawing is Not Included. | Verified by re-reading A851:D872 - tags, values and fill colours all confirmed. FLAGGED YELLOW for review: FCU_2F_049 (row 866) and FCU_2F_052 (row 869) sit in a middle column between the rest rooms and the individual study rooms with no label directly above them, so each was given a dual name pending your decision. NOT WRITTEN: FCU_2F_041 (858) and _042 (859) do not appear on this view. Backlog still open: VAV_2F_S14_015 (1035), _021 (1041), VAV_2F_S13_005/006/009/011/012/013, VAV_2F_S10_001/002/004/005. Still no CAV, FEV or VEV tags on any drawing so far - nothing inserted above the SSC header (row 1166).
20 | 2026-08-12 | Fifth image: IMG_9621.jpeg - QNL Honeywell HMI, 'Terrace Floor Zone-1-P1' (Key Plan: Terrace Level, Current View = Part-1). First terrace-level drawing; only 4 tags on the view. | Filled C/D for 4 FCU rows, all Included: FCU_2F_060/061/062 (rows 877-879) = Recreational Area; FCU_2F_003 (row 848) = 'Book Shelf (IMG_9621.jpeg)' flagged yellow. No red rows - every sensor had a nearby drawing label. | FCU_2F_060, _061 and _062 sit clearly inside the walled box carrying the 'Recreational Area' label, so those three were straightforward. FCU_2F_003 is the judgement call: it sits at the left end of the long open strip along the top of the terrace that carries three repeated 'Book Shelf' labels. That is a furniture/zone descriptor rather than a discrete room, and because the label repeats three times it does not uniquely identify a space - so it was named 'Book Shelf (IMG_9621.jpeg)' and flagged yellow rather than red, since a real drawing label does exist and the Key Plan fallback was not strictly triggered. Note the terrace level still uses the FCU_2F_ tag prefix, so terrace assets live inside the same FCU_2F block (rows 846-879) as the second floor - no separate terrace range. | Verified by re-reading A877:D879 and A848:D848 as rendered text - tags, values and Included flags all confirmed. Open question raised with the user: whether 'Book Shelf' should stand as the room name or be replaced with the Terrace Zone-1 Part-1 Key Plan name. Backlog still owed: VAV_2F_S14_015 (1035), _021 (1041), VAV_2F_S13_005/006/009/011/012/013 (1009/1010/1013/1015/1016/1017), VAV_2F_S10_001/002/004/005 (969/970/972/973), plus FCU_2F_041 (858) and _042 (859). Also still pending user decision: middle-column rows 866 and 869 from IMG_9611, and the Ad. Admin & Planning rows 1014/1019 from IMG_9608. Still zero CAV/FEV/VEV on any drawing so far.
21 | 2026-08-12 | Sixth image: IMG_9622.jpeg - QNL Honeywell HMI, 'Terrace Floor Zone-2-P1' (Key Plan: Terrace Level, Current View = Part-1). Fill in the QNL section using the established rules. | Filled C/D for 5 rows, all Included: FCU_2F_056-059 (rows 873-876) = Internal Terrace; FCU_2F_004 (row 849) = zone name, red fill. Confirmed tags in column A before writing. | The four sensors FCU_2F_056-059 sit inside the walled box carrying the blue 'Internal Terrace' label, so that room name was used directly - no highlight needed. FCU_2F_004 sits alone in the upper open band at the top right of the drawing with no room or area label anywhere near it, so the Key Plan fallback applied: 'Terrace Floor Zone-2 Part-1 (IMG_9622.jpeg)', Included, red fill. Neither the technical-room nor executive-room exclusion applies to anything on this view. Row positions confirmed against the FCU_2F block: 034=851 so 056=873 ... 059=876, and 004=849. | Verified by re-reading A849:D849 and A873:D876 - tags, values and fill colours all confirmed. Open question still unanswered from the previous turn: how to treat terrace open-plan furniture labels (Book Shelf, Carrels, Media Station, Computer Station, Open Seating) - use the label as-is or fall back to the Key Plan zone name. Row 848 remains yellow pending that decision. Backlog owed: FCU_2F_041 (858), _042 (859), VAV_2F_S14_015 (1035), _021 (1041), VAV_2F_S13_005/006/009/011/012/013, VAV_2F_S10_001/002/004/005. Pending user decisions: rows 866/869 middle column, rows 1014/1019 Ad. Admin & Planning. Still zero CAV/FEV/VEV on any drawing, so nothing appended above the SSC header (row 1166).
22 | 2026-08-12 | Seventh image: IMG_9624.jpeg - QNL Honeywell HMI, 'Terrace Floor Zone-3-P1' (Key Plan: Terrace Level, Zn-3, Current View = Part-1). Fill in the QNL section. | Filled C/D for a single row: FCU_1F_001 (row 781) = Included / 'Scholarly Journals (IMG_9624.jpeg)', yellow flagged pending the terrace naming decision. | This view has only one tag on the whole drawing. Note the prefix is FCU-1F-001, not FCU-2F - the terrace level draws on both the FCU_1F and FCU_2F blocks, so row lookup was confirmed by reading A780:B782 (FCU_1F_001 = row 781, immediately after AHUB015 at row 780). The only nearby label is 'Scholarly Journals', which is a collection/furniture-area descriptor of the same kind as 'Book Shelf' on row 848 - not a discrete room. Handled it identically to row 848: used the drawing label with the image name appended and flagged yellow, so both rows can be flipped together once the user decides whether terrace furniture labels count as room names or should fall back to the Key Plan zone name. Included, as it is neither a technical nor an executive room. | Verified by re-reading A781:D781 as rendered text - tag FCU_1F_001, Included, 'Scholarly Journals (IMG_9624.jpeg)' confirmed. No other tags on this view. Backlog still owed: FCU_2F_041 (858), _042 (859), VAV_2F_S14_015 (1035), _021 (1041), VAV_2F_S13_005/006/009/011/012/013, VAV_2F_S10_001/002/004/005. Awaiting user decisions on: terrace furniture-label policy (rows 848 and 781), rows 866/869 middle column, rows 1014/1019 Ad. Admin & Planning. Still zero CAV, FEV or VEV tags across all seven drawings, so nothing appended above the SSC header (row 1166).
23 | 2026-08-12 | Ninth image: IMG_9627.jpeg - QNL Honeywell HMI, 'Terrace Floor Zone-4-P2' (Key Plan: Terrace Level, Current View = Part-2). Fill in the QNL section. | Filled C/D for 2 rows: FCU_2F_001 (846) and FCU_2F_002 (847), both Included with the Key Plan zone name and red fill. | Only two tags on this view: FCU-2F-001 (39.9 C) and FCU-2F-002 (38.7 C), both sitting in the unlabelled triangular open corner at the left of the plan, inside the outer wall. The surrounding text on this floor is all repeated open-plan furniture descriptors (Carrels, Media Station, Computer Station, Open Seating) rather than room names, and none of them sits on top of either unit - the nearest, Carrels, falls between the two. Because those descriptors repeat many times across the terrace and cannot uniquely identify a location, both rows got 'Terrace Floor Zone-4 Part-2 (IMG_9627.jpeg)' per the Key Plan rule, Included, red fill. Note this differs from rows 848 and 781, where the unit did sit inside a single labelled strip so the drawing label was kept and flagged yellow instead - both approaches remain open pending the user's terrace naming decision. | Verified by re-reading A846:D847 as rendered text - tags confirmed as FCU_2F_001 and FCU_2F_002, values and red fill correct. Backlog still owed: FCU_2F_041 (858), _042 (859), VAV_2F_S14_015 (1035), _021 (1041), VAV_2F_S13_005/006/009/011/012/013 (1009/1010/1013/1015/1016/1017), VAV_2F_S10_001/002/004/005 (969/970/972/973). Awaiting user decisions on: terrace furniture-label policy (rows 781, 848 and the approach used here), rows 866/869 middle column, rows 1014/1019 Ad. Admin & Planning. No CAV, FEV or VEV tags on this drawing - none seen on any of the eight drawings so far, so nothing appended above the SSC header (row 1166).
24 | 2026-08-12 | IMG_9587.jpeg - QNL Honeywell HMI, 'Basement Zone-1-P1' (Key Plan: Basement Level, Current View = Part-1). Largest drawing so far and the FIRST one containing CAV tags, which per the earlier instruction must be added above the SSC section. | Filled C/D for 49 existing rows and INSERTED 2 new CAV rows. Existing: VAV_B_S11_001-046 (rows 1071-1116, minus _023 not on view), VAV_B_S13_001/002/006 (1117/1118/1122), FCU_B_002 (881). New: inserted rows 1166-1167 for CAV_B_S13_007 and CAV_B_S13_020 - the SSC section header consequently moved from row 1166 to row 1168. | Basement row map confirmed by reading A1047:A1166: VAV_B_S10_001-024 = 1047-1070, VAV_B_S11_001-046 = 1071-1116, VAV_B_S13_001-008 = 1117-1124, VAV_B_S14 = 1125+, VAV_B_S15_013 = 1165. Small labelled offices mapped one-to-one: 024 Kitchen, 025 Storage, 026 Finance Cooridinator & Business Support OFCR. (yellow leader arrow), 028 Analog Resources, 029 Digital Resources, 030+031 Budget & Payment, 032+033 Ad Collection, 034 Engineering, 035 Arabic Sudies, 037 Art & Humanities, 038 Procurement SPC, 039 Business Computing, 040 Social Sciences, 041 Literature Language, 042 Coordinator, 043-046 Receiving Area, 022 Corridor 1, S13_001+002 Meeting Room. VAV_B_S11_036 sits alone at the top of the drawing but has a yellow leader line running down and left to the 'Licensing Expert' label, so it was named from the leader rather than from proximity. Spellings kept exactly as drawn ('Cooridinator', 'Arabic Sudies'). Both CAVs set Not Included as technical rooms (MV Room-01 / MV Room-02) and flagged yellow. Row 1091 (VAV_B_S11_021) has no room label so it took the Key Plan name, Included, red. | Verified by re-reading A1071:D1073, A1090:D1092, A1094:D1098, A1106:D1107, A1116:D1118, A1122:D1122, A881:D881 and A1163:D1170 - tags, values and the row insert all confirmed; SSC header now at 1168. YELLOW flagged for user review (7 rows + 2 CAV): 1071/1072/1081/1082 Break Out Area - the top open area carries TWO labels ('Break Out Area' and 'Tech, Services & Collections Office') with no dividing wall between them, so the split point between VAV _002/_003 and _012/_013 is a judgement call; 1097 (VAV_B_S11_027) sits between the Finance and Budget & Payment cells with no label above it; 1122 + 881 'Freeze Area' - unclear whether this counts as a technical/plant space (currently Included); 1166/1167 CAVs - inferred from proximity to the MV rooms. NOT WRITTEN: VAV_B_S11_023 (row 1093) is not shown on this view. Non-HVAC tags on the drawing (EF-B-09, GCP-01, SMDB, DX-B-xx, MV Panel-1/2/3, CPNL-0006, LCP-Z1, FWS/FWP-01) are out of scope. Future CAV/FEV/VEV inserts now go at row 1168.
25 | 2026-08-12 | IMG_9588.jpeg - QNL Honeywell HMI, 'Basement Zone-1-P2' (Lower Level Floor Plan Zone-1 Part-2). Heavily plant-orientated view containing 15 new CAV tags plus 18 FCU_B tags and the one VAV that was missing from the previous drawing. | Filled C/D for 19 existing rows and INSERTED 15 new CAV rows. Existing: FCU_B_003/006/007/008/009/011/012/013/014/027/028/031-037 (rows 882-916) and VAV_B_S11_023 (row 1093). New: inserted rows 1168-1182 and rewrote the whole CAV block A1166:D1182 in sorted tag order - the SSC section header moved from row 1168 to row 1183. | FCU_B row map confirmed (FCU_B_00N = row 879+N, 001=880 ... 038=917). Plant/technical rooms set Not Included per the rule: Plant Room 1 (FCU_B_011/012 + CAV_B_S12_001/002/003), Plant Room 2 (FCU_B_013/014 + CAV_B_S13_010/011), Sprinklers Pumps (FCU_B_007 + CAV_B_S13_021), Server Room (CAV_B_S13_013/014/015), Fire Command (FCU_B_006 + CAV_B_S13_006/012), GAS Suppression (CAV_B_S13_008), IDF (FCU_B_003). Library spaces set Included: Sorting Shelving Room (FCU_B_027/028), Compact Shelving Main Collection (FCU_B_031), Shell Space-Special Collection (FCU_B_032/033/034/035), IT Office (FCU_B_036 - treated as a staff office, not a plant room), Corridor 2 (CAV_B_S13_001/002). FCU_B_003 was named from a yellow leader line running up to the IDF label rather than by proximity. The CAV block was rebuilt as a single sorted range so the two CAVs added last turn (S13_007, S13_020) now sit in tag order with the new ones; their names were kept and re-stamped with their source image (IMG_9587). | Verified by re-reading A882:D888, A890:D893, A906:D916, A1093:D1093 and A1166:D1183 - all 36 rows, the 15-row insert and the new SSC header position at 1183 confirmed. YELLOW flagged for review (10 rows): 882 IDF and 916 Corridor (leader/proximity calls); 885 + 1172 + 1177 Fire Command - three units sit in the top strip shared by Fire Command, GAS Suppression and UPS Battery Room with no clear wall, so the split is inferred partly from leader lines; 1174 GAS Suppression (same strip); 1178 + 1179 Server Room - these two sit left of the Server Room label near MF-B-02 and may belong to a separate space; 1171 Corridor - sits between People Mover, Shell Space and the Corridor label; 1093 VAV_B_S11_023 - sits exactly on the Plant Room 1 / Plant Room 2 boundary, though both are technical so Not Included holds either way. RED (2 rows): 887 + 888 (FCU_B_008/009) are at the cropped right edge with no room label, so they took the Key Plan name. Out of scope on this drawing: AHU-B-xx, EF-B-xx, DX-B-xx, PDP, PCP, MF-B, CPNL, GWSHL, CC-B, ATS Panel, SWP, FP/JP. Future CAV/FEV/VEV inserts now go at row 1183.
26 | 2026-08-12 | IMG_9589.jpeg - QNL Honeywell HMI, 'Basement Zone-2-P1' (Lower Level Floor Plan Zone-2 Part-1). Back-of-house / bindery view with 28 VAV_B_S14 tags and 5 new CAV tags. | Filled C/D for 28 existing VAV rows (VAV_B_S14_001-016 = rows 1125-1140, _040-051 = rows 1141-1152) and INSERTED 5 new CAV rows at 1183-1187 (CAV_B_S14_001, _006, _007, CAV_B_S15_002, _003). SSC section header moved from row 1183 to row 1188. Everything on this drawing is Included - no technical or executive rooms carry a controllable tag here. | Clean one-to-one mappings: S14_001 Office, _002 Office DG., _003 Office AD. For LIT, _004/_005/_006 Digitization Room, _007/_008 Shell Space, _009 Dry Store, _015 Reception & Lounge. CAVs: S14_001 Loading Area, S14_006 Referigerate Store, S14_007 BOH Kitchen, S15_002 Corridor 5 (label sits directly beside it). Kept the drawing's own spelling 'Referigerate Store'. The Q-Tel Room, Telecom Room and MEP Kitchen are technical spaces but carry no VAV/CAV/FCU tag on this view, so nothing was set to Not Included. Out of scope: EF-B-xx, DX-B-17/18/19, SWP-05/06, CCU-B-01 to 04, LCP-Z2, DRS & DTS, Calorifier. | Verified by re-reading A1125:D1152 and A1180:D1190 - all 33 rows, the 5-row insert and the new SSC header position at 1188 confirmed. IMPORTANT DISCREPANCY logged as a cell note on D1129: the HMI label between VAV-B-S14-004 and VAV-B-S14-006 reads 'VAV-B-S11-005', but VAV_B_S11_005 (row 1075) was already assigned to Tech, Services & Collections Office from IMG_9587.jpeg. Recorded positionally as VAV_B_S14_005 = Digitization Room and flagged yellow - user to confirm the correct tag. OTHER YELLOW FLAGS (9 rows total): 1136/1137/1144/1145/1150/1151 - 'Fine Binding' and 'Binding & Preservation Space' label one large open area with no dividing wall, so the left/right split of the 16 units in that room is a judgement call and these six sit nearest the split point; 1140 (S14_016) sits below the Reception & Lounge cell near the DRS & DTS panel; 1141 (S14_040) is drawn outside the plan at the bottom and was named from its yellow leader line running up into the BOH Kitchen; 1187 (CAV_B_S15_003) sits well above the Corridor 5 label and may belong to the bindery instead.
27 | 2026-08-12 | IMG_9591.jpeg - QNL Honeywell HMI, 'Basement Zone-3-P1' (Lower Level Floor Plan Zone-3 Part-1). Heritage/researcher entrance sequence. The whole plan is drawn on a 45-degree diagonal, which makes label-to-device proximity much less reliable than on the orthogonal views. | Filled C/D for 16 existing rows, all Included: VAV_B_S10_020-023 (rows 1066-1069), VAV_B_S15_001-009 (rows 1153-1161), VAV_B_S15_013 (row 1165), FCU_B_029 (row 908), FCU_B_038 (row 917). No CAV, FEV or VEV tags on this drawing, so no rows were inserted and the SSC header stays at row 1188. | Confident mappings: S10_020/021 Reserchers Reading Area, S10_023 Entry, S15_008 Vestibule, S15_013 Reserchers & Doc. RCRDS MGMT (yellow leader lines link the tag and that label across the drawing), FCU_B_029 Heritage Collection Entrance, FCU_B_038 Pantry (named from its yellow leader, since the tag itself sits outside the room outline). Drawing spellings preserved exactly: 'Reserchers Reading Area', 'Loby and Security', 'Reserchers & Doc. RCRDS MGMT'. Nothing was set to Not Included - the only technical space on the view is the IDF Room and it carries no controllable tag. FCU_B_038 displays '??????' rather than a temperature, recorded as a cell note on D917. | Verified by re-reading A908:D908, A917:D917, A1066:D1069, A1153:D1161 and A1165:D1165 - all values and notes confirmed. YELLOW flagged (9 rows): 1153/1157/1158 Prof. Librarian and 1154/1155/1156/1159 Loby and Security - these seven S15 units sit in the diagonal entrance band where Entry, Prof. Librarian, Loby and Security, Vestibule and Pantry are packed close together and the 45-degree rotation makes nearest-label assignment unreliable, so the split between Prof. Librarian and Loby and Security needs user confirmation; 1068 (S10_022) sits below the Reserchers Reading Area label and may belong to the adjacent space; 1161 (S15_009) Asst. Head is flagged for the INCLUSION question rather than the name - it is a management office and may qualify as an executive room, currently left Included, cell note added to D1161. NOT WRITTEN: VAV_B_S15_010/011/012 (rows 1162-1164) do not appear on this view.
28 | 2026-08-12 | IMG_9592.jpeg - QNL Honeywell HMI, 'Basement Zone-3-P2' (Lower Level Floor Plan Zone-3 Part-2). Sparse view: mostly plant equipment plus the executive suite at the top. Contains the three S15 VAVs that were left blank from the previous drawing. | Filled C/D for 4 existing rows: VAV_B_S15_010/011/012 (rows 1162-1164) and FCU_B_001 (row 880). No CAV, FEV or VEV tags on this drawing, so no rows inserted and the SSC header stays at row 1188. The VAV_B_S15 block (rows 1153-1165) is now complete. | Applied the executive-room rule: VAV_B_S15_010 = Director Head and VAV_B_S15_012 = VIP Majlis, both Not Included, consistent with how Lib. Director's Room / VIP Room / VIP Meeting were treated on the second floor. Room names sit just below-right of each sensor's T circle on this drawing, which is what drove the assignment. Note the 'Asst. Head' label appears on BOTH this view and Zone-3-P1 - it is the same room seen across the Part-1 / Part-2 boundary, already recorded against VAV_B_S15_009 (row 1161), so it was not duplicated here. Out of scope on this drawing: UPS Panel, EF-B-12, FWP-05/06, PHX-B-01 to 04, CHWP-1/2/3/4, PU-B-01, CPNL-0005, LCP-Z3. Plant Room 4, Ventilation, Air Shaft, Maintanance and Corridor are labelled but carry no controllable tag, so nothing else was set to Not Included. | Verified by re-reading A880:D880 and A1161:D1165 - values, fills and notes confirmed. YELLOW (1 row): 1163 (VAV_B_S15_011) sits between the Director Head and VIP Majlis labels with no clear wall; assigned to VIP Majlis, though both candidates are executive so Not Included holds either way. RED (1 row): 880 (FCU_B_001) is drawn outside the plan outline on the left with NO leader line to any room, so it took the Key Plan name and was auto-Included per the agreed rule - however its two nearest labels are 'IDF Rooom' and 'VIP Restroom', and BOTH of those would make it Not Included (technical / executive). This is the one row on this drawing where the standing rule and the likely reality disagree, so a cell note was added to D880 asking the user to confirm. Two 'VIP Restroom' labels with upward yellow leader arrows exist on the view but neither points at a controllable tag.
29 | 2026-08-12 | IMG_9593.jpeg - QNL Honeywell HMI, 'Basement Zone-4-P1' (Lower Level Floor Plan Zone-4 Part-1). Almost entirely empty view - the bulk of it is the Compact Shelving Main Collection stacks and the Vault / Heritage Collection block, none of which carry controllable tags. | Filled C/D for 1 existing row: FCU_B_005 (row 884) set to Not Included / 'HL Plant Room'. No CAV, FEV or VEV tags on this drawing, so no rows inserted and the SSC header stays at row 1188. | FCU_B_005 was named from its yellow leader line rather than by proximity: the 'HL Plant Room' label sits below-left of the tag and runs a leader right then up into the small room at the apex of the diagonal wall, and the CCU-1,2,3,4,5,6 block leaders into the same space. HL Plant Room is a plant/technical room, so the technical-room rule applies and it was set Not Included. No highlight was needed - the leader makes the assignment unambiguous. Labelled but untagged on this view: Compact Shelving Main Collection (x2), Vault, Heritage Collection. Out of scope: CCU-1,2,3,4,5,6. | Verified by re-reading A884:D884 as rendered text - FCU_B_005 / FCU / Not Included / HL Plant Room confirmed. No yellow or red flags raised on this drawing. Outstanding backlog unchanged: FCU_2F_041 (858), FCU_2F_042 (859), VAV_2F_S14_015 (1035), VAV_2F_S14_021 (1041), VAV_2F_S13_005/006/009/011/012/013 (1009/1010/1013/1015/1016/1017), VAV_2F_S10_001/002/004/005 (969/970/972/973). Pending user decisions carried forward: terrace furniture-label policy (rows 781, 848 vs 846/847), rows 866/869 middle column, rows 1014/1019 Ad. Admin & Planning, row 1129 VAV-B-S11-005 vs S14-005 tag conflict, Fine Binding / Binding & Preservation split, row 1161 Asst. Head executive question, row 880 FCU_B_001.
30 | 2026-08-12 | IMG_9594.jpeg - QNL Honeywell HMI, 'Basement Zone-4-P2' (Lower Level Floor Plan Zone-4 Part-2). Plant-heavy view: Plant Room 4, PH Plant, Pump Room, FM Storage and the misting/storage cluster off Corridor 6. | Filled C/D for 11 existing FCU rows: FCU_B_004 (883), _018/_019/_020/_021 (897-900), _022/_023 (901-902), _024 (903), _025/_026 (904-905), _030 (909). Seven set Not Included as technical rooms, four Included. No CAV, FEV or VEV tags on this drawing, so no rows inserted and the SSC header stays at row 1188. | Technical rooms set Not Included per the rule: Plant Room 4 (FCU_B_018/019/020/021 - the room also holds AHU-B-01/05/06/07/08, EF-B-03, GWSHL-B-05, LCP-Z4, CPNL-0004), PH Plant (FCU_B_024, room holds PPSP-01 to 06), Pump Room (FCU_B_030), Misting System (FCU_B_026). Included: FM Storage (FCU_B_004/022/023) and Storage (FCU_B_025) - storage areas are neither technical plant nor executive, so they stay in scope. FCU_B_025 and _026 are drawn BELOW the plan outline and were placed using their yellow leader lines, which run up into the two small rooms off Corridor 6 labelled 'Storage' and 'Misting System'. Out of scope on this drawing: AHU-B-xx, EF-B-03, GWSHL-B-04/05, PDS/PDP-03/05, PPSP-01 to 06, MBP-01, LCP-Z4, CPNL-0004, CC-B-10/11, SWP-11/12, ST-12. | Verified by re-reading A883:D883 and A897:D909 as rendered text - all 11 rows confirmed. YELLOW flagged (3 rows): 883 (FCU_B_004) sits OUTSIDE the FM Storage wall on the left with no leader line, assigned to FM Storage as the nearest room but unconfirmed; 904 (FCU_B_025) and 905 (FCU_B_026) - both are drawn outside the plan and their leaders terminate very close together at the Storage / Misting System pair, with the 'Corridor 6' label sitting directly between the two leader lines, so the Storage vs Misting System vs Corridor 6 split is a judgement call. This matters for classification, not just naming: FCU_B_025 was left Included as Storage while FCU_B_026 was set Not Included as Misting System, so if the pairing is reversed the inclusion flips too. FCU_B block status: 34 of 38 rows now filled; still blank are FCU_B_010 (889), _015 (894), _016 (895) and _017 (896), none of which have appeared on any drawing yet.
31 | 2026-08-12 | IMG_9596.jpeg - QNL Honeywell HMI, 'First Floor Zone-1-P1' (First Level Floor Plan Zone-1 Part-1). First drawing from the first floor and the first to contain CAV_1F tags. Dense teaching/study view with 26 VAV_1F_S11, 8 VAV_1F_S15, 6 CAV_1F_S11 and one FCU_1F. | Filled C/D for 34 existing rows and INSERTED 6 new CAV rows. Existing: VAV_1F_S11_001-022 (rows 919-940), _088/_089/_090 (942-944), VAV_1F_S15_005/006/007/008 (949-952), _012 (956), _039S (964), _096/_097 (966-967), FCU_1F_002 (782). New: inserted rows 1166-1171 for CAV_1F_S11_001/002/006/007/008/009, placed AHEAD of the CAV_B block to keep the CAV section in tag order. CAV block now spans 1166-1193 and the SSC header moved from row 1188 to row 1194. | Clean mappings: Group Study Room1/2/3/4 (S11_001/002/003/022), Computer Classroom (S11_014-021, eight units in the right-hand teaching block), Childeren Library (S15_006/007/008 + CAV_1F_S11_009), Multipurpose Room (S15_096/097), Staff Office (S15_039S), Security Room (CAV_1F_S11_001), Open Reading Area (CAV_1F_S11_006). Drawing spellings preserved: 'Infor. Lteracy Instr.1/2', 'Childeren Library'. EXECUTIVE RULE APPLIED: VAV_1F_S15_005 = Head Librarian Office set Not Included, consistent with Lib. Director's Room and Director Head. Everything else on this view is Included. FCU_1F_002 named from its yellow leader line running down to the ICT Room (Women) label. Out of scope: EF-1-02C, LCP-Z1, ST-01, ST-16, L-1, L-2. | Verified by re-reading A782, A919:D944, A949:D952, A956, A964:D967 and A1164:D1196 - all 40 rows, the 6-row insert and the new SSC header position at 1194 confirmed. YELLOW flagged (9 rows): 922/923/924/928 - the Infor. Lteracy Instr.1 and Instr.2 labels sit one above the other over a single 2x5 grid of VAVs with no clear wall between them; split as 2 units to Instr.1 and 8 to Instr.2, which is uneven and needs confirmation; 956 (S15_012) sits below the Staff Office in an unlabelled pocket and was assigned to Childeren Library on proximity; 782 (FCU_1F_002) ICT Room (Women) - flagged for the INCLUSION question, currently Included as a public ICT space rather than a technical room; 1167 (CAV_1F_S11_002) leader points into the Rest Room / ICT block; 1169 (CAV_1F_S11_007) sits in the corridor gap between the Computer Classroom and the Head Librarian/Staff Office block, reading a notably cold 15.2; 1170 (CAV_1F_S11_008) sits exactly between the downward leader arrows for Infor. Lteracy Instr.1 and Computer Classroom, so it was given a dual name. RED (3 rows): 942/943/944 (S11_088/089/090) sit in the bottom-right run with no room label. NOT WRITTEN: VAV_1F_S11_087 (row 941) does not appear on this view.
32 | 2026-08-12 | IMG_9598.jpeg - QNL Honeywell HMI, 'First Floor Zone-2-P1' (First Level Floor Plan Zone-2 Part-1). Restaurant / Front Kitchen / Public Service view with 12 new CAV_1F_S15 tags. | Filled C/D for 11 existing rows and INSERTED 12 new CAV rows. Existing: FCU_1F_003 (783), FCU_1F_059-064 (839-844), VAV_1F_S15_009/010/011 (953-955), VAV_1F_S15_098 (968). New: inserted rows 1172-1183 for CAV_1F_S15_002/005/006/010/011/012/013/014/015/016/017/018, placed after the CAV_1F_S11 group. CAV block now spans 1166-1205 and the SSC header moved from row 1194 to row 1206. | The Restaurant / Front Kitchen block was split by row: the bottom run of sensors sits level with the 'Front Kitchen' label (CAV_1F_S15_006 + FCU_1F_062/063/064) and everything above it belongs to the Restaurant (CAV_1F_S15_002/005/010/011/012/013/014/015 + FCU_1F_059/060/061). Both are Included - a kitchen is neither plant nor executive. Multipurpose Room (VAV_1F_S15_098) sits inside the circular room outline, unambiguous. FCU_1F_003 = IDF Room set Not Included as a technical room. The right-hand staff rooms on this view (Bibliographer1/2, Spec. Coll & Arch, R&L Services, AD. Public Service, REF. Librarian 1-12) carry NO controllable tags, so none were recorded. Out of scope: EF-2-01, EF-1-01C, L-3, L-4, ST-03. | Verified by re-reading A783, A839:D844, A953:D955, A968 and A1170:D1207 - all 23 rows, the 12-row insert and the new SSC header position at 1206 confirmed. YELLOW flagged (3 rows): 783 (FCU_1F_003) sits between the 'Storage' label above and 'IDF Room' below; assigned IDF Room per this drawing's label-below-right convention, which also drives the Not Included call, so if it is actually Storage the classification flips; 1181 + 1182 (CAV_1F_S15_016/017) sit just outside the restaurant's right-hand wall in the circulation zone and were assigned to Public Service on proximity. RED (4 rows): 953/954/955 (VAV_1F_S15_009/010/011) sit in the unlabelled open area at top-left outside the room outline; 1183 (CAV_1F_S15_018) sits in an unlabelled pocket near the L-3/L-4 lifts, above the Media Studio / Storage strip. Cell note added to D1180: CAV_1F_S15_015 displays '??????' instead of a temperature - second sensor found showing this fault after FCU_B_038 (row 917).
33 | 2026-08-12 | IMG_9599.jpeg - QNL Honeywell HMI, 'First Floor Zone-2-P2' (First Level Floor Plan Zone-2 Part-2). Media studios, prayer/ablution block and the lounge FCU bank. Also contains VAV_1F_S11_087, which was outstanding from IMG_9596. | Filled C/D for 26 existing rows and INSERTED 2 new CAV rows. Existing: FCU_1F_027/029/030/031/032/033/034/035 (807-815), FCU_1F_047-050 (827-830), VAV_1F_S11_087 (941), VAV_1F_S15_001-004 (945-948), _021-025 (957-961), _038/_039/_040 (962/963/965). New: CAV_1F_S15_004 at row 1173 and CAV_1F_S15_019 at row 1185, both placed in sorted tag position. CAV block now spans 1166-1207 and the SSC header moved from row 1206 to row 1208. Everything on this drawing is Included. | Clean mappings: Media Studio1 (S15_001/002), Storage (S15_003), Media Studio2 (S15_004), Prayer Room (Female) (S15_021/022), Prayer Room (Male) (S15_023), Lounge (FCU_1F_047/048/049/050). Prayer rooms, ablution rooms and lounges are all public spaces, so none of the exclusion rules apply. BACKLOG CLEARED: VAV_1F_S11_087 (row 941) was the tag missing from IMG_9596 and appears here in the unlabelled open area at top-left, so it took the Key Plan name for THIS drawing (Zone-2 Part-2) rather than Zone-1 Part-1. Out of scope: Structure Area, Special Events and People Mover Main Entrance are labelled but carry no controllable tags. | Verified by re-reading A807:D815, A827:D830, A941:D948, A957:D965 and A1170:D1209 - all 28 rows, both inserts and the new SSC header position at 1208 confirmed. YELLOW flagged (14 rows): 807/809/810/811/812/813/814/815 - eight FCUs drawn OUTSIDE the building outline below the two 'Lounge' cells with no labels of their own; all given 'Lounge' since both labels read the same, but whether they serve the lounges at all needs confirming; 960 (S15_024) and 961 (S15_025) sit between Prayer Room (Male)/(Female) and the two Ablution rooms, whose labels are placed far right with long horizontal leader arrows, making the split uncertain; 962 (S15_038) assigned Ablution (Men) from the same leader cluster; 963 + 965 (S15_039/040) and 1173 (CAV_1F_S15_004) - three units surround the small 'Green Room' label from above, left and below, which is more units than a green room would normally need; 1185 (CAV_1F_S15_019) sits just below the Media Studio1 block, possibly in the corridor. RED (1 row): 941. TEMPERATURE ANOMALIES noted as cell notes: D830 FCU_1F_050 reads 41.7 C against ~17 C on its neighbours, and D947 VAV_1F_S15_003 reads 34.1 C in Storage. NOT WRITTEN: FCU_1F_028 (row 808) does not appear on this view despite sitting mid-sequence in the lounge bank.
34 | 2026-08-12 | IMG_9600.jpeg - QNL Honeywell HMI, 'First Floor Zone-3-P1' (First Level Floor Plan Zone-3 Part-1). Unusual view: 19 FCU tags but the drawing carries only ONE piece of text, the word 'Enter' near the top - no room names anywhere. | Filled C/D for 19 existing rows, all Included and all red: FCU_1F_014 (794), _016/_017/_018 (796-798), _020 (800), _022-_028 (802-808), _036-_040 (816-820), _051/_052 (831-832), _065 (845). No CAV, FEV or VEV tags, so no rows inserted and the SSC header stays at row 1208. | Every one of the 19 sensors took the Key Plan name 'First Floor Zone-3 Part-1 (IMG_9600.jpeg)' and was auto-Included per the agreed rule, because the drawing contains no room labels at all. The only text on the plan is 'Enter', which marks a doorway rather than naming a room, so it was not used. The sensors are drawn as a free-floating grid over an open diagonal area with no room outlines around them, which is consistent with this being open library floor rather than cellular rooms. BACKLOG CLEARED: FCU_1F_028 (row 808) was noted last turn as missing from the lounge bank on IMG_9599 - it appears here instead. | Verified by re-reading A794:D845 - all 19 rows carry the correct zone name, and spot-checked A794:D798, A805:D808 and A845 as rendered text. No yellow flags: with no labels present there is nothing ambiguous to flag, the whole set is red for your review. Rows deliberately left blank because those tags are not on this view: FCU_1F_015 (795), _019 (799), _021 (801). FCU_1F block status: 40 of 65 rows now filled; still blank are FCU_1F_004-013 (784-793), _015 (795), _019 (799), _021 (801), _041-046 (821-826) and _053-058 (833-838). Temperature spread on this view is wide - FCU_1F_018 reads 12.8 C and _020 reads 14.1 C against 21.2 C on _023 - but all are plausible for an open floor so no anomaly notes were added.
35 | 2026-08-12 | IMG_9601.jpeg - QNL Honeywell HMI, 'First Floor Zone-3-P2' (First Level Floor Plan Zone-3 Part-2). Circulation / book-handling area: 23 FCU tags arranged as a free-floating grid over open floor with blue zone labels interleaved between the rows. | Filled C/D for 23 existing FCU_1F rows: _004-_013 (784-793), _015 (795), _019 (799), _021 (801), _041-_046 (821-826), _053/_054 (833-834), _057/_058 (837-838). Seventeen Included, six Not Included as executive rooms. No CAV, FEV or VEV tags, so no rows inserted and the SSC header stays at row 1208. | There are no room outlines on this view - the sensors sit in two column-pairs and the blue labels act as headers sitting ABOVE each group, so assignment was made by reading down from each label to the next one. Left pair: 'Access Service' heads the first two rows (FCU_1F_019/021/053/054), then 'Book Drop Off' heads the remaining four rows (FCU_1F_011/012/010/042/008/009/007/041). Right pair: 'Circulation Director' heads the first two rows (FCU_1F_015/013/045/046), then 'Book Exit Point' heads the rest (FCU_1F_006/005/044/043/004). 'ILL Director' heads the two units above everything else (FCU_1F_057/058). EXECUTIVE RULE APPLIED: ILL Director and Circulation Director both set Not Included, consistent with Head Librarian Office, Lib. Director's Room and Director Head. People Mover Main Entrance and Heritage Collection Entrance are labelled on the view but sit well away from any tag. | Verified by re-reading A784:D795, A799:D801, A821:D826 and A833:D838 as rendered text - all 23 rows confirmed. YELLOW flagged (6 rows): 837/838 ILL Director and 793/795/825/826 Circulation Director. The flag is about GROUPING, not the executive call - assigning four sensors to a single 'Circulation Director' office and two to 'ILL Director' is a lot for cellular offices, which suggests these blue labels may mark open-plan functional zones (a director's desk area within the circulation floor) rather than enclosed rooms. If they are open zones rather than private offices, the Not Included classification on all six rows should be reversed. TEMPERATURE ANOMALY: cell note added to D837 - FCU_1F_057 reads 56.3 C, the highest reading seen on any QNL drawing so far, against 19.6 C on FCU_1F_058 directly beneath it; almost certainly a failed sensor. FCU_1F BLOCK NOW 63 of 65 FILLED - only FCU_1F_055 (835) and _056 (836) remain outstanding.
36 | 2026-08-12 | IMG_9603.jpeg - QNL Honeywell HMI, 'First Floor Zone-4-P2' (First Level Floor Plan Zone-4 Part-2). Final image of the batch. Near-empty view with only two FCU tags. User indicated this was the last drawing, so a completeness sweep of the whole QNL section was run afterwards. | Filled C/D for the final 2 FCU_1F rows: FCU_1F_056 (836) = Included / 'External Book Drop', and FCU_1F_055 (835) = Included / 'First Floor Zone-4 Part-2 (IMG_9603.jpeg)' in red. This completes the FCU_1F block (all 65 rows, 781-845). No CAV, FEV or VEV tags; SSC header remains at row 1208. | FCU_1F_056 has its room name printed directly beneath the tag inside the same box outline ('External Book Drop'), which is the clearest label placement seen on any drawing so far - no ambiguity, no highlight. FCU_1F_055 sits alone in a small angled room at top-right with no label anywhere near it, so it took the Key Plan name and was auto-Included per the rule. The other two blue labels on the view, 'RP-06' and 'Main Entrance', are a ramp reference and an entrance marker rather than room names, and both sit far from either tag, so neither was used. FCU_1F_056 reads 13.4 C, which is consistent with an external book drop exposed to outside air. | Verified by re-reading A835:D836 as rendered text. COMPLETENESS SWEEP of the full QNL section (rows 766-1207, 442 tags) found 381 filled and 61 still blank, broken down as: AHUB001-015 (766-780, 15 rows); FCU_2F_041/042 (858-859); FCU_B_010/015/016/017 (889, 894, 895, 896); VAV0001 (918); VAV_2F_S10_001/002/004/005 (969, 970, 972, 973); VAV_2F_S13_005/006/007/009/011/012/013/014 (1009-1018); VAV_2F_S14_015/021 (1035, 1041); VAV_B_S10_001-019 and _024 (1047-1065, 1070 - 20 rows); VAV_B_S13_003/004/005/007/008 (1119-1124). RAISED WITH USER: the 15 AHUB rows are a scope question, not a missing drawing - AHU-B-01 to AHU-B-13 were visible inside Plant Room 1, Plant Room 2 and Plant Room 4 on IMG_9588 and IMG_9594 but were treated as out of scope because the brief named VAV, FCU, CAV, FEV and VEV only. If AHUs are wanted they would all be Not Included as plant-room equipment. The largest genuine gap is VAV_B_S10 (20 rows) - only _020 to _023 have appeared on any drawing so far.
37 | 2026-08-12 | New validation stream: sending Honeywell BMS screenshots to validate/correct/update QNL room names and inclusion status, noting column A tag formats differ but are distinguishable. First image IMG_9563.jpeg = VAV Summary Type-01, basement S11 units. | Matched the 24 VAV/B/S11 units on the BMS screen to registry rows 1071-1094 and 1113-1116. Appended the BMS room codes (B001, B001A, B002, B008, B009) to column D and corrected VAV_B_S11_022/023. Changed C1093 from Not Included to Included, flagged C1093:D1093 yellow and added an explanatory note. | Tag format maps as VAV/B/S11/nnn -> VAV_B_S11_nnn. BMS location groups: 001-004 + 011-014 = Tech.Services Area B001 & Break Out Area B001A (kept the registry's finer Break Out vs Tech Services split, only added the codes); 005-010 + 015-020 = Tech.Services Area B001; 024 = Kitchen B002; 043-046 = Receiving Area B008; 022 + 023 = Corridor Leading To Reception & Lounge B009. The Location column in the photo is skewed progressively downward toward the bottom, so group boundaries were resolved using the registry's existing names as the cross-check (024=Kitchen and 043-046=Receiving already agreed, which anchors the alignment). Row 1091 (VAV_B_S11_021, 'Basement Zone-1 Part-1') is not on this screen and was left untouched, as were rows 1095-1112 (S11_025-042). | Verified by re-reading A1071:D1094 and A1113:D1116 - all 24 room names and the C1093 inclusion change confirmed. ONE CONFLICT RAISED: VAV_B_S11_023 was 'Plant Room 1 / Plant Room 2 (IMG_9588.jpeg)' / Not Included from an earlier drawing; the BMS pairs it with 022 (Master/Slave) on the corridor, so it was updated to Corridor Leading To Reception & Lounge B009 / Included and flagged yellow pending your confirmation. Awaiting the next BMS image.
38 | 2026-08-12 | Asked why the TRANSPOSE(FILTER(...)) formula in 'SSC Room Names'!D45 — pulling matching Tag Nos from the Controllable Asset Registry into a horizontal list — always returns #N/A. | Diagnosed the criteria range and rewrote D45 to wrap the comparison in IFERROR. | Scanned 'Controllable Asset Registry'!E1214:E1332 for error values: exactly one, E1287 (#N/A), on VAV0063 whose room reads '(NOT FOUND ON DRAWING LEVEL 3)'. A single error anywhere in a FILTER include-array poisons the whole array, so FILTER returned #N/A regardless of the match. New formula: =TRANSPOSE(FILTER('Controllable Asset Registry'!$A$1214:$A$1332,IFERROR('Controllable Asset Registry'!$E$1214:$E$1332=C45,FALSE),"No Equipment in entity")). Chose IFERROR over patching E1287 so the formula is robust to future error rows; E1287 itself still needs an entity name. | D45 now spills VAV0002, VAV0003, VAV0004 across D45:F45. Only D45 was changed — same fix should be copied to other rows in column D. Open item: E1287 in the Controllable Asset Registry is still #N/A.
39 | 2026-08-14 | Sent IMG_9565.jpeg - Honeywell VAV Summary Type-01 (QNL). Asked me to take the VAV names from the 3rd column of the screen, find them in column A of the Controllable Asset Registry, and fill the Location text from the 1st column into column D. | Matched all 27 VAV tags on the screen to registry rows. Filled the 5 rows whose column D was blank: D1068 (VAV_B_S10_009), D1071/D1072/D1073 (VAV_B_S10_012/013/014) and D1078 (VAV_B_S10_019). Left the other 22 rows untouched because they already held room names. | Screen tag format VAV/B/S10/009 maps to registry format VAV_B_S10_009. Groupings read off the merged Location cells: S10/009 = CR6 Circulation; S10/012, 013, 014 = CR6 Conversation Work Area B.209; S10/019 = CR6 Prof Librarian B.208. Image name appended in parentheses per the established convention. CONFLICTS NOT OVERWRITTEN, needing your call: (1) VAV_B_S15_001 row 1166 registry says 'Prof. Librarian (IMG_9591.jpeg)' but this screen shows it under HC Lobby & Vestibule B154; (2) VAV_B_S15_002/003/004 rows 1167-1169 say 'Loby and Security' vs screen 'HC Lobby & Vestibule B154'; (3) VAV_B_S15_011/012 rows 1176-1177 say 'VIP Majlis' vs screen 'Basement Zone 3 HC VIP Majlis B148' - same room, different wording. Rows 1060-1067 + 1083 (Digitisation Area B.200), 1069/1070 (Technical Services B.204), 1074 (Instruction Outreach B.206), 1075-1077 (Multimedia Presentation B.205) and 1137 (Security Control Room B.105) all agree with the screen. | 5 blank cells filled and verified by re-reading A1068:D1068, A1071:D1073 and A1078:D1078. Awaiting your decision on the 7 VAV_B_S15 wording conflicts listed in Details.
40 | 2026-08-14 | Sent IMG_9564.jpeg - Honeywell VAV Summary Type-01 page P2 (QNL). Same task as the previous screen: match the VAV names to column A of the Controllable Asset Registry and write the Location into column D, and highlight all the matched rows in blue. | Matched all 26 VAV tags from the screen, wrote the screen Location into column D for each, and applied a blue fill (#BDD7EE) across A:D on all 26 rows. Rows touched: 1104, 1108, 1132, 1133, 1135, 1141-1143, 1146-1149, 1152-1165. | Adopted the naming convention you applied by hand earlier this session: dropped the 'Basement Zone N' prefix and punctuated the room number as B.xxx, no image-name suffix. Screen typo 'Presrvation' corrected to 'Preservation' to match existing sheet spelling; 'Boh Kitchen' written as 'BOH Kitchen' for the same reason. Location groupings read off the merged cells, allowing for the row drift in the Honeywell page: S14_040 = BOH Kitchen B.044 (standalone) and S13_003/004 = Processing Room B.103 (slave + master). Unlike the previous image I overwrote existing column D text, because the old entries were generic placeholders without room numbers. One overwrite worth noting: D1104 (VAV_B_S11_021) previously read 'Basement Zone-1 Part-1 (IMG_9587.jpeg)' and is now 'Reception & Lounge B.009' per this screen - flag if IMG_9587 was the better source. | All 26 rows re-read after writing; tag, location text and #BDD7EE fill confirmed on every one. Prior turn's VAV_B_S15 conflicts (rows 1166-1169, 1176-1177) remain open.
41 | 2026-08-14 | Sent IMG_9563.jpeg - Honeywell VAV Summary Type-01 page P1 (QNL). Same task: match the VAV names to column A of the Controllable Asset Registry, put the Location into column D, and highlight them in blue. | Matched all 27 VAV_B_S11 tags from the screen. Normalised 5 column D entries that still carried the old image-suffix format (D1107 to 'Kitchen B.002'; D1126:D1129 to 'Receiving Area B.008') and applied the blue fill (#BDD7EE) across A:D on all 27 rows: 1084-1103, 1105-1107, 1126-1129. | The other 22 rows already held correct room text from your earlier manual pass, so I left the wording alone and only added the highlight. Deliberate decision on group 1: the screen shows one merged label 'Tech.Services Area B001 & Break Out Area B001A' covering S11_001/002/003/004/011/012/013/014, but the sheet already splits that group - 001, 002, 011, 012 as 'Break Out Area B.001A' and 003, 004, 013, 014 as 'Tech, Services & Collections Office B.001'. The split is more precise than the merged screen label so I preserved it rather than flattening all eight rows to the combined name. Row drift on the Honeywell page handled as before: standalone S11_024 = Kitchen B.002, and S11_022/023 = Corridor Leading To Reception & Lounge B.009. | All 27 rows re-read after writing; tag, location text and #BDD7EE fill confirmed on each. Open items unchanged: VAV_B_S15 wording conflicts at rows 1166-1169 and 1176-1177, and whether D1104 should revert to the IMG_9587 value.
42 | 2026-08-17 | Sent IMG_3029.jpeg - Siemens RDC BMS 'Utility Building FCU Summary'. Asked me to take the FCU names from the 5th column of the screen, find them in column A of the Controllable Asset Registry, and write their location (room name + room no. from the 4th and 3rd columns) into column D, matching the format of the selected cell D2240. | Matched all 29 RDC Utility Building FCU tags on the screen to registry rows 2238-2266 and wrote the room name + room number into column D for the 28 that were blank (D2240 was already filled). | Format followed from D2240 ('MAIL ROOM U-0128'): room name in caps followed by the room number. Ground floor (RDC_UB_GF_): FCU8001 GENERAL STORAGE ROOM U-0129, 8002 SHOP U-0135, 8004 GENERAL STORAGE U-0108, 8005 RECYCLING ROOM U-0109, 8006 CYLINDER STORAGE U-0105, 8007 LN2 DISPENSER U-0104, 8008 FLAMMABLE STORAGE U-0103, 8009 FLAMMABLE WASTE STORAGE U-0102, 8010 BMS ROOM U-0117, 8011 BREAK ROOM U-0118, 8012 OFFICE SPACE U-0119, 8013/8014/8512/8513/8514/8515 WET/MECH/FIRE ROOM U-0120, 8502-8505 SHIPPING AND RECEIVING. Mezzanine (RDC_UB_MF_): FCU8501/8506/8507/8508/8509/8510/8511 MECHANICAL ROOM U-1101. Two judgement calls: (1) FCU-8502 to 8505 sit against a merged 'SHIPPING AND RECEIVING' room-name cell with the ROOM NO. column blank on the screen, so no room number was appended - note added on D2252. (2) U-1101 is shown as a single merged room number spanning the whole Level -1 mechanical block, so it was applied to all seven mezzanine FCUs. | Rows 2238-2266 of column D on Controllable Asset Registry are now fully populated; verified by re-reading A2238:D2266. Open item: room numbers for the four SHIPPING AND RECEIVING FCUs (8502-8505) need confirming from drawings.
43 | 2026-08-17 | Sent IMG_3056.jpeg - Siemens RDC BMS 'South Building Fan Coil Unit' summary (Level 0 and Level -1) - and asked me to apply the same treatment as the Utility Building screen: match the FCU tags to column A of the Controllable Asset Registry and write their room location into column D. | Located all 26 South Building FCUs from the screen (rows 2191-2202 Level -1, rows 2223-2237 Ground Floor). Column D was already populated in an older abbreviated style, so I stopped and asked before overwriting; user chose to rewrite all 26 to the BMS format. Wrote D2191:D2202 and D2223:D2237. | Format followed from D2240: room name in caps + room number. Level -1: FCU0501/FCU3501 STAIR-04 1ST04, FCU0502/0503 UPS ROOM S-1107D, FCU1501/1502 IDF ROOM S-1156, FCU1503 STAIR-01 1ST01, FCU2501 STAIR-03 1ST03, FCU2502/2503 IDF ROOM S-1244, FCU2504/2505 UPS ROOM S-1276. Ground floor: FCU0001 STAIR-02 S-02T02, FCU1001/1002 QTEL ROOM S-0132, FCU1003/1004 IDF ROOM S-0133, FCU1005/1006 EC MDF ROOM S-0134, FCU1007 MECHANICAL ROOM S-0136, FCU1008 STAIR-01 S-01T01, FCU2001 STAIR-03 S-0ST03, FCU2002/2003 AV ROOM S-0210, FCU2004/2005 IDF ROOM S-0271, FCU3001 STAIR-04 S-0ST04. Four rows were genuine data conflicts, not just wording: FCU2502 was 'MEETING ROOM S-1247' (screen pairs 2502 and 2503 to IDF S-1244), FCU2505 was 'MEETING ROOM S-1272' (screen pairs 2504 and 2505 to UPS S-1276), FCU0501 was 'Stair 2 S-1ST02' and FCU3501 was 'Stair S-1ST104' (screen shows both as STAIR-04 1ST04). Two cosmetic calls noted in-cell: the screen labels S-0271 'IDF-S-0271' and S-0ST04 'STAIR-OST04'; both were normalised to match the other IDF and stair entries. | D2191:D2202 and D2223:D2237 rewritten and verified by re-read. Pre-existing drawing notes on D2192 and D2193 were left intact. Not covered: the screen has a NEXT >> button, so any further South Building FCU pages have not been reviewed, and the 2F rows (2203-2222) were untouched.
40 | 2026-08-17 | Uploaded RDC_HVAC_DRAWINGS_MERGED.pdf (68 A0 as-built sheets) and the register. Asked to fill blank and verify yellow column-D cells for RDC FCU/VAV/EV/VEV equipment from the drawing schedules, North Building first. Rule: if room name/number not found, put the schedule page in column D and highlight blue; if a yellow row cannot be verified, note where to look in column E. | Extracted the AIR TERMINAL DEVICES SCHEDULES and FAN COIL UNIT SCHEDULES for all North Building parts, then matched every NB target row by tag number. Processed all 219 NB targets: 105 VERIFIED (yellow cleared), 28 verified by room number but schedule uses a different room NAME (noted in E), 53 CORRECTED, 8 blanks filled, 12 blanks flagged blue (found but no room number on the schedule), 11 yellow unverifiable, 2 tags not in any NB schedule. | Pages 1-66 have NO text layer (raster scans; confirmed with poppler and PyMuPDF) and OCR misread reference numbers (e.g. EV-5026 as EV-5025), so all tables were read visually at native 200 DPI. Sources: Level 0 p6 (A2.1), p7 (A2.2), p8 (A2.3), p9 (B2.1 + FCU@L0), p10 (B2.2); Level 1 p21 (A2.1 + FCU@L1), p22 (A2.2), p23 (A2.3), p24 (B2.1), p25 (B2.2); Level 2 FCU p32; Pedestrian Walkway FCU p57. 860 air-terminal refs + 44 FCUs captured. The AT schedules list VAV, EV, VEV, FEV, CEV and CAV refs in one table, so EV/VEV rows resolve from the same source. Corrections were applied only where the schedule room NUMBER differed; the previous value is preserved verbatim in column E as was: "...". Saved with openpyxl only - NOT LibreOffice-recalc - to preserve the 159 TRANSPOSE(FILTER) array formulas in SSC Room Names with Equip. (verified 159/159 intact). | North Building COMPLETE - zero blank column-D cells remain in the NB block. KEY FINDING: the 53 corrections are not random - whole blocks were shifted by one position (e.g. GF lab block VAV5180-5270A: registry had Analyt Core-1/Org Chem/Furnace/MBE-Evap where the schedule reads Analytical Core Lab 2 N-0140A, Furnace N-0140B, Prep Lab N-0140C, Sputter N-0140D, ALD N-0140F, Support N-0140H, PLD N-0140J, Organic Chem N-0140K; also VAV4210-4212 CSP Lab -> Desalination Lab N-0240D; VAV7195 Conference N-0440 -> Office 04 N-0436). Note there is no MBE Room anywhere in the A2.2 schedule. DISCREPANCY: FCU-5993/5994 are listed on the LEVEL 0 schedule (p9, Part A2.2, Conference Room) but are tagged NB_1F in the register. UNRESOLVED: VAV5054 (schedule jumps 5053 to 5055) and FCU2004 (not in any NB schedule - likely a South Building unit). STILL TO DO: South Building (55 blank + 33 yellow) from Level 0 p1-p5/p11, Level 1 p16-p20/p26, Level 2 p27-p30, and rooms on p59-p60. Utility Building schedules are NOT in this PDF.
41 | 2026-08-17 | After verifying and trimming my North Building edits, asked me to do the South Building and the Utility Building if any, using the same rules (fill blanks where found; verify yellows; blue + page ref in D when the schedule has no room name/number; note where to look in column E when a yellow cannot be verified). | UTILITY BUILDING: nothing to do - all 38 UB rows already filled with no yellow flags, and this PDF contains no UB equipment schedule (UB appears only as airflow diagrams p56/p58 and one section sheet p45). SOUTH BUILDING: processed all 88 targets - 47 blanks filled, 23 verified (yellow cleared), 3 verified by room number but the schedule uses a different name, 2 corrected, 4 blanks blue-flagged, 9 not found (notes in column E). | KEY: every South sheet carries an AIR TERMINAL UNIT NUMBERING legend that decodes the tags - digit 1 = drawing part (0 = A1.3 and B1.1, 1 = B1.2, 2 = A1.2, 3 = A1.1), digit 2 = level (0 = Level 0, 5 = Level 1, 2 = Level 2). So AT-3511 is A1.1/Level 1 and AT-0509 is B1.1/Level 1. Sources read at native 200 DPI: A1.1 L0 p1, B1.1 L0 p4, A1.1 plus a short A1.2 table L1 p16, A1.2 L1 p17, B1.1 L1 p19, B1.2 L1 p20. FCU tags were deliberately excluded from the air-terminal lookup so that e.g. FCU2502 is not matched to AT-2502. Saved with openpyxl only (no LibreOffice recalc); 159/159 TRANSPOSE(FILTER) array formulas verified intact. The North Building block was not touched this turn. | South corrections: VAV3511 Dressing Room S-1286 -> Corridor S-1280; VAV3514 Office S-1294 -> Office S-1284. VAV3519 filled as Open Plan S-1293. NOT RESOLVABLE FROM THIS PDF: (1) the A1.2 and B1.2 Level 0 schedules on p2 and p5 have NO room name/number columns at all - only airflow and duct dimensions - so VAV1003/1004/1008 and VAV2005 are blue-flagged; (2) there is NO South Building fan-coil schedule anywhere in the document, so FCU2004, FCU2502, FCU2503 and FCU2205 stay unverified; (3) VAV0001 and VAV0002 - the B1.1 schedule starts at AT-0003; (4) AT-0122 - its second digit does not fit the level legend. DATA-ENTRY ISSUE: rows 1629 and 1782 have tags RDC_SB_1F_VAV and RDC_SB_GF_VAV with no unit number at all, so they can never be matched - complete or remove them at source. Remaining across the whole RDC block: 4 blank cells (rows 1629, 1782, 1783, 1784) and 5 SB plus 2 NB yellows.
42 | 2026-08-17 | Pointed out that the AIR FLOW DIAGRAM sheets carry schedules I had dismissed, and that they may show the VAV locations I had inferred to be AT. Asked me to (1) use the exhaust/return diagrams for the EV/VEV rows, (2) resolve the rows still unresolved, and (3) cross-check everything already written. | Opened the airflow diagrams (previously excluded at the indexing stage - my error). Item 2 COMPLETE: resolved 6 rows that the plan-sheet schedules could not - VAV0001, VAV0002, VAV1003, VAV1004, VAV1008, VAV2005. Item 3 STARTED: spot-verified North and South rows against the diagrams; every row checked so far confirms. Item 1 NOT STARTED: the return/exhaust diagrams (p51-p55, p64-p65 South) have not been read yet. | AT vs VAV QUESTION SETTLED. The diagrams tag each terminal AT-xxxx with a vertical label beside it giving the valve type (VAV-01, VAV-02, VAV-05, CAV-01, CAV-03). The p36/p46 EQUIPMENT legend reads: AT = Air Terminal Device (Supply), VAV = Variable Air Valve (Supply Venturi), CAV = Constant Air Valve (Supply Venturi); and the SCHEMATIC LEGEND gives AT, VAV and CAV a single shared symbol. So AT-xxxx is the device number and VAV-nn is the valve fitted to it - there is no separate parallel VAV numbering series. Registry VAVxxxx = drawing AT-xxxx is therefore correct. IMPORTANT CORRECTION to an earlier note of mine: supply-side (AT/VAV/CAV) and exhaust-side (VEV/CEV/FEV/EV) are SEPARATELY NUMBERED. AT-1002 on the supply diagram is NOT VEV-1002. Any EV/VEV/FEV/CEV room I previously inferred from a paired VAV row needs checking against the exhaust diagrams. | VERIFIED AGAINST THE DIAGRAMS (all matched what was already written): South p48 - AT-0017 S-0119 COMP.LAB, AT-0012 S-0114, AT-0011 S-0113 CONF, AT-0009/0010 S-0111/S-0112 PHONE, AT-0007 S-0109 CONF, AT-0004 S-0104, AT-0005 S-0105, AT-0006 S-0107/S-0106, AT-0008 S-0110, AT-0020 S-0120/0120A/0120B, AT-0018/0019 S-0123 RESTAURANT. North p35 - VAV-4190/4191 + FEV-4193/4194 CSP LAB N-0240B, AT-4200/VEV-4201 TEST RM 1 N-0240C, AT-4290 OFFICE N-0261. North p36 - VAV-5250/VEV-5251 SUP RM N-0140H, VAV-5260/VEV-5261 PLD N-0140J, CAV-5240/CEV-5241 A/L N-0140G, VAV-5220/VEV-5221 EVAP N-0140E, CAV-5170 SERVICE CORR N-0136, AT-5140 N-0123, AT-5135 N-0122. These independently confirm the Level 0 lab-block corrections made from the plan schedules. STILL OPEN: VAV5054 (not yet located on p36); the full exhaust-side pass (item 1); and the remaining bulk cross-check of ~300 rows (item 3). Airflow-diagram sheet map: North p35 A2.1 L0, p36 A2.2 L0, p37 B2.1 L0, p38 B2.2 L0, p39-p43 Level 1; South supply p46 (A1.1/A1.2/A1.3 L0), p47 (A1.x L1), p48 (B1.1/B1.2 L0), p49-p50; South return p51-p55; South exhaust p64-p65; Utility p56/p58.
43 | 2026-08-17 | Told me to go ahead using all the document's information without limiting myself to specified pages, and asked what about the FEV, VEV and EV rows. | Ran a full cross-check of EVERY RDC row against the extracted schedules, not just the blank/yellow ones. EXHAUST SIDE (202 rows: 73 FEV, 62 EV, 51 VEV, 12 CEV, 1 CAV, 3 SB EV): 152 already correct, 39 CORRECTED, 9 flagged unverifiable. SUPPLY SIDE (AT/VAV/CAV, 1383 rows with data): 1171 already correct, 47 CORRECTED, 17 held back by guards, 155 with no schedule source. | The air terminal schedules list EV, VEV, FEV, CEV and CAV refs in the same AT-REF column as the supply tags, so the exhaust rows could be verified from the schedules already extracted - no new drawing reading was needed for them. THREE GUARDS stopped false corrections: (1) multi-node sensors AT-7090-N1/N2, AT-7105-N1/N2 and AT-7120-N1..N9 serve several rooms each and the schedule lists only the parent tag once, so all 13 were left as-is; (2) VAV5930P and VAV5940P carry a P suffix meaning penthouse/Level 2 and are distinct devices from the Level 1 5930/5940, so they were left as-is; (3) VAV4312 and AT-4312 map to a schedule row (Breakout) that has no room number, so they were noted rather than changed. Diagram evidence used: p35 and p36 North airflow diagrams independently confirmed the Level 0 lab-block corrections (VAV-5250/VEV-5251 SUP RM N-0140H, VAV-5260/VEV-5261 PLD N-0140J, CAV-5240/CEV-5241 A/L N-0140G, VAV-5220/VEV-5221 EVAP N-0140E). | EXHAUST PATTERN FOUND - same lazy-fill as the supply side: EV-4236/4261/4286 all read Corridor N-0246 but belong to N-0250/N-0255/N-0260; EV-6356/6381/6401 all read Corridor N-0365 but belong to N-0372/N-0378/N-0381; EV-7396/7426/7461/7486 all read Corridor N-0451 but belong to N-0446/N-0452/N-0457/N-0462; EV-4661/4686/4711/4736 all read Corridor N-1223 but belong to N-1227/N-1232/N-1237/N-1242; EV-5891/5921/5941 all read Corridor N-1150 but belong to N-1160/N-1168/N-1165. Also corrected the pre-existing AT-0003 row (was Corridor S-0117, which duplicated AT-0015; the p4 schedule gives Entrance Lobby S-0102). Supply/exhaust numbering is SEPARATE: AT-1002 feeds S-0139 Comp Lab while EV-1002 serves NOC S-0140A. RUNNING TOTAL of corrections across the whole RDC block: 53 (North supply) + 2 (South supply) + 39 (exhaust) + 47 (full supply sweep) = 141. STILL OPEN: 155 supply and 9 exhaust rows with no schedule source (mostly multi-node sensors, Level 2 units and South AT rows on parts whose schedules carry no room columns) - these need the return/exhaust airflow diagrams p51-p55 and p64-p65, plus North p37-p43, which have not been read yet. VAV5054 still not located.
44 | 2026-08-17 | Asked me to close out the 22 rows I had held back - the 13 multi-node sensors and the 9 unverified exhaust rows. | Read p38 (Air Flow Diagram B2.2 Level 0) and re-used p36/p48. Outcome on the 22: 6 VERIFIED as already correct, 3 corrected or normalised, 13 multi-node rows deliberately left as-is with an explanatory note, and 3 marked NOT CONFIRMED as provisional. | MULTI-NODE FINDING: p38 shows AT-7090, AT-7105 and AT-7120 each as a SINGLE air terminal (serving N-0412, WKS N-0415 and WKS N-0418 respectively). The diagrams depict air terminals, not BMS sensor points, so they can neither confirm nor refute the -N1..-N9 sub-node rooms (N-0412A, N-0415A, N-0418A, N-0430A..N-0430F) that an earlier session read off the plan drawings. Both can be true at once: one terminal serving a zone, with several sensor nodes distributed through it. Each of the 13 rows now carries a note saying explicitly NOT to overwrite them with the parent terminal's room - this is the trap an automated sweep would fall into. OTHER VERIFICATIONS: p38 confirmed VAV-7070/7071 SURF ANALYSIS N-0404F with VEV-7072/7073 and FEV-7074 on the exhaust branch (so FEV-7075 is consistent); CAV-7220/CEV-7221/EV-7126 SERVICE CORR N-0441 and NORMAL ELEC N-0420; EV-7122 IDF N-0419, confirming an earlier correction. p48 confirmed the South exhaust series runs one behind the supply series (AT-1002 supply = S-0139, EV-1001 exhaust = S-0139), which validates EV-1001/1002/1003. | CHANGED: FEV-7232 corrected to Inter Lab N-0442A (the p10 schedule puts the 7230 series in N-0442A and the 7240 series in Optical Lab N-0442B); FEV-5222 and FEV-5223 normalised to Evap Room N-0140E, confirmed on the p36 EVAP branch alongside VAV-5220/VEV-5221. STILL PROVISIONAL (3 rows, flagged in column E): VEV-6053, EV-4920 and EV-6981 - VEV-6053 is absent from the p9 B2.1 schedule, and the two Level 2 units cannot be resolved because the p32 Level 2 FCU schedule carries no room numbers at all. RDC block final state: 2 blank cells (rows 1629 and 1782, tags with no unit number), 142 total corrections applied across all passes.
45 | 2026-08-17 | Approved the room corrections, then asked me to delete all of column C and redo the Included / Not Included assessment across ALL sections (not just RDC), since the inclusion status may not have been updated after the room names were corrected. Rules: HQ excludes executive, technical AND public rooms; SSC, QNL and RDC exclude executive and technical only. | Cleared all 2,942 existing column C values across HQ, QNL, SSC and RDC, then reclassified every row from the room name in column D. Result: HQ 404 Included / 368 Not Included; QNL 368 / 81; SSC 101 / 22; RDC 1,226 / 533. 5 rows could not be classified and were left blank and highlighted yellow. Column D and all other columns were left untouched. | Classification is keyword-based on the column D room name. EXECUTIVE: executive, exec, director, dir., manager, sheikh(a), VP, president, chairman, CEO, head of, majlis, VIP, board room. TECHNICAL: electrical, mechanical, plant, IDF, MDF, UPS, BMS, FPC, sprinkler, pump, AHU, riser, shaft, telecom, MCC, server, control room/centre, switchgear, generator, chiller, vent plant, battery, penthouse, transformer, GSM, fire command, gas suppression, misting, Q-tel, AV room, calorifier, MEP, duct, air lock, service equipment, pipe chase, security, panel, boiler. PUBLIC (HQ ONLY): lobby, corridor, toilet/WC, prayer, ablution, vestibule, foyer, atrium, stair, lift, cafe, restaurant, reception, waiting, visitor, exhibition, gallery, auditorium, entrance, walkway, bridge, mens/womens, spa, salon, fitness, treatment, relaxation, changing, nursery, lounge, terrace, dining. THREE JUDGEMENT CALLS were put to the user before applying and answered as follows: (1) LABORATORIES count as technical -> Not Included (bio-med chem, NMR, nano, gene therapy, analytical core, tissue culture, clean room, high bay, desal, CSP, photovoltaic, etc.); (2) EXECUTIVE SUPPORT rooms (VP secretary, exec. assistant, director's staff, officers, members, workstations) are Included, because the occupant is staff rather than the executive; (3) CEILING VOIDS and plenums are classified by the room they serve, so Bridge Ceiling Void and Auditorium high-level void are Included. | 5 rows left BLANK and highlighted YELLOW because column D holds no usable room name: HQ r126 'NOT FOUND ON THE DRAWING OR SCHEDULE', HQ r718 (blank), QNL r931 (blank), QNL r1134 (blank), SSC r1309 '(NOT FOUND ON DRAWING LEVEL 3)'. NOTE the classification is only as good as the room name in column D - rows whose column D holds a page reference (the blue-flagged RDC rows) or a Key Plan zone name rather than a real room were classified on that text and should be re-checked once the real room name is known. Borderline calls worth a spot-check: 'Service Corridor', 'Service Dock' and 'Shop' in RDC were left Included as circulation/back-of-house rather than plant; 'Technical Open Plan S-0211' and 'Situation Room' were left Included as occupied workspaces.
46 | 2026-08-17 | In the RDC section of Controllable Asset Registry, column A tags like RDC_SB_GF_VAV1003_VEV1002 were typed as VAV in column B when the trailing token shows the real device type (VEV). Asked me to review all such tags in the RDC section and correct them. | Scanned A1356:B3114 (RDC section = rows 1356-3114) for tags containing more than one type token, compared column B against the trailing token's letters, and rewrote column B where they disagreed. 153 rows corrected. | Rule applied: the LAST type token in the tag wins (e.g. ..._VAV1003_VEV1002 -> VEV). Verified the target types already exist as valid values elsewhere in the RDC block (EV 65, VEV 51, CEV 12, FEV 73), so no new type vocabulary was introduced. Corrections by type: EV 80, VEV 71, CEV 2. Affected rows span 1394-2105. Tag strings in column A were left unchanged - only the Equipment Type in column B was corrected, since renaming tags would break the links to the RDC Asset Register and the appended AT/valve rows. | Complete and verified: re-scanned A1356:B3114 after the write and found 0 remaining mismatches; spot-checked row 1797 (RDC_SB_GF_VAV1003_VEV1002 = VEV) and row 1394 (RDC_NB_GF_VAV4005_EV4006 = EV). Open item if wanted: whether the composite tag names in column A should also be shortened to the single correct type.
47 | 2026-08-17 | Asked me to read and explain the column D formula on 'HQ Room Names with Equip.' and confirm whether 771 equipment names are returned (cells not equal to 'No Equipment in entity'). | Explained the spilling FILTER/TRANSPOSE formula, then counted equipment names across the full spill region D2:L1042 and reconciled against the source register A4:A777. Added a live audit block at N1:O6. | Key point: the formula TRANSPOSE(FILTER('Controllable Asset Registry'!A4:A777, E4:E777=A2, "No Equipment in entity")) spills HORIZONTALLY, so a room with multiple assets fills D, E, F ... up to column L. Counting column D alone undercounts. Audit formulas used: O3 =COUNTA(D2:L1042)-COUNTIF(D2:L1042,"No Equipment in entity"); O4 =COUNTIF(...); O5 =COUNTA(source); O6 =O5-O3. Also checked for duplicate returns (0) and error cells (0). | Count is 772, not 771. 1041 rooms, 434 with no equipment, 774 equipment rows in source, 2 unplaced: FCU0097 (row 126, col D says NOT FOUND ON THE DRAWING OR SCHEDULE) and VAV0558 (row 718) - both have a blank column E room entity so they can never match. Open item: user to decide whether to assign room entities to those 2 assets.
48 | 2026-08-17 | Acknowledged the equipment count findings - no further work requested. | No changes made to the workbook. | Confirmed count stands at 772 equipment names returned (not 771), with 2 unplaced assets due to blank room entities. | Closed. Open item carried forward from turn 47: FCU0097 (row 126) and VAV0558 (row 718) still have no room entity in Controllable Asset Registry column E and remain unmatched.
49 | 2026-08-17 | After editing some room numbers, the equipment count in column D jumped from 772 to 773 while the 2 blank-entity assets were still blank. Asked whether there is a duplicate somewhere. | Scanned column A for duplicate room entities and the whole D2:L1042 spill region for repeated asset tags. Found the duplicate, then hardened the audit block at N1:O9 with duplicate detection and a duplicate-proof unplaced count. | Root cause: room entity 'entity:HQ_5.110_VP_EDU_OFFICERS' now appears TWICE in column A - row 526 and row 1017. VAV0283 exists only once in the register (row 443) but each duplicate room row runs its own FILTER, so the tag is returned twice, inflating the raw count to 773. Rooms with no equipment also fell 434 to 433 because row 1017 previously matched nothing. New audit formulas: O6 distinct returned =SUM(--(UNIQUE(TOCOL(D2:L1042,3))<>"No Equipment in entity")); O7 duplicate room rows; O8 duplicated equipment returns; O9 unplaced =O5-O6. Replaced the old O6 (=O5-O3) because subtracting the raw count made unplaced read 1 instead of 2 whenever a duplicate existed. | Diagnosed, not yet fixed. Distinct equipment is still 772 and unplaced still 2 (FCU0097, VAV0558), so no data was lost - only row 1017 is a spurious duplicate of row 526. Awaiting user decision on whether to delete row 1017 or correct its room number to the intended one; I did not guess the intended value.
50 | 2026-08-18 | Asked me to confirm that all equipment in Controllable Asset Registry column A rows 779-1229 (QNL block) has been filtered and transposed into column D of 'QNL Room Names with Equip.', matching CAR column E to QNL column A, excluding assets with no value in column E. | Read-only audit. Built the set of 451 QNL tags (CAR A779:A1229) with their column E entity, read every spilled value in QNL D2:AK1041, and reconciled the two sets both ways. | 451 tags, no duplicates. 2 have blank column E (VAV0001 row 931, VAV_B_S13_005 row 1134) - correctly excluded by rule, but they spill into QNL rows 338-1041 where column A is blank, because the FILTER test compares blank E to blank A and returns TRUE. 16 tags (VAV_B_S11_003 to _020, CAR rows 1086-1103) are missing entirely: CAR E reads entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE while QNL A323 reads entity:QNL_B_001_TECH_SERVICES_&_COLLECTIONS_OFFICE (AND vs &). Remaining 433 tags all placed. All 1040 rows of column D carry the formula. | Not fully confirmed: 433 of 449 eligible tags transposed. Awaiting user decision on (a) which spelling to standardise for the B.001 Tech Services room and (b) whether to stop the formula spilling into blank-column-A rows.
51 | 2026-08-18 | After editing QNL room names in A2:C337 and clearing rows 338 down, asked me to re-run the confirmation check. | Re-ran the full two-way reconciliation of CAR A779:A1229 against the column D spills in 'QNL Room Names with Equip.', then spot-checked row 323 and the cleared tail rows. | 451 tags total, 449 eligible (2 blank-entity: VAV0001 row 931, VAV_B_S13_005 row 1134). All 449 eligible tags now found in column D - 0 missing. The AND vs & mismatch is resolved: A323 now reads entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE and returns its 16 VAVs (VAV_B_S11_003 to _020). The blank-entity leak is gone - column D formulas now stop at row 337 (336 rooms), and A338:E345 verified empty of both values and formulas. 172 of 336 rooms legitimately show 'No Equipment in entity'. | Confirmed. QNL block fully reconciled: 449 of 449 eligible assets transposed, 2 correctly excluded for having no column E value, no spurious spill.
52 | 2026-08-18 | Asked me to redo the validation exercise on the QNL equipment mapping. | Re-ran the two-way reconciliation, found 5 newly added rooms had no formula in column D, and filled D337 down to D338:D342. | Initial re-run showed 16 eligible tags unplaced across 5 entities (L2_992_GULF_MATERIAL, L2_993_CORRIDOR, L1_BC1_BRIDGE_CEILING, L1_BC2_BRIDGE_CEILING, L1_BI_BRIDGE_IDF). Cause was structural, not a name mismatch: rooms were added at rows 338-342 in column A but the TRANSPOSE(FILTER(...)) formula still stopped at row 337. Copied D337 into D338:D342 (destination was empty, no overwrite). Also checked for duplicate CAR tags, duplicate placements, tags landing in the wrong room row, and spill errors - none found. | Resolved. 449 of 449 eligible tags now placed, 0 missing, 0 misplaced, 0 errors. Formula rows in D now 341, matching the 341 rooms in column A. New rows returned 6, 7, 1, 1 and 1 asset respectively.
53 | 2026-08-26 | Uploaded a photo of the QNL Honeywell DX Unit Summary HMI page and asked to copy the room numbers in for the equipment in column A, rows 1230-1253. | Mapped the 24 DX units on the HMI screen to rows 1230-1253 and wrote room numbers into column D (not C - see details). Wrote D1234:D1252 (16 cells); left 3 cells blank with explanatory notes. | User said column C, but C is the 'Included/Not Included' flag column and D is 'ROOM NAME AS PER DRAWINGS' - D1230:D1233 and D1243 already held B.081/B.082 matching the HMI, confirming D is the right target. Mapping: B01/B02=B.081; B03/B04/B14=B.082; B05/B06=B.083; B07/B16=B.095; B08/B09=B.084; B10=B.102; B12/B23=B.107; B13/B15=B.093; B17/B18/B19=B.045A; B20=B.092; B22=B.106. DX_B11 (Basement Zone 5) has no room number on the HMI; DX_B21 and DX_B24 are DX/RP roof units (Zone C) with no room number - notes added instead of values. | Verified by re-reading A1230:D1253 - all 24 rows populated except D1240, D1250, D1253 which are intentionally blank with notes. Column C left untouched.
54 | 2026-08-26 | Supplied a full QNL basement room name/number list and asked to prefix the room names before every room number already in column D, from row 1230 to the end of the QNL section. | Determined QNL section spans rows 1230-1329 (row 1330 = SSC header). Populated names on 24 cells: D1230:D1252 (DX units) and D1301:D1311 (CCU units). Left 8 cells with bare room numbers and added explanatory notes. | Format used: NAME + existing room number, e.g. 'MV ROOM B.081'. Only rows 1230-1253 and 1301-1311 held room numbers within the QNL block; all other QNL rows (HEX, EF, KEF, SEF, TEF, CHW pumps, generator) have empty column D so nothing to prefix. Unresolved: B.083 (rows 1234-1235) and B.045A (rows 1246-1248) do not appear in the supplied list; B.106 (row 1251) and B.141 (rows 1308-1309) each have two candidate names in the list. 'TRANSH CHAMBER B093' interpreted as TRASH CHAMBER. Rows 1240/1250/1253 hold Basement Zone 5 and ROOF ZONE C - no room number, left as-is. | Verified by re-reading A1230:D1253 and A1301:D1311 - 24 cells now carry name + number; 8 flagged with notes pending user confirmation.
55 | 2026-08-27 | User asked to re-run the validation of the QNL room/equipment mapping. | Re-audited 'Controllable Asset Registry' A779:A1329 against column D of 'QNL Room Names with Equip.'. Read-only; no changes made. | Source range in the column D TRANSPOSE(FILTER(...)) formulas has widened since the earlier audit, from A779:A1229 to A779:A1329, and now carries an if_empty argument returning "No Equipment in entity". Rooms in column A run to row 353 (352 entities) with matching formulas in D2:D353. Audited against the widened range: 551 asset tags, 537 with a non-blank column E entity. Also checked CAR rows below 1329 - 271 further assets exist but all carry SSC_ prefixed entities (different building), so ending the range at 1329 is correct and no QNL assets are excluded. | Clean. 537 of 537 eligible assets placed in the correct room row; 0 unplaced, 0 misplaced, 0 orphans, 0 spill errors, no duplicate tags or duplicate room entities. 14 blank-entity assets correctly excluded with no leakage. 154 rooms legitimately show "No Equipment in entity".

## HQ Asset Register
EQUIPMENT ASSET REGISTER
Tag No. | Equipment Type | Description | Remarks
AHU12_0001 | AHU | Air Handling Unit
AHU12_0002 | AHU | Air Handling Unit
AHU12_0003 | AHU | Air Handling Unit
AHU12_0004 | AHU | Air Handling Unit |  | EQUIPMENT COUNT SUMMARY
AHU12_0006 | AHU | Air Handling Unit |  | AHU | 26
AHU12_0007 | AHU | Air Handling Unit |  | FCU | 133
AHU12_0008 | AHU | Air Handling Unit |  | CHW Pump | 4
AHU12_0009 | AHU | Air Handling Unit |  | Variable Air Volume | 602
AHU12_0010 | AHU | Air Handling Unit |  | DX Unit | 24
AHU2_0001 | AHU | Air Handling Unit |  | Heat Exchanger | 5
AHU5_0001 | AHU | Air Handling Unit |  | CCU | 11
AHU5_0002 | AHU | Air Handling Unit |  | EF | 12
AHU9_0001 | AHU | Air Handling Unit |  | GEF | 13
AHU9_0002 | AHU | Air Handling Unit |  | TEF | 4
AHU9_0003 | AHU | Air Handling Unit |  | CEF | 60
AHUB_0001 | AHU | Air Handling Unit |  | SF | 16
AHUB_0002 | AHU | Air Handling Unit |  | Generator | 2
AHUB_0003 | AHU | Air Handling Unit |  | TOTAL | 912
AHUB_0004 | AHU | Air Handling Unit
AHUB_0005 | AHU | Air Handling Unit
AHUB_0006 | AHU | Air Handling Unit
AHUB_0007 | AHU | Air Handling Unit
AHUB_0008 | AHU | Air Handling Unit
AHUB_0009 | AHU | Air Handling Unit
AHUB_0010 | AHU | Air Handling Unit |  | # | Equipment type | Tag(s) in IO list | Assumption
AHUB_0011 | AHU | Air Handling Unit |  | 1 | AHU | AHU12_0010 | These two tags refer to the same physical unit
DX_B0001 | DX Unit | DX Unit - Interior |  |  |  | AHU12_10
DX_B0002 | DX Unit | DX Unit - Interior |  | 2 | AHU | AHUB01_02 | These two tags refer to the same physical unit
DX_B0003 | DX Unit | DX Unit - Interior |  |  |  | AHUB_0002
DX_B0004 | DX Unit | DX Unit - Interior |  | 3 | AHU | AHUB03_04 | These two tags refer to the same physical unit
DX_B0005 | DX Unit | DX Unit - Interior |  |  |  | AHUB_0004
DX_B0006 | DX Unit | DX Unit - Interior |  | 4 | AHU | AHUB05_06 | These two tags refer to the same physical unit
DX_B0007 | DX Unit | DX Unit - Interior |  |  |  | AHUB_0006
DX_B0008 | DX Unit | DX Unit - Interior |  | 5 | AHU | AHUB07 | These two tags refer to the same physical unit
DX_B0009 | DX Unit | DX Unit - Interior |  |  |  | AHUB_0007
DX_B0010 | DX Unit | DX Unit - Interior |  | 6 | AHU | AHUB08 | These two tags refer to the same physical unit
DX_B0011 | DX Unit | DX Unit - Interior |  |  |  | AHUB_0008
DX_B0012 | DX Unit | DX Unit - Interior |  | 7 | AHU | AHUB10 | These two tags refer to the same physical unit
DX_B0013 | DX Unit | DX Unit - Interior |  |  |  | AHUB_0010
DX_B0014 | DX Unit | DX Unit - Interior |  | 8 | AHU | AHUB11 | These two tags refer to the same physical unit
DX_B0015 | DX Unit | DX Unit - Interior |  |  |  | AHUB_0011
DX_B0016 | DX Unit | DX Unit - Interior |  | 9 | DX Unit | DX_ODSB0101 | This DX unit was added later and not reflected in the HVAC Drawing
DX_CP_0001 | DX Unit | DX Unit - Interior |  | 10 | DX Unit | DX_ODSB0102 | This DX unit was added later and not reflected in the HVAC Drawing
DX_G0001 | DX Unit | DX Unit - Interior |  | 11 | DX Unit | DX_ODSB0201 | This DX unit was added later and not reflected in the HVAC Drawing
DX_G0002 | DX Unit | DX Unit - Interior |  | 12 | DX Unit | DX_ODSB0202 | This DX unit was added later and not reflected in the HVAC Drawing
DX_G0003 | DX Unit | DX Unit - Interior |  | 13 | DX Unit | DX_CP_0001 | This DX unit was added later and not reflected in the HVAC Drawing
DX_ODSB0101 | DX Unit | DX Unit - Exterior
DX_ODSB0102 | DX Unit | DX Unit - Exterior
DX_ODSB0201 | DX Unit | DX Unit - Exterior
DX_ODSB0202 | DX Unit | DX Unit - Exterior
FCU0001 | FCU | Fan Coil Unit
FCU0002 | FCU | Fan Coil Unit
FCU0003 | FCU | Fan Coil Unit
FCU0004 | FCU | Fan Coil Unit
FCU0005 | FCU | Fan Coil Unit
FCU0006 | FCU | Fan Coil Unit
FCU0007 | FCU | Fan Coil Unit
FCU0008 | FCU | Fan Coil Unit
FCU0009 | FCU | Fan Coil Unit
FCU0010 | FCU | Fan Coil Unit
FCU0011 | FCU | Fan Coil Unit
FCU0012 | FCU | Fan Coil Unit
FCU0013 | FCU | Fan Coil Unit
FCU00133 | FCU | Fan Coil Unit
FCU0014 | FCU | Fan Coil Unit
FCU0015 | FCU | Fan Coil Unit
FCU0016 | FCU | Fan Coil Unit
FCU0017 | FCU | Fan Coil Unit
FCU0018 | FCU | Fan Coil Unit
FCU0019 | FCU | Fan Coil Unit
FCU0020 | FCU | Fan Coil Unit
FCU0021 | FCU | Fan Coil Unit
FCU0022 | FCU | Fan Coil Unit
FCU0023 | FCU | Fan Coil Unit
FCU0024 | FCU | Fan Coil Unit
FCU0025 | FCU | Fan Coil Unit
FCU0026 | FCU | Fan Coil Unit
FCU0027 | FCU | Fan Coil Unit
FCU0028 | FCU | Fan Coil Unit
FCU0029 | FCU | Fan Coil Unit
FCU0030 | FCU | Fan Coil Unit
FCU0031 | FCU | Fan Coil Unit
FCU0032 | FCU | Fan Coil Unit
FCU0033 | FCU | Fan Coil Unit
FCU0034 | FCU | Fan Coil Unit
FCU0035 | FCU | Fan Coil Unit
FCU0036 | FCU | Fan Coil Unit
FCU0037 | FCU | Fan Coil Unit
FCU0038 | FCU | Fan Coil Unit
FCU0039 | FCU | Fan Coil Unit
FCU0040 | FCU | Fan Coil Unit
FCU0041 | FCU | Fan Coil Unit
FCU0042 | FCU | Fan Coil Unit
FCU0043 | FCU | Fan Coil Unit
FCU0044 | FCU | Fan Coil Unit
FCU0045 | FCU | Fan Coil Unit
FCU0046 | FCU | Fan Coil Unit
FCU0047 | FCU | Fan Coil Unit
FCU0048 | FCU | Fan Coil Unit
FCU0049 | FCU | Fan Coil Unit
FCU0050 | FCU | Fan Coil Unit
FCU0051 | FCU | Fan Coil Unit
FCU0052 | FCU | Fan Coil Unit
FCU0053 | FCU | Fan Coil Unit
FCU0054 | FCU | Fan Coil Unit
FCU0055 | FCU | Fan Coil Unit
FCU0056 | FCU | Fan Coil Unit
FCU0057 | FCU | Fan Coil Unit
FCU0058 | FCU | Fan Coil Unit
FCU0059 | FCU | Fan Coil Unit
FCU0060 | FCU | Fan Coil Unit
FCU0061 | FCU | Fan Coil Unit
FCU0062 | FCU | Fan Coil Unit
FCU0063 | FCU | Fan Coil Unit
FCU0064 | FCU | Fan Coil Unit
FCU0065 | FCU | Fan Coil Unit
FCU0066 | FCU | Fan Coil Unit
FCU0067 | FCU | Fan Coil Unit
FCU0068 | FCU | Fan Coil Unit
FCU0069 | FCU | Fan Coil Unit
FCU0070 | FCU | Fan Coil Unit
FCU0071 | FCU | Fan Coil Unit
FCU0072 | FCU | Fan Coil Unit
FCU0073 | FCU | Fan Coil Unit
FCU0074 | FCU | Fan Coil Unit
FCU0075 | FCU | Fan Coil Unit
FCU0076 | FCU | Fan Coil Unit
FCU0077 | FCU | Fan Coil Unit
FCU0078 | FCU | Fan Coil Unit
FCU0079 | FCU | Fan Coil Unit
FCU0080 | FCU | Fan Coil Unit
FCU0081 | FCU | Fan Coil Unit
FCU0082 | FCU | Fan Coil Unit
FCU0083 | FCU | Fan Coil Unit
FCU0084 | FCU | Fan Coil Unit
FCU0085 | FCU | Fan Coil Unit
FCU0086 | FCU | Fan Coil Unit
FCU0087 | FCU | Fan Coil Unit
FCU0088 | FCU | Fan Coil Unit
FCU0089 | FCU | Fan Coil Unit
FCU0090 | FCU | Fan Coil Unit
FCU0091 | FCU | Fan Coil Unit
FCU0092 | FCU | Fan Coil Unit
FCU0093 | FCU | Fan Coil Unit
FCU0094 | FCU | Fan Coil Unit
FCU0095 | FCU | Fan Coil Unit
FCU0096 | FCU | Fan Coil Unit
FCU0097 | FCU | Fan Coil Unit
FCU0098 | FCU | Fan Coil Unit
FCU0099 | FCU | Fan Coil Unit
FCU0100 | FCU | Fan Coil Unit
FCU0101 | FCU | Fan Coil Unit
FCU0102 | FCU | Fan Coil Unit
FCU0103 | FCU | Fan Coil Unit
FCU0104 | FCU | Fan Coil Unit
FCU0105 | FCU | Fan Coil Unit
FCU0106 | FCU | Fan Coil Unit
FCU0107 | FCU | Fan Coil Unit
FCU0108 | FCU | Fan Coil Unit
FCU0109 | FCU | Fan Coil Unit
FCU0110 | FCU | Fan Coil Unit
FCU0111 | FCU | Fan Coil Unit
FCU0112 | FCU | Fan Coil Unit
FCU0113 | FCU | Fan Coil Unit
FCU0114 | FCU | Fan Coil Unit
FCU0115 | FCU | Fan Coil Unit
FCU0116 | FCU | Fan Coil Unit
FCU0117 | FCU | Fan Coil Unit
FCU0118 | FCU | Fan Coil Unit
FCU0119 | FCU | Fan Coil Unit
FCU0120 | FCU | Fan Coil Unit
FCU0121 | FCU | Fan Coil Unit
FCU0122 | FCU | Fan Coil Unit
FCU0123 | FCU | Fan Coil Unit
FCU0124 | FCU | Fan Coil Unit
FCU0125 | FCU | Fan Coil Unit
FCU0126 | FCU | Fan Coil Unit
FCU0127 | FCU | Fan Coil Unit
FCU0128 | FCU | Fan Coil Unit
FCU0129 | FCU | Fan Coil Unit
FCU0130 | FCU | Fan Coil Unit
FCU0131 | FCU | Fan Coil Unit
FCU0132 | FCU | Fan Coil Unit
HEX01 | HEX | Heat Exchanger
HEX02 | HEX | Heat Exchanger
HEX03 | HEX | Heat Exchanger
HEX04 | HEX | Heat Exchanger
HEX05 | HEX | Heat Exchanger
VAV0001 | VAV | Variable Air Volume
VAV0002 | VAV | Variable Air Volume
VAV0003 | VAV | Variable Air Volume
VAV0004 | VAV | Variable Air Volume
VAV0005 | VAV | Variable Air Volume
VAV0006 | VAV | Variable Air Volume
VAV0007 | VAV | Variable Air Volume
VAV0008 | VAV | Variable Air Volume
VAV0009 | VAV | Variable Air Volume
VAV0011 | VAV | Variable Air Volume
VAV0012 | VAV | Variable Air Volume
VAV0013 | VAV | Variable Air Volume
VAV0014 | VAV | Variable Air Volume
VAV0015 | VAV | Variable Air Volume
VAV0016 | VAV | Variable Air Volume
VAV0017 | VAV | Variable Air Volume
VAV0018 | VAV | Variable Air Volume
VAV0019 | VAV | Variable Air Volume
VAV0020 | VAV | Variable Air Volume
VAV0021 | VAV | Variable Air Volume
VAV0022 | VAV | Variable Air Volume
VAV0023 | VAV | Variable Air Volume
VAV0024 | VAV | Variable Air Volume
VAV0025 | VAV | Variable Air Volume
VAV0026 | VAV | Variable Air Volume
VAV0027 | VAV | Variable Air Volume
VAV0028 | VAV | Variable Air Volume
VAV0029 | VAV | Variable Air Volume
VAV0030 | VAV | Variable Air Volume
VAV0031 | VAV | Variable Air Volume
VAV0032 | VAV | Variable Air Volume
VAV0033 | VAV | Variable Air Volume
VAV0034 | VAV | Variable Air Volume
VAV0035 | VAV | Variable Air Volume
VAV0036 | VAV | Variable Air Volume
VAV0037 | VAV | Variable Air Volume
VAV0038 | VAV | Variable Air Volume
VAV0039 | VAV | Variable Air Volume
VAV0040 | VAV | Variable Air Volume
VAV0041 | VAV | Variable Air Volume
VAV0042 | VAV | Variable Air Volume
VAV0043 | VAV | Variable Air Volume
VAV0044 | VAV | Variable Air Volume
VAV0045 | VAV | Variable Air Volume
VAV0046 | VAV | Variable Air Volume
VAV0047 | VAV | Variable Air Volume
VAV0048 | VAV | Variable Air Volume
VAV0049 | VAV | Variable Air Volume
VAV0050 | VAV | Variable Air Volume
VAV0051 | VAV | Variable Air Volume
VAV0052 | VAV | Variable Air Volume
VAV0053 | VAV | Variable Air Volume
VAV0054 | VAV | Variable Air Volume
VAV0055 | VAV | Variable Air Volume
VAV0056 | VAV | Variable Air Volume
VAV0057 | VAV | Variable Air Volume
VAV0058 | VAV | Variable Air Volume
VAV0059 | VAV | Variable Air Volume
VAV0060 | VAV | Variable Air Volume
VAV0061 | VAV | Variable Air Volume
VAV0062 | VAV | Variable Air Volume
VAV0063 | VAV | Variable Air Volume
VAV0064 | VAV | Variable Air Volume
VAV0065 | VAV | Variable Air Volume
VAV0066 | VAV | Variable Air Volume
VAV0067 | VAV | Variable Air Volume
VAV0068 | VAV | Variable Air Volume
VAV0069 | VAV | Variable Air Volume
VAV0070 | VAV | Variable Air Volume
VAV0071 | VAV | Variable Air Volume
VAV0072 | VAV | Variable Air Volume
VAV0073 | VAV | Variable Air Volume
VAV0074 | VAV | Variable Air Volume
VAV0075 | VAV | Variable Air Volume
VAV0076 | VAV | Variable Air Volume
VAV0077 | VAV | Variable Air Volume
VAV0078 | VAV | Variable Air Volume
VAV0079 | VAV | Variable Air Volume
VAV0080 | VAV | Variable Air Volume
VAV0081 | VAV | Variable Air Volume
VAV0082 | VAV | Variable Air Volume
VAV0083 | VAV | Variable Air Volume
VAV0084 | VAV | Variable Air Volume
VAV0085 | VAV | Variable Air Volume
VAV0086 | VAV | Variable Air Volume
VAV0087 | VAV | Variable Air Volume
VAV0088 | VAV | Variable Air Volume
VAV0089 | VAV | Variable Air Volume
VAV0090 | VAV | Variable Air Volume
VAV0091 | VAV | Variable Air Volume
VAV0092 | VAV | Variable Air Volume
VAV0093 | VAV | Variable Air Volume
VAV0094 | VAV | Variable Air Volume
VAV0095 | VAV | Variable Air Volume
VAV0096 | VAV | Variable Air Volume
VAV0097 | VAV | Variable Air Volume
VAV0098 | VAV | Variable Air Volume
VAV0099 | VAV | Variable Air Volume
VAV0100 | VAV | Variable Air Volume
VAV0101 | VAV | Variable Air Volume
VAV0102 | VAV | Variable Air Volume
VAV0103 | VAV | Variable Air Volume
VAV0104 | VAV | Variable Air Volume
VAV0105 | VAV | Variable Air Volume
VAV0106 | VAV | Variable Air Volume
VAV0107 | VAV | Variable Air Volume
VAV0108 | VAV | Variable Air Volume
VAV0109 | VAV | Variable Air Volume
VAV0110 | VAV | Variable Air Volume
VAV0111 | VAV | Variable Air Volume
VAV0112 | VAV | Variable Air Volume
VAV0113 | VAV | Variable Air Volume
VAV0114 | VAV | Variable Air Volume
VAV0115 | VAV | Variable Air Volume
VAV0116 | VAV | Variable Air Volume
VAV0117 | VAV | Variable Air Volume
VAV0118 | VAV | Variable Air Volume
VAV0119 | VAV | Variable Air Volume
VAV0120 | VAV | Variable Air Volume
VAV0121 | VAV | Variable Air Volume
VAV0122 | VAV | Variable Air Volume
VAV0123 | VAV | Variable Air Volume
VAV0124 | VAV | Variable Air Volume
VAV0125 | VAV | Variable Air Volume
VAV0126 | VAV | Variable Air Volume
VAV0127 | VAV | Variable Air Volume
VAV0128 | VAV | Variable Air Volume
VAV0129 | VAV | Variable Air Volume
VAV0130 | VAV | Variable Air Volume
VAV0131 | VAV | Variable Air Volume
VAV0132 | VAV | Variable Air Volume
VAV0133 | VAV | Variable Air Volume
VAV0134 | VAV | Variable Air Volume
VAV0135 | VAV | Variable Air Volume
VAV0136 | VAV | Variable Air Volume
VAV0137 | VAV | Variable Air Volume
VAV0138 | VAV | Variable Air Volume
VAV0139 | VAV | Variable Air Volume
VAV0140 | VAV | Variable Air Volume
VAV0141 | VAV | Variable Air Volume
VAV0142 | VAV | Variable Air Volume
VAV0143 | VAV | Variable Air Volume
VAV0144 | VAV | Variable Air Volume
VAV0145 | VAV | Variable Air Volume
VAV0146 | VAV | Variable Air Volume
VAV0147 | VAV | Variable Air Volume
VAV0148 | VAV | Variable Air Volume
VAV0149 | VAV | Variable Air Volume
VAV0150 | VAV | Variable Air Volume
VAV0151 | VAV | Variable Air Volume
VAV0152 | VAV | Variable Air Volume
VAV0153 | VAV | Variable Air Volume
VAV0154 | VAV | Variable Air Volume
VAV0155 | VAV | Variable Air Volume
VAV0156 | VAV | Variable Air Volume
VAV0157 | VAV | Variable Air Volume
VAV0158 | VAV | Variable Air Volume
VAV0159 | VAV | Variable Air Volume
VAV0160 | VAV | Variable Air Volume
VAV0161 | VAV | Variable Air Volume
VAV0162 | VAV | Variable Air Volume
VAV0163 | VAV | Variable Air Volume
VAV0164 | VAV | Variable Air Volume
VAV0165 | VAV | Variable Air Volume
VAV0166 | VAV | Variable Air Volume
VAV0167 | VAV | Variable Air Volume
VAV0168 | VAV | Variable Air Volume
VAV0169 | VAV | Variable Air Volume
VAV0170 | VAV | Variable Air Volume
VAV0171 | VAV | Variable Air Volume
VAV0172 | VAV | Variable Air Volume
VAV0173 | VAV | Variable Air Volume
VAV0174 | VAV | Variable Air Volume
VAV0175 | VAV | Variable Air Volume
VAV0176 | VAV | Variable Air Volume
VAV0177 | VAV | Variable Air Volume
VAV0178 | VAV | Variable Air Volume
VAV0179 | VAV | Variable Air Volume
VAV0180 | VAV | Variable Air Volume
VAV0181 | VAV | Variable Air Volume
VAV0182 | VAV | Variable Air Volume
VAV0183 | VAV | Variable Air Volume
VAV0184 | VAV | Variable Air Volume
VAV0185 | VAV | Variable Air Volume
VAV0186 | VAV | Variable Air Volume
VAV0187 | VAV | Variable Air Volume
VAV0188 | VAV | Variable Air Volume
VAV0189 | VAV | Variable Air Volume
VAV0190 | VAV | Variable Air Volume
VAV0191 | VAV | Variable Air Volume
VAV0192 | VAV | Variable Air Volume
VAV0193 | VAV | Variable Air Volume
VAV0194 | VAV | Variable Air Volume
VAV0195 | VAV | Variable Air Volume
VAV0196 | VAV | Variable Air Volume
VAV0197 | VAV | Variable Air Volume
VAV0198 | VAV | Variable Air Volume
VAV0199 | VAV | Variable Air Volume
VAV0200 | VAV | Variable Air Volume
VAV0201 | VAV | Variable Air Volume
VAV0202 | VAV | Variable Air Volume
VAV0203 | VAV | Variable Air Volume
VAV0204 | VAV | Variable Air Volume
VAV0205 | VAV | Variable Air Volume
VAV0206 | VAV | Variable Air Volume
VAV0207 | VAV | Variable Air Volume
VAV0208 | VAV | Variable Air Volume
VAV0209 | VAV | Variable Air Volume
VAV0210 | VAV | Variable Air Volume
VAV0211 | VAV | Variable Air Volume
VAV0212 | VAV | Variable Air Volume
VAV0213 | VAV | Variable Air Volume
VAV0214 | VAV | Variable Air Volume
VAV0215 | VAV | Variable Air Volume
VAV0216 | VAV | Variable Air Volume
VAV0217 | VAV | Variable Air Volume
VAV0218 | VAV | Variable Air Volume
VAV0219 | VAV | Variable Air Volume
VAV0220 | VAV | Variable Air Volume
VAV0221 | VAV | Variable Air Volume
VAV0222 | VAV | Variable Air Volume
VAV0223 | VAV | Variable Air Volume
VAV0224 | VAV | Variable Air Volume
VAV0225 | VAV | Variable Air Volume
VAV0226 | VAV | Variable Air Volume
VAV0227 | VAV | Variable Air Volume
VAV0228 | VAV | Variable Air Volume
VAV0229 | VAV | Variable Air Volume
VAV0230 | VAV | Variable Air Volume
VAV0231 | VAV | Variable Air Volume
VAV0232 | VAV | Variable Air Volume
VAV0233 | VAV | Variable Air Volume
VAV0234 | VAV | Variable Air Volume
VAV0235 | VAV | Variable Air Volume
VAV0236 | VAV | Variable Air Volume
VAV0237 | VAV | Variable Air Volume
VAV0238 | VAV | Variable Air Volume
VAV0239 | VAV | Variable Air Volume
VAV0240 | VAV | Variable Air Volume
VAV0241 | VAV | Variable Air Volume
VAV0242 | VAV | Variable Air Volume
VAV0243 | VAV | Variable Air Volume
VAV0244 | VAV | Variable Air Volume
VAV0245 | VAV | Variable Air Volume
VAV0246 | VAV | Variable Air Volume
VAV0247 | VAV | Variable Air Volume
VAV0248 | VAV | Variable Air Volume
VAV0249 | VAV | Variable Air Volume
VAV0250 | VAV | Variable Air Volume
VAV0251 | VAV | Variable Air Volume
VAV0252 | VAV | Variable Air Volume
VAV0253 | VAV | Variable Air Volume
VAV0254 | VAV | Variable Air Volume
VAV0255 | VAV | Variable Air Volume
VAV0256 | VAV | Variable Air Volume
VAV0257 | VAV | Variable Air Volume
VAV0258 | VAV | Variable Air Volume
VAV0259 | VAV | Variable Air Volume
VAV0260 | VAV | Variable Air Volume
VAV0261 | VAV | Variable Air Volume
VAV0262 | VAV | Variable Air Volume
VAV0263 | VAV | Variable Air Volume
VAV0264 | VAV | Variable Air Volume
VAV0265 | VAV | Variable Air Volume
VAV0266 | VAV | Variable Air Volume
VAV0267 | VAV | Variable Air Volume
VAV0268 | VAV | Variable Air Volume
VAV0269 | VAV | Variable Air Volume
VAV0270 | VAV | Variable Air Volume
VAV0271 | VAV | Variable Air Volume
VAV0272 | VAV | Variable Air Volume
VAV0273 | VAV | Variable Air Volume
VAV0274 | VAV | Variable Air Volume
VAV0275 | VAV | Variable Air Volume
VAV0276 | VAV | Variable Air Volume
VAV0277 | VAV | Variable Air Volume
VAV0278 | VAV | Variable Air Volume
VAV0279 | VAV | Variable Air Volume
VAV0280 | VAV | Variable Air Volume
VAV0281 | VAV | Variable Air Volume
VAV0282 | VAV | Variable Air Volume
VAV0283 | VAV | Variable Air Volume
VAV0284 | VAV | Variable Air Volume
VAV0285 | VAV | Variable Air Volume
VAV0286 | VAV | Variable Air Volume
VAV0287 | VAV | Variable Air Volume
VAV0288 | VAV | Variable Air Volume
VAV0289 | VAV | Variable Air Volume
VAV0290 | VAV | Variable Air Volume
VAV0291 | VAV | Variable Air Volume
VAV0292 | VAV | Variable Air Volume
VAV0293 | VAV | Variable Air Volume
VAV0294 | VAV | Variable Air Volume
VAV0295 | VAV | Variable Air Volume
VAV0296 | VAV | Variable Air Volume
VAV0297 | VAV | Variable Air Volume
VAV0298 | VAV | Variable Air Volume
VAV0299 | VAV | Variable Air Volume
VAV0300 | VAV | Variable Air Volume
VAV0301 | VAV | Variable Air Volume
VAV0302 | VAV | Variable Air Volume
VAV0303 | VAV | Variable Air Volume
VAV0304 | VAV | Variable Air Volume
VAV0305 | VAV | Variable Air Volume
VAV0306 | VAV | Variable Air Volume
VAV0307 | VAV | Variable Air Volume
VAV0308 | VAV | Variable Air Volume
VAV0309 | VAV | Variable Air Volume
VAV0310 | VAV | Variable Air Volume
VAV0311 | VAV | Variable Air Volume
VAV0312 | VAV | Variable Air Volume
VAV0313 | VAV | Variable Air Volume
VAV0314 | VAV | Variable Air Volume
VAV0315 | VAV | Variable Air Volume
VAV0316 | VAV | Variable Air Volume
VAV0317 | VAV | Variable Air Volume
VAV0318 | VAV | Variable Air Volume
VAV0319 | VAV | Variable Air Volume
VAV0320 | VAV | Variable Air Volume
VAV0321 | VAV | Variable Air Volume
VAV0322 | VAV | Variable Air Volume
VAV0323 | VAV | Variable Air Volume
VAV0324 | VAV | Variable Air Volume
VAV0325 | VAV | Variable Air Volume
VAV0326 | VAV | Variable Air Volume
VAV0327 | VAV | Variable Air Volume
VAV0328 | VAV | Variable Air Volume
VAV0329 | VAV | Variable Air Volume
VAV0330 | VAV | Variable Air Volume
VAV0331 | VAV | Variable Air Volume
VAV0332 | VAV | Variable Air Volume
VAV0333 | VAV | Variable Air Volume
VAV0334 | VAV | Variable Air Volume
VAV0335 | VAV | Variable Air Volume
VAV0336 | VAV | Variable Air Volume
VAV0337 | VAV | Variable Air Volume
VAV0338 | VAV | Variable Air Volume
VAV0339 | VAV | Variable Air Volume
VAV0340 | VAV | Variable Air Volume
VAV0341 | VAV | Variable Air Volume
VAV0342 | VAV | Variable Air Volume
VAV0343 | VAV | Variable Air Volume
VAV0344 | VAV | Variable Air Volume
VAV0345 | VAV | Variable Air Volume
VAV0346 | VAV | Variable Air Volume
VAV0347 | VAV | Variable Air Volume
VAV0348 | VAV | Variable Air Volume
VAV0349 | VAV | Variable Air Volume
VAV0350 | VAV | Variable Air Volume
VAV0351 | VAV | Variable Air Volume
VAV0352 | VAV | Variable Air Volume
VAV0353 | VAV | Variable Air Volume
VAV0354 | VAV | Variable Air Volume
VAV0355 | VAV | Variable Air Volume
VAV0356 | VAV | Variable Air Volume
VAV0357 | VAV | Variable Air Volume
VAV0358 | VAV | Variable Air Volume
VAV0359 | VAV | Variable Air Volume
VAV0360 | VAV | Variable Air Volume
VAV0361 | VAV | Variable Air Volume
VAV0362 | VAV | Variable Air Volume
VAV0363 | VAV | Variable Air Volume
VAV0364 | VAV | Variable Air Volume
VAV0365 | VAV | Variable Air Volume
VAV0366 | VAV | Variable Air Volume
VAV0367 | VAV | Variable Air Volume
VAV0368 | VAV | Variable Air Volume
VAV0369 | VAV | Variable Air Volume
VAV0370 | VAV | Variable Air Volume
VAV0371 | VAV | Variable Air Volume
VAV0372 | VAV | Variable Air Volume
VAV0373 | VAV | Variable Air Volume
VAV0374 | VAV | Variable Air Volume
VAV0375 | VAV | Variable Air Volume
VAV0376 | VAV | Variable Air Volume
VAV0377 | VAV | Variable Air Volume
VAV0378 | VAV | Variable Air Volume
VAV0379 | VAV | Variable Air Volume
VAV0380 | VAV | Variable Air Volume
VAV0381 | VAV | Variable Air Volume
VAV0382 | VAV | Variable Air Volume
VAV0383 | VAV | Variable Air Volume
VAV0384 | VAV | Variable Air Volume
VAV0385 | VAV | Variable Air Volume
VAV0386 | VAV | Variable Air Volume
VAV0387 | VAV | Variable Air Volume
VAV0388 | VAV | Variable Air Volume
VAV0389 | VAV | Variable Air Volume
VAV0390 | VAV | Variable Air Volume
VAV0391 | VAV | Variable Air Volume
VAV0392 | VAV | Variable Air Volume
VAV0393 | VAV | Variable Air Volume
VAV0394 | VAV | Variable Air Volume
VAV0395 | VAV | Variable Air Volume
VAV0396 | VAV | Variable Air Volume
VAV0397 | VAV | Variable Air Volume
VAV0398 | VAV | Variable Air Volume
VAV0399 | VAV | Variable Air Volume
VAV0400 | VAV | Variable Air Volume
VAV0401 | VAV | Variable Air Volume
VAV0402 | VAV | Variable Air Volume
VAV0403 | VAV | Variable Air Volume
VAV0404 | VAV | Variable Air Volume
VAV0405 | VAV | Variable Air Volume
VAV0406 | VAV | Variable Air Volume
VAV0407 | VAV | Variable Air Volume
VAV0408 | VAV | Variable Air Volume
VAV0409 | VAV | Variable Air Volume
VAV0410 | VAV | Variable Air Volume
VAV0411 | VAV | Variable Air Volume
VAV0412 | VAV | Variable Air Volume
VAV0413 | VAV | Variable Air Volume
VAV0414 | VAV | Variable Air Volume
VAV0415 | VAV | Variable Air Volume
VAV0416 | VAV | Variable Air Volume
VAV0417 | VAV | Variable Air Volume
VAV0418 | VAV | Variable Air Volume
VAV0419 | VAV | Variable Air Volume
VAV0420 | VAV | Variable Air Volume
VAV0421 | VAV | Variable Air Volume
VAV0422 | VAV | Variable Air Volume
VAV0423 | VAV | Variable Air Volume
VAV0424 | VAV | Variable Air Volume
VAV0425 | VAV | Variable Air Volume
VAV0426 | VAV | Variable Air Volume
VAV0427 | VAV | Variable Air Volume
VAV0428 | VAV | Variable Air Volume
VAV0429 | VAV | Variable Air Volume
VAV0430 | VAV | Variable Air Volume
VAV0431 | VAV | Variable Air Volume
VAV0432 | VAV | Variable Air Volume
VAV0433 | VAV | Variable Air Volume
VAV0434 | VAV | Variable Air Volume
VAV0435 | VAV | Variable Air Volume
VAV0436 | VAV | Variable Air Volume
VAV0437 | VAV | Variable Air Volume
VAV0438 | VAV | Variable Air Volume
VAV0439 | VAV | Variable Air Volume
VAV0440 | VAV | Variable Air Volume
VAV0441 | VAV | Variable Air Volume
VAV0442 | VAV | Variable Air Volume
VAV0443 | VAV | Variable Air Volume
VAV0444 | VAV | Variable Air Volume
VAV0445 | VAV | Variable Air Volume
VAV0446 | VAV | Variable Air Volume
VAV0447 | VAV | Variable Air Volume
VAV0448 | VAV | Variable Air Volume
VAV0449 | VAV | Variable Air Volume
VAV0450 | VAV | Variable Air Volume
VAV0451 | VAV | Variable Air Volume
VAV0452 | VAV | Variable Air Volume
VAV0453 | VAV | Variable Air Volume
VAV0454 | VAV | Variable Air Volume
VAV0455 | VAV | Variable Air Volume
VAV0456 | VAV | Variable Air Volume
VAV0457 | VAV | Variable Air Volume
VAV0458 | VAV | Variable Air Volume
VAV0459 | VAV | Variable Air Volume
VAV0460 | VAV | Variable Air Volume
VAV0461 | VAV | Variable Air Volume
VAV0462 | VAV | Variable Air Volume
VAV0463 | VAV | Variable Air Volume
VAV0464 | VAV | Variable Air Volume
VAV0465 | VAV | Variable Air Volume
VAV0466 | VAV | Variable Air Volume
VAV0467 | VAV | Variable Air Volume
VAV0468 | VAV | Variable Air Volume
VAV0469 | VAV | Variable Air Volume
VAV0470 | VAV | Variable Air Volume
VAV0471 | VAV | Variable Air Volume
VAV0472 | VAV | Variable Air Volume
VAV0473 | VAV | Variable Air Volume
VAV0474 | VAV | Variable Air Volume
VAV0475 | VAV | Variable Air Volume
VAV0476 | VAV | Variable Air Volume
VAV0477 | VAV | Variable Air Volume
VAV0478 | VAV | Variable Air Volume
VAV0479 | VAV | Variable Air Volume
VAV0480 | VAV | Variable Air Volume
VAV0481 | VAV | Variable Air Volume
VAV0482 | VAV | Variable Air Volume
VAV0483 | VAV | Variable Air Volume
VAV0484 | VAV | Variable Air Volume
VAV0485 | VAV | Variable Air Volume
VAV0486 | VAV | Variable Air Volume
VAV0487 | VAV | Variable Air Volume
VAV0488 | VAV | Variable Air Volume
VAV0489 | VAV | Variable Air Volume
VAV0490 | VAV | Variable Air Volume
VAV0491 | VAV | Variable Air Volume
VAV0492 | VAV | Variable Air Volume
VAV0493 | VAV | Variable Air Volume
VAV0494 | VAV | Variable Air Volume
VAV0495 | VAV | Variable Air Volume
VAV0496 | VAV | Variable Air Volume
VAV0497 | VAV | Variable Air Volume
VAV0498 | VAV | Variable Air Volume
VAV0499 | VAV | Variable Air Volume
VAV0500 | VAV | Variable Air Volume
VAV0501 | VAV | Variable Air Volume
VAV0502 | VAV | Variable Air Volume
VAV0503 | VAV | Variable Air Volume
VAV0504 | VAV | Variable Air Volume
VAV0505 | VAV | Variable Air Volume
VAV0506 | VAV | Variable Air Volume
VAV0507 | VAV | Variable Air Volume
VAV0508 | VAV | Variable Air Volume
VAV0509 | VAV | Variable Air Volume
VAV0510 | VAV | Variable Air Volume
VAV0511 | VAV | Variable Air Volume
VAV0512 | VAV | Variable Air Volume
VAV0513 | VAV | Variable Air Volume
VAV0514 | VAV | Variable Air Volume
VAV0515 | VAV | Variable Air Volume
VAV0516 | VAV | Variable Air Volume
VAV0517 | VAV | Variable Air Volume
VAV0518 | VAV | Variable Air Volume
VAV0519 | VAV | Variable Air Volume
VAV0520 | VAV | Variable Air Volume
VAV0521 | VAV | Variable Air Volume
VAV0522 | VAV | Variable Air Volume
VAV0523 | VAV | Variable Air Volume
VAV0524 | VAV | Variable Air Volume
VAV0525 | VAV | Variable Air Volume
VAV0526 | VAV | Variable Air Volume
VAV0527 | VAV | Variable Air Volume
VAV0528 | VAV | Variable Air Volume
VAV0529 | VAV | Variable Air Volume
VAV0530 | VAV | Variable Air Volume
VAV0531 | VAV | Variable Air Volume
VAV0532 | VAV | Variable Air Volume
VAV0533 | VAV | Variable Air Volume
VAV0534 | VAV | Variable Air Volume
VAV0535 | VAV | Variable Air Volume
VAV0536 | VAV | Variable Air Volume
VAV0537 | VAV | Variable Air Volume
VAV0538 | VAV | Variable Air Volume
VAV0539 | VAV | Variable Air Volume
VAV0540 | VAV | Variable Air Volume
VAV0541 | VAV | Variable Air Volume
VAV0542 | VAV | Variable Air Volume
VAV0543 | VAV | Variable Air Volume
VAV0544 | VAV | Variable Air Volume
VAV0545 | VAV | Variable Air Volume
VAV0546 | VAV | Variable Air Volume
VAV0547 | VAV | Variable Air Volume
VAV0548 | VAV | Variable Air Volume
VAV0549 | VAV | Variable Air Volume
VAV0550 | VAV | Variable Air Volume
VAV0551 | VAV | Variable Air Volume
VAV0552 | VAV | Variable Air Volume
VAV0553 | VAV | Variable Air Volume
VAV0554 | VAV | Variable Air Volume
VAV0555 | VAV | Variable Air Volume
VAV0556 | VAV | Variable Air Volume
VAV0557 | VAV | Variable Air Volume
VAV0558 | VAV | Variable Air Volume
VAV0559 | VAV | Variable Air Volume
VAV0560 | VAV | Variable Air Volume
VAV0561 | VAV | Variable Air Volume
VAV0562 | VAV | Variable Air Volume
VAV0564 | VAV | Variable Air Volume
VAV0565 | VAV | Variable Air Volume
VAV0567 | VAV | Variable Air Volume
VAV0568 | VAV | Variable Air Volume
VAV0570 | VAV | Variable Air Volume
VAV0571 | VAV | Variable Air Volume
VAV0573 | VAV | Variable Air Volume
VAV0574 | VAV | Variable Air Volume
VAV0575 | VAV | Variable Air Volume
VAV0576 | VAV | Variable Air Volume
VAV0577 | VAV | Variable Air Volume
VAV0578 | VAV | Variable Air Volume
VAV0579 | VAV | Variable Air Volume
VAV0580 | VAV | Variable Air Volume
VAV0581 | VAV | Variable Air Volume
VAV0582 | VAV | Variable Air Volume
VAV0583 | VAV | Variable Air Volume
VAV0584 | VAV | Variable Air Volume
VAV0585 | VAV | Variable Air Volume
VAV0586 | VAV | Variable Air Volume
VAV0587 | VAV | Variable Air Volume
VAV0588 | VAV | Variable Air Volume
VAV0589 | VAV | Variable Air Volume
VAV0590 | VAV | Variable Air Volume
VAV0591 | VAV | Variable Air Volume
VAV0592 | VAV | Variable Air Volume
VAV0593 | VAV | Variable Air Volume
VAV0594 | VAV | Variable Air Volume
VAV0595 | VAV | Variable Air Volume
VAV0596 | VAV | Variable Air Volume
VAV0597 | VAV | Variable Air Volume
VAV0598 | VAV | Variable Air Volume
VAV0599 | VAV | Variable Air Volume
VAV0600 | VAV | Variable Air Volume
VAV0601 | VAV | Variable Air Volume
VAV0602 | VAV | Variable Air Volume
VAV0603 | VAV | Variable Air Volume
VAV0604 | VAV | Variable Air Volume
VAV0605 | VAV | Variable Air Volume
VAV0606 | VAV | Variable Air Volume
VAV0607 | VAV | Variable Air Volume
CCU_B0001 | CCU | CCU
CCU_B0002 | CCU | CCU
CCU_B0003A | CCU | CCU
CCU_B0003B | CCU | CCU
CCU_B0004A | CCU | CCU
CCU_B0004B | CCU | CCU
CCU_B0005 | CCU | CCU
CCU_B0006 | CCU | CCU
CCU_B0007 | CCU | CCU
CCU_B0008 | CCU | CCU
CCU_B0009 | CCU | CCU
GEF_BF | GEF | GEF
GEF12 | GEF | GEF
GEF12_0005 | GEF | GEF
GEF12_0006 | GEF | GEF
GEF12_0008 | GEF | GEF
GEF12_0009 | GEF | GEF
GEFB_0007 | GEF | GEF
GEFB_0010 | GEF | GEF
GEFB_0011 | GEF | GEF
GEFB_0012 | GEF | GEF
GEFB_0013 | GEF | GEF
GEFB_CP0001 | GEF | GEF
GEFB_CP0002 | GEF | GEF
EF_CommonFireAlm | EF | Exhaust Fan
EF_CommonFireAlm_1 | EF | Exhaust Fan
EF_CommonFireAlm_2 | EF | Exhaust Fan
EF_CPZ1 | EF | Exhaust Fan
EF_CPZ2 | EF | Exhaust Fan
EF_CPZ3 | EF | Exhaust Fan
EF_CPZ4 | EF | Exhaust Fan
EF_CPZ5 | EF | Exhaust Fan
EF_CPZ6 | EF | Exhaust Fan
EF_CPZ7 | EF | Exhaust Fan
EF_CPZ8 | EF | Exhaust Fan
EF_CPZ9 | EF | Exhaust Fan
TEF12_0001 | TEF | TEF
TEF12_0002 | TEF | TEF
TEF12_0003 | TEF | TEF
TEF12_0004 | TEF | TEF
CEF_CPZ1_B01 | CEF | CEF
CEF_CPZ1_B02 | CEF | CEF
CEF_CPZ1_B03 | CEF | CEF
CEF_CPZ1_B04 | CEF | CEF
CEF_CPZ1_B05 | CEF | CEF
CEF_CPZ2_B06 | CEF | CEF
CEF_CPZ2_B07 | CEF | CEF
CEF_CPZ2_B08 | CEF | CEF
CEF_CPZ2_B09 | CEF | CEF
CEF_CPZ2_B10 | CEF | CEF
CEF_CPZ3_B13 | CEF | CEF
CEF_CPZ3_B14 | CEF | CEF
CEF_CPZ3_B15 | CEF | CEF
CEF_CPZ3_B19 | CEF | CEF
CEF_CPZ4_B20 | CEF | CEF
CEF_CPZ4_B22 | CEF | CEF
CEF_CPZ4_B23 | CEF | CEF
CEF_CPZ4_B24 | CEF | CEF
CEF_CPZ5_B21 | CEF | CEF
CEF_CPZ5_B25 | CEF | CEF
CEF_CPZ5_B26 | CEF | CEF
CEF_CPZ5_B27 | CEF | CEF
CEF_CPZ7_B16 | CEF | CEF
CEF_CPZ7_B17 | CEF | CEF
CEF_CPZ7_B18 | CEF | CEF
CEF_CPZ8_B11 | CEF | CEF
CEF_CPZ8_B12 | CEF | CEF
CEF_Zone1 | CEF | CEF
CEF_Zone2 | CEF | CEF
CEF_Zone3 | CEF | CEF
CEF_Zone4 | CEF | CEF
CEF_Zone5 | CEF | CEF
CEF_Zone6_9 | CEF | CEF
CPNL09_CEF_B06 | CEF | CEF
CPNL09_CEF_B07 | CEF | CEF
CPNL09_CEF_B08 | CEF | CEF
CPNL09_CEF_B09 | CEF | CEF
CPNL09_CEF_B10 | CEF | CEF
CPNL09_CEF_B11 | CEF | CEF
CPNL09_CEF_B12 | CEF | CEF
CPNL09_CEF_B13 | CEF | CEF
CPNL09_CEF_B14 | CEF | CEF
CPNL09_CEF_B15 | CEF | CEF
CPNL09_CEF_B16 | CEF | CEF
CPNL09_CEF_B17 | CEF | CEF
CPNL09_CEF_B18 | CEF | CEF
CPNL09_CEF_B19 | CEF | CEF
CSRR10_CEF_B01_INV | CEF | CEF
CSRR10_CEF_B02_INV | CEF | CEF
CSRR10_CEF_B03_INV | CEF | CEF
CSRR10_CEF_B04_INV | CEF | CEF
CSRR10_CEF_B05_INV | CEF | CEF
CSRR9_CEF_B20_INV | CEF | CEF
CSRR9_CEF_B21_INV | CEF | CEF
CSRR9_CEF_B22_INV | CEF | CEF
CSRR9_CEF_B23_INV | CEF | CEF
CSRR9_CEF_B24_INV | CEF | CEF
CSRR9_CEF_B25_INV | CEF | CEF
CSRR9_CEF_B26_INV | CEF | CEF
CSRR9_CEF_B27_INV | CEF | CEF
CHW_CHWP01 | CHW Pump | Chilled Water Pump
CHW_CHWP02 | CHW Pump | Chilled Water Pump
CHW_CHWP03 | CHW Pump | Chilled Water Pump
CHW_CHWP04 | CHW Pump | Chilled Water Pump
SF05_0001A | SF | Fan
SF05_0001B | SF | Fan
SF05_0002A | SF | Fan
SF05_0002B | SF | Fan
SF12_0001A | SF | Fan
SF12_0001B | SF | Fan
SF12_0002A | SF | Fan
SF12_0002B | SF | Fan
SF12_0003A | SF | Fan
SF12_0003B | SF | Fan
SF12_0004A | SF | Fan
SF12_0004B | SF | Fan
SF12_0005A | SF | Fan
SF12_0005B | SF | Fan
SF12_0006A | SF | Fan
SF12_0006B | SF | Fan
ELEC_Gen2 | Generator | Generator
ELEC_Gen3 | Generator | Generator

## QNL Asset Register
EQUIPMENT ASSET REGISTER
Tag No. | Equipment Type | Description | Remarks
AHUB001 | AHU | Air Handling Unit
AHUB002 | AHU | Air Handling Unit
AHUB003 | AHU | Air Handling Unit
AHUB004 | AHU | Air Handling Unit |  | EQUIPMENT COUNT SUMMARY
AHUB005 | AHU | Air Handling Unit |  | AHU | 15
AHUB006 | AHU | Air Handling Unit |  | FCU | 137
AHUB007 | AHU | Air Handling Unit |  | CHW Pump | 6
AHUB008 | AHU | Air Handling Unit |  | Variable Air Volume | 248
AHUB009 | AHU | Air Handling Unit |  | Constant Air Volume | 51
AHUB010 | AHU | Air Handling Unit |  | DX Unit | 24
AHUB011 | AHU | Air Handling Unit |  | Heat Exchanger | 5
AHUB012 | AHU | Air Handling Unit |  | CCU | 22
AHUB013 | AHU | Air Handling Unit |  | EF | 18
AHUB014 | AHU | Air Handling Unit |  | SEF | 12
AHUB015 | AHU | Air Handling Unit |  | TEF | 8
DX_B01 | DX Unit | DX Unit |  | KEF | 4
DX_B02 | DX Unit | DX Unit |  | Generator | 1
DX_B03 | DX Unit | DX Unit |  | TOTAL | 550
DX_B04 | DX Unit | DX Unit
DX_B05 | DX Unit | DX Unit
DX_B06 | DX Unit | DX Unit
DX_B07 | DX Unit | DX Unit |  | # | Equipment type | Tag(s) in IO list | Assumption
DX_B08 | DX Unit | DX Unit |  | 1 | EF | EF_RP001 | This is the same asset as : EF_RP01
DX_B09 | DX Unit | DX Unit |  | 2 | EF | EF_RP002 | This is the same asset as : EF_RP02
DX_B10 | DX Unit | DX Unit |  | 3 | EF | EF_RP003 | This is the same asset as : EF_RP03
DX_B11 | DX Unit | DX Unit |  | 4 | EF | EF_B009 | This is the same asset as : EF_B09
DX_B12 | DX Unit | DX Unit |  | 5 | EF | EF_B011 | This is the same asset as : EF_B11
DX_B13 | DX Unit | DX Unit |  | 6 | DX Unit | DX_B0010 | This is the same asset as : DX_B10
DX_B14 | DX Unit | DX Unit |  | 7 | DX Unit | DX_B0011 | This is the same asset as : DX_B11
DX_B15 | DX Unit | DX Unit |  | 8 | DX Unit | DX_B0012 | This is the same asset as : DX_B12
DX_B16 | DX Unit | DX Unit |  | 9 | DX Unit | DX_B0020 | This is the same asset as : DX_B20
DX_B17 | DX Unit | DX Unit |  | 10 | DX Unit | DX_B022 | This is the same asset as : DX_B21
DX_B18 | DX Unit | DX Unit |  | 11 | DX Unit | DX_B023 | This is the same asset as : DX_B22
DX_B19 | DX Unit | DX Unit |  | 12 | DX Unit | DX_B22 | This DX unit was added later and not reflected in the HVAC Drawing
DX_B20 | DX Unit | DX Unit |  | 13 | DX Unit | DX_B23 | This DX unit was added later and not reflected in the HVAC Drawing
DX_B21 | DX Unit | DX Unit |  | 14 | DX Unit | DX_B24 | This DX unit was added later and not reflected in the HVAC Drawing
DX_B22 | DX Unit | DX Unit | This asset is available in the Local and SWS SCADA but not in the HVAC Drawings | 15 | HEX | HEX05 | This Heat Exchanger was added later and not reflecteed in the HVAC Drawing
DX_B23 | DX Unit | DX Unit | This asset is available in the Local and SWS SCADA but not in the HVAC Drawings | 16 | CCU | CCU_AVServer_Rm | This CCU is available in the Local SCADA but not configures in the SWS
DX_B24 | DX Unit | DX Unit | This asset is available in the Local and SWS SCADA but not in the HVAC Drawings
FCU_1F_001 | FCU | Fan Coil Unit
FCU_1F_002 | FCU | Fan Coil Unit
FCU_1F_003 | FCU | Fan Coil Unit
FCU_1F_004 | FCU | Fan Coil Unit
FCU_1F_005 | FCU | Fan Coil Unit
FCU_1F_006 | FCU | Fan Coil Unit
FCU_1F_007 | FCU | Fan Coil Unit
FCU_1F_008 | FCU | Fan Coil Unit
FCU_1F_009 | FCU | Fan Coil Unit
FCU_1F_010 | FCU | Fan Coil Unit
FCU_1F_011 | FCU | Fan Coil Unit
FCU_1F_012 | FCU | Fan Coil Unit
FCU_1F_013 | FCU | Fan Coil Unit
FCU_1F_014 | FCU | Fan Coil Unit
FCU_1F_015 | FCU | Fan Coil Unit
FCU_1F_016 | FCU | Fan Coil Unit
FCU_1F_017 | FCU | Fan Coil Unit
FCU_1F_018 | FCU | Fan Coil Unit
FCU_1F_019 | FCU | Fan Coil Unit
FCU_1F_020 | FCU | Fan Coil Unit
FCU_1F_021 | FCU | Fan Coil Unit
FCU_1F_022 | FCU | Fan Coil Unit
FCU_1F_023 | FCU | Fan Coil Unit
FCU_1F_024 | FCU | Fan Coil Unit
FCU_1F_025 | FCU | Fan Coil Unit
FCU_1F_026 | FCU | Fan Coil Unit
FCU_1F_027 | FCU | Fan Coil Unit
FCU_1F_028 | FCU | Fan Coil Unit
FCU_1F_029 | FCU | Fan Coil Unit
FCU_1F_030 | FCU | Fan Coil Unit
FCU_1F_031 | FCU | Fan Coil Unit
FCU_1F_032 | FCU | Fan Coil Unit
FCU_1F_033 | FCU | Fan Coil Unit
FCU_1F_034 | FCU | Fan Coil Unit
FCU_1F_035 | FCU | Fan Coil Unit
FCU_1F_036 | FCU | Fan Coil Unit
FCU_1F_037 | FCU | Fan Coil Unit
FCU_1F_038 | FCU | Fan Coil Unit
FCU_1F_039 | FCU | Fan Coil Unit
FCU_1F_040 | FCU | Fan Coil Unit
FCU_1F_041 | FCU | Fan Coil Unit
FCU_1F_042 | FCU | Fan Coil Unit
FCU_1F_043 | FCU | Fan Coil Unit
FCU_1F_044 | FCU | Fan Coil Unit
FCU_1F_045 | FCU | Fan Coil Unit
FCU_1F_046 | FCU | Fan Coil Unit
FCU_1F_047 | FCU | Fan Coil Unit
FCU_1F_048 | FCU | Fan Coil Unit
FCU_1F_049 | FCU | Fan Coil Unit
FCU_1F_050 | FCU | Fan Coil Unit
FCU_1F_051 | FCU | Fan Coil Unit
FCU_1F_052 | FCU | Fan Coil Unit
FCU_1F_053 | FCU | Fan Coil Unit
FCU_1F_054 | FCU | Fan Coil Unit
FCU_1F_055 | FCU | Fan Coil Unit
FCU_1F_056 | FCU | Fan Coil Unit
FCU_1F_057 | FCU | Fan Coil Unit
FCU_1F_058 | FCU | Fan Coil Unit
FCU_1F_059 | FCU | Fan Coil Unit
FCU_1F_060 | FCU | Fan Coil Unit
FCU_1F_061 | FCU | Fan Coil Unit
FCU_1F_062 | FCU | Fan Coil Unit
FCU_1F_063 | FCU | Fan Coil Unit
FCU_1F_064 | FCU | Fan Coil Unit
FCU_1F_065 | FCU | Fan Coil Unit
FCU_2F_001 | FCU | Fan Coil Unit
FCU_2F_002 | FCU | Fan Coil Unit
FCU_2F_003 | FCU | Fan Coil Unit
FCU_2F_004 | FCU | Fan Coil Unit
FCU_2F_005 | FCU | Fan Coil Unit
FCU_2F_034 | FCU | Fan Coil Unit
FCU_2F_035 | FCU | Fan Coil Unit
FCU_2F_036 | FCU | Fan Coil Unit
FCU_2F_037 | FCU | Fan Coil Unit
FCU_2F_038 | FCU | Fan Coil Unit
FCU_2F_039 | FCU | Fan Coil Unit
FCU_2F_040 | FCU | Fan Coil Unit
FCU_2F_041 | FCU | Fan Coil Unit
FCU_2F_042 | FCU | Fan Coil Unit
FCU_2F_043 | FCU | Fan Coil Unit
FCU_2F_044 | FCU | Fan Coil Unit
FCU_2F_045 | FCU | Fan Coil Unit
FCU_2F_046 | FCU | Fan Coil Unit
FCU_2F_047 | FCU | Fan Coil Unit
FCU_2F_048 | FCU | Fan Coil Unit
FCU_2F_049 | FCU | Fan Coil Unit
FCU_2F_050 | FCU | Fan Coil Unit
FCU_2F_051 | FCU | Fan Coil Unit
FCU_2F_052 | FCU | Fan Coil Unit
FCU_2F_053 | FCU | Fan Coil Unit
FCU_2F_054 | FCU | Fan Coil Unit
FCU_2F_055 | FCU | Fan Coil Unit
FCU_2F_056 | FCU | Fan Coil Unit
FCU_2F_057 | FCU | Fan Coil Unit
FCU_2F_058 | FCU | Fan Coil Unit
FCU_2F_059 | FCU | Fan Coil Unit
FCU_2F_060 | FCU | Fan Coil Unit
FCU_2F_061 | FCU | Fan Coil Unit
FCU_2F_062 | FCU | Fan Coil Unit
FCU_B_001 | FCU | Fan Coil Unit
FCU_B_002 | FCU | Fan Coil Unit
FCU_B_003 | FCU | Fan Coil Unit
FCU_B_004 | FCU | Fan Coil Unit
FCU_B_005 | FCU | Fan Coil Unit
FCU_B_006 | FCU | Fan Coil Unit
FCU_B_007 | FCU | Fan Coil Unit
FCU_B_008 | FCU | Fan Coil Unit
FCU_B_009 | FCU | Fan Coil Unit
FCU_B_010 | FCU | Fan Coil Unit
FCU_B_011 | FCU | Fan Coil Unit
FCU_B_012 | FCU | Fan Coil Unit
FCU_B_013 | FCU | Fan Coil Unit
FCU_B_014 | FCU | Fan Coil Unit
FCU_B_015 | FCU | Fan Coil Unit
FCU_B_016 | FCU | Fan Coil Unit
FCU_B_017 | FCU | Fan Coil Unit
FCU_B_018 | FCU | Fan Coil Unit
FCU_B_019 | FCU | Fan Coil Unit
FCU_B_020 | FCU | Fan Coil Unit
FCU_B_021 | FCU | Fan Coil Unit
FCU_B_022 | FCU | Fan Coil Unit
FCU_B_023 | FCU | Fan Coil Unit
FCU_B_024 | FCU | Fan Coil Unit
FCU_B_025 | FCU | Fan Coil Unit
FCU_B_026 | FCU | Fan Coil Unit
FCU_B_027 | FCU | Fan Coil Unit
FCU_B_028 | FCU | Fan Coil Unit
FCU_B_029 | FCU | Fan Coil Unit
FCU_B_030 | FCU | Fan Coil Unit
FCU_B_031 | FCU | Fan Coil Unit
FCU_B_032 | FCU | Fan Coil Unit
FCU_B_033 | FCU | Fan Coil Unit
FCU_B_034 | FCU | Fan Coil Unit
FCU_B_035 | FCU | Fan Coil Unit
FCU_B_036 | FCU | Fan Coil Unit
FCU_B_037 | FCU | Fan Coil Unit
FCU_B_038 | FCU | Fan Coil Unit
HEX01 | HEX | Heat Exchanger
HEX02 | HEX | Heat Exchanger
HEX03 | HEX | Heat Exchanger
HEX04 | HEX | Heat Exchanger
HEX05 | HEX | Heat Exchanger | This asset is available in the Local and SWS SCADA but not in the HVAC Drawings
VAV0001 | VAV | Variable Air Volume
VAV_1F_S11_001 | VAV | Variable Air Volume
VAV_1F_S11_002 | VAV | Variable Air Volume
VAV_1F_S11_003 | VAV | Variable Air Volume
VAV_1F_S11_004 | VAV | Variable Air Volume
VAV_1F_S11_005 | VAV | Variable Air Volume
VAV_1F_S11_006 | VAV | Variable Air Volume
VAV_1F_S11_007 | VAV | Variable Air Volume
VAV_1F_S11_008 | VAV | Variable Air Volume
VAV_1F_S11_009 | VAV | Variable Air Volume
VAV_1F_S11_010 | VAV | Variable Air Volume
VAV_1F_S11_011 | VAV | Variable Air Volume
VAV_1F_S11_012 | VAV | Variable Air Volume
VAV_1F_S11_013 | VAV | Variable Air Volume
VAV_1F_S11_014 | VAV | Variable Air Volume
VAV_1F_S11_015 | VAV | Variable Air Volume
VAV_1F_S11_016 | VAV | Variable Air Volume
VAV_1F_S11_017 | VAV | Variable Air Volume
VAV_1F_S11_018 | VAV | Variable Air Volume
VAV_1F_S11_019 | VAV | Variable Air Volume
VAV_1F_S11_020 | VAV | Variable Air Volume
VAV_1F_S11_021 | VAV | Variable Air Volume
VAV_1F_S11_022 | VAV | Variable Air Volume
VAV_1F_S11_087 | VAV | Variable Air Volume
VAV_1F_S11_088 | VAV | Variable Air Volume
VAV_1F_S11_089 | VAV | Variable Air Volume
VAV_1F_S11_090 | VAV | Variable Air Volume
VAV_1F_S15_001 | VAV | Variable Air Volume
VAV_1F_S15_002 | VAV | Variable Air Volume
VAV_1F_S15_003 | VAV | Variable Air Volume
VAV_1F_S15_004 | VAV | Variable Air Volume
VAV_1F_S15_005 | VAV | Variable Air Volume
VAV_1F_S15_006 | VAV | Variable Air Volume
VAV_1F_S15_007 | VAV | Variable Air Volume
VAV_1F_S15_008 | VAV | Variable Air Volume
VAV_1F_S15_009 | VAV | Variable Air Volume
VAV_1F_S15_010 | VAV | Variable Air Volume
VAV_1F_S15_011 | VAV | Variable Air Volume
VAV_1F_S15_012 | VAV | Variable Air Volume
VAV_1F_S15_021 | VAV | Variable Air Volume
VAV_1F_S15_022 | VAV | Variable Air Volume
VAV_1F_S15_023 | VAV | Variable Air Volume
VAV_1F_S15_024 | VAV | Variable Air Volume
VAV_1F_S15_025 | VAV | Variable Air Volume
VAV_1F_S15_038 | VAV | Variable Air Volume
VAV_1F_S15_039 | VAV | Variable Air Volume
VAV_1F_S15_039S | VAV | Variable Air Volume
VAV_1F_S15_040 | VAV | Variable Air Volume
VAV_1F_S15_096 | VAV | Variable Air Volume
VAV_1F_S15_097 | VAV | Variable Air Volume
VAV_1F_S15_098 | VAV | Variable Air Volume
VAV_2F_S10_001 | VAV | Variable Air Volume
VAV_2F_S10_002 | VAV | Variable Air Volume
VAV_2F_S10_003 | VAV | Variable Air Volume
VAV_2F_S10_004 | VAV | Variable Air Volume
VAV_2F_S10_005 | VAV | Variable Air Volume
VAV_2F_S10_006 | VAV | Variable Air Volume
VAV_2F_S12_001 | VAV | Variable Air Volume
VAV_2F_S12_002 | VAV | Variable Air Volume
VAV_2F_S12_003 | VAV | Variable Air Volume
VAV_2F_S12_004 | VAV | Variable Air Volume
VAV_2F_S12_005 | VAV | Variable Air Volume
VAV_2F_S12_006 | VAV | Variable Air Volume
VAV_2F_S12_007 | VAV | Variable Air Volume
VAV_2F_S12_008 | VAV | Variable Air Volume
VAV_2F_S12_009 | VAV | Variable Air Volume
VAV_2F_S12_010 | VAV | Variable Air Volume
VAV_2F_S12_011 | VAV | Variable Air Volume
VAV_2F_S12_012 | VAV | Variable Air Volume
VAV_2F_S12_013 | VAV | Variable Air Volume
VAV_2F_S12_014 | VAV | Variable Air Volume
VAV_2F_S12_015 | VAV | Variable Air Volume
VAV_2F_S12_016 | VAV | Variable Air Volume
VAV_2F_S12_017 | VAV | Variable Air Volume
VAV_2F_S12_018 | VAV | Variable Air Volume
VAV_2F_S12_019 | VAV | Variable Air Volume
VAV_2F_S12_020 | VAV | Variable Air Volume
VAV_2F_S12_021 | VAV | Variable Air Volume
VAV_2F_S12_022 | VAV | Variable Air Volume
VAV_2F_S12_023 | VAV | Variable Air Volume
VAV_2F_S12_024 | VAV | Variable Air Volume
VAV_2F_S12_025 | VAV | Variable Air Volume
VAV_2F_S12_026 | VAV | Variable Air Volume
VAV_2F_S12_027 | VAV | Variable Air Volume
VAV_2F_S12_028 | VAV | Variable Air Volume
VAV_2F_S12_029 | VAV | Variable Air Volume
VAV_2F_S12_097 | VAV | Variable Air Volume
VAV_2F_S13_001 | VAV | Variable Air Volume
VAV_2F_S13_002 | VAV | Variable Air Volume
VAV_2F_S13_003 | VAV | Variable Air Volume
VAV_2F_S13_004 | VAV | Variable Air Volume
VAV_2F_S13_005 | VAV | Variable Air Volume
VAV_2F_S13_006 | VAV | Variable Air Volume
VAV_2F_S13_007 | VAV | Variable Air Volume
VAV_2F_S13_008 | VAV | Variable Air Volume
VAV_2F_S13_009 | VAV | Variable Air Volume
VAV_2F_S13_010 | VAV | Variable Air Volume
VAV_2F_S13_011 | VAV | Variable Air Volume
VAV_2F_S13_012 | VAV | Variable Air Volume
VAV_2F_S13_013 | VAV | Variable Air Volume
VAV_2F_S13_014 | VAV | Variable Air Volume
VAV_2F_S13_015 | VAV | Variable Air Volume
VAV_2F_S13_016 | VAV | Variable Air Volume
VAV_2F_S14_001 | VAV | Variable Air Volume
VAV_2F_S14_002 | VAV | Variable Air Volume
VAV_2F_S14_003 | VAV | Variable Air Volume
VAV_2F_S14_004 | VAV | Variable Air Volume
VAV_2F_S14_005 | VAV | Variable Air Volume
VAV_2F_S14_006 | VAV | Variable Air Volume
VAV_2F_S14_007 | VAV | Variable Air Volume
VAV_2F_S14_008 | VAV | Variable Air Volume
VAV_2F_S14_009 | VAV | Variable Air Volume
VAV_2F_S14_010 | VAV | Variable Air Volume
VAV_2F_S14_011 | VAV | Variable Air Volume
VAV_2F_S14_012 | VAV | Variable Air Volume
VAV_2F_S14_013 | VAV | Variable Air Volume
VAV_2F_S14_014 | VAV | Variable Air Volume
VAV_2F_S14_015 | VAV | Variable Air Volume
VAV_2F_S14_016 | VAV | Variable Air Volume
VAV_2F_S14_017 | VAV | Variable Air Volume
VAV_2F_S14_018 | VAV | Variable Air Volume
VAV_2F_S14_019 | VAV | Variable Air Volume
VAV_2F_S14_020 | VAV | Variable Air Volume
VAV_2F_S14_021 | VAV | Variable Air Volume
VAV_2F_S15_001 | VAV | Variable Air Volume
VAV_2F_S15_002 | VAV | Variable Air Volume
VAV_2F_S15_003 | VAV | Variable Air Volume
VAV_2F_S15_004 | VAV | Variable Air Volume
VAV_2F_S15_005 | VAV | Variable Air Volume
VAV_B_S10_001 | VAV | Variable Air Volume
VAV_B_S10_002 | VAV | Variable Air Volume
VAV_B_S10_003 | VAV | Variable Air Volume
VAV_B_S10_004 | VAV | Variable Air Volume
VAV_B_S10_005 | VAV | Variable Air Volume
VAV_B_S10_006 | VAV | Variable Air Volume
VAV_B_S10_007 | VAV | Variable Air Volume
VAV_B_S10_008 | VAV | Variable Air Volume
VAV_B_S10_009 | VAV | Variable Air Volume
VAV_B_S10_010 | VAV | Variable Air Volume
VAV_B_S10_011 | VAV | Variable Air Volume
VAV_B_S10_012 | VAV | Variable Air Volume
VAV_B_S10_013 | VAV | Variable Air Volume
VAV_B_S10_014 | VAV | Variable Air Volume
VAV_B_S10_015 | VAV | Variable Air Volume
VAV_B_S10_016 | VAV | Variable Air Volume
VAV_B_S10_017 | VAV | Variable Air Volume
VAV_B_S10_018 | VAV | Variable Air Volume
VAV_B_S10_019 | VAV | Variable Air Volume
VAV_B_S10_020 | VAV | Variable Air Volume
VAV_B_S10_021 | VAV | Variable Air Volume
VAV_B_S10_022 | VAV | Variable Air Volume
VAV_B_S10_023 | VAV | Variable Air Volume
VAV_B_S10_024 | VAV | Variable Air Volume
VAV_B_S11_001 | VAV | Variable Air Volume
VAV_B_S11_002 | VAV | Variable Air Volume
VAV_B_S11_003 | VAV | Variable Air Volume
VAV_B_S11_004 | VAV | Variable Air Volume
VAV_B_S11_005 | VAV | Variable Air Volume
VAV_B_S11_006 | VAV | Variable Air Volume
VAV_B_S11_007 | VAV | Variable Air Volume
VAV_B_S11_008 | VAV | Variable Air Volume
VAV_B_S11_009 | VAV | Variable Air Volume
VAV_B_S11_010 | VAV | Variable Air Volume
VAV_B_S11_011 | VAV | Variable Air Volume
VAV_B_S11_012 | VAV | Variable Air Volume
VAV_B_S11_013 | VAV | Variable Air Volume
VAV_B_S11_014 | VAV | Variable Air Volume
VAV_B_S11_015 | VAV | Variable Air Volume
VAV_B_S11_016 | VAV | Variable Air Volume
VAV_B_S11_017 | VAV | Variable Air Volume
VAV_B_S11_018 | VAV | Variable Air Volume
VAV_B_S11_019 | VAV | Variable Air Volume
VAV_B_S11_020 | VAV | Variable Air Volume
VAV_B_S11_021 | VAV | Variable Air Volume
VAV_B_S11_022 | VAV | Variable Air Volume
VAV_B_S11_023 | VAV | Variable Air Volume
VAV_B_S11_024 | VAV | Variable Air Volume
VAV_B_S11_025 | VAV | Variable Air Volume
VAV_B_S11_026 | VAV | Variable Air Volume
VAV_B_S11_027 | VAV | Variable Air Volume
VAV_B_S11_028 | VAV | Variable Air Volume
VAV_B_S11_029 | VAV | Variable Air Volume
VAV_B_S11_030 | VAV | Variable Air Volume
VAV_B_S11_031 | VAV | Variable Air Volume
VAV_B_S11_032 | VAV | Variable Air Volume
VAV_B_S11_033 | VAV | Variable Air Volume
VAV_B_S11_034 | VAV | Variable Air Volume
VAV_B_S11_035 | VAV | Variable Air Volume
VAV_B_S11_036 | VAV | Variable Air Volume
VAV_B_S11_037 | VAV | Variable Air Volume
VAV_B_S11_038 | VAV | Variable Air Volume
VAV_B_S11_039 | VAV | Variable Air Volume
VAV_B_S11_040 | VAV | Variable Air Volume
VAV_B_S11_041 | VAV | Variable Air Volume
VAV_B_S11_042 | VAV | Variable Air Volume
VAV_B_S11_043 | VAV | Variable Air Volume
VAV_B_S11_044 | VAV | Variable Air Volume
VAV_B_S11_045 | VAV | Variable Air Volume
VAV_B_S11_046 | VAV | Variable Air Volume
VAV_B_S13_001 | VAV | Variable Air Volume
VAV_B_S13_002 | VAV | Variable Air Volume
VAV_B_S13_003 | VAV | Variable Air Volume
VAV_B_S13_004 | VAV | Variable Air Volume
VAV_B_S13_005 | VAV | Variable Air Volume
VAV_B_S13_006 | VAV | Variable Air Volume
VAV_B_S13_007 | VAV | Variable Air Volume
VAV_B_S13_008 | VAV | Variable Air Volume
VAV_B_S14_001 | VAV | Variable Air Volume
VAV_B_S14_002 | VAV | Variable Air Volume
VAV_B_S14_003 | VAV | Variable Air Volume
VAV_B_S14_004 | VAV | Variable Air Volume
VAV_B_S14_005 | VAV | Variable Air Volume
VAV_B_S14_006 | VAV | Variable Air Volume
VAV_B_S14_007 | VAV | Variable Air Volume
VAV_B_S14_008 | VAV | Variable Air Volume
VAV_B_S14_009 | VAV | Variable Air Volume
VAV_B_S14_010 | VAV | Variable Air Volume
VAV_B_S14_011 | VAV | Variable Air Volume
VAV_B_S14_012 | VAV | Variable Air Volume
VAV_B_S14_013 | VAV | Variable Air Volume
VAV_B_S14_014 | VAV | Variable Air Volume
VAV_B_S14_015 | VAV | Variable Air Volume
VAV_B_S14_016 | VAV | Variable Air Volume
VAV_B_S14_040 | VAV | Variable Air Volume
VAV_B_S14_041 | VAV | Variable Air Volume
VAV_B_S14_042 | VAV | Variable Air Volume
VAV_B_S14_043 | VAV | Variable Air Volume
VAV_B_S14_044 | VAV | Variable Air Volume
VAV_B_S14_045 | VAV | Variable Air Volume
VAV_B_S14_046 | VAV | Variable Air Volume
VAV_B_S14_047 | VAV | Variable Air Volume
VAV_B_S14_048 | VAV | Variable Air Volume
VAV_B_S14_049 | VAV | Variable Air Volume
VAV_B_S14_050 | VAV | Variable Air Volume
VAV_B_S14_051 | VAV | Variable Air Volume
VAV_B_S15_001 | VAV | Variable Air Volume
VAV_B_S15_002 | VAV | Variable Air Volume
VAV_B_S15_003 | VAV | Variable Air Volume
VAV_B_S15_004 | VAV | Variable Air Volume
VAV_B_S15_005 | VAV | Variable Air Volume
VAV_B_S15_006 | VAV | Variable Air Volume
VAV_B_S15_007 | VAV | Variable Air Volume
VAV_B_S15_008 | VAV | Variable Air Volume
VAV_B_S15_009 | VAV | Variable Air Volume
VAV_B_S15_010 | VAV | Variable Air Volume
VAV_B_S15_011 | VAV | Variable Air Volume
VAV_B_S15_012 | VAV | Variable Air Volume
VAV_B_S15_013 | VAV | Variable Air Volume
CAV_1F_S11_001 | CAV | Constant Air Volume
CAV_1F_S11_002 | CAV | Constant Air Volume
CAV_1F_S11_006 | CAV | Constant Air Volume
CAV_1F_S11_007 | CAV | Constant Air Volume
CAV_1F_S11_008 | CAV | Constant Air Volume
CAV_1F_S11_009 | CAV | Constant Air Volume
CAV_1F_S15_001 | CAV | Constant Air Volume
CAV_1F_S15_002 | CAV | Constant Air Volume
CAV_1F_S15_004 | CAV | Constant Air Volume
CAV_1F_S15_005 | CAV | Constant Air Volume
CAV_1F_S15_006 | CAV | Constant Air Volume
CAV_1F_S15_010 | CAV | Constant Air Volume
CAV_1F_S15_011 | CAV | Constant Air Volume
CAV_1F_S15_012 | CAV | Constant Air Volume
CAV_1F_S15_013 | CAV | Constant Air Volume
CAV_1F_S15_014 | CAV | Constant Air Volume
CAV_1F_S15_015 | CAV | Constant Air Volume
CAV_1F_S15_016 | CAV | Constant Air Volume
CAV_1F_S15_017 | CAV | Constant Air Volume
CAV_1F_S15_018 | CAV | Constant Air Volume
CAV_1F_S15_019 | CAV | Constant Air Volume
CAV_B_S12_001 | CAV | Constant Air Volume
CAV_B_S12_002 | CAV | Constant Air Volume
CAV_B_S12_003 | CAV | Constant Air Volume
CAV_B_S13_001 | CAV | Constant Air Volume
CAV_B_S13_002 | CAV | Constant Air Volume
CAV_B_S13_003 | CAV | Constant Air Volume
CAV_B_S13_004 | CAV | Constant Air Volume
CAV_B_S13_005 | CAV | Constant Air Volume
CAV_B_S13_006 | CAV | Constant Air Volume
CAV_B_S13_007 | CAV | Constant Air Volume
CAV_B_S13_008 | CAV | Constant Air Volume
CAV_B_S13_009 | CAV | Constant Air Volume
CAV_B_S13_010 | CAV | Constant Air Volume
CAV_B_S13_011 | CAV | Constant Air Volume
CAV_B_S13_012 | CAV | Constant Air Volume
CAV_B_S13_013 | CAV | Constant Air Volume
CAV_B_S13_014 | CAV | Constant Air Volume
CAV_B_S13_015 | CAV | Constant Air Volume
CAV_B_S13_020 | CAV | Constant Air Volume
CAV_B_S13_021 | CAV | Constant Air Volume
CAV_B_S14_001 | CAV | Constant Air Volume
CAV_B_S14_002 | CAV | Constant Air Volume
CAV_B_S14_003 | CAV | Constant Air Volume
CAV_B_S14_004 | CAV | Constant Air Volume
CAV_B_S14_005 | CAV | Constant Air Volume
CAV_B_S14_006 | CAV | Constant Air Volume
CAV_B_S14_007 | CAV | Constant Air Volume
CAV_B_S15_001 | CAV | Constant Air Volume
CAV_B_S15_002 | CAV | Constant Air Volume
CAV_B_S15_003 | CAV | Constant Air Volume
EF_201 | EF | EF
EF_B05 | EF | EF
EF_B06 | EF | EF
EF_B07 | EF | EF
EF_B08 | EF | EF
EF_B09 | EF | EF
EF_B10 | EF | EF
EF_B11 | EF | EF
EF_B12 | EF | EF
EF_B13 | EF | EF
EF_B14 | EF | EF
EF_B15 | EF | EF
EF_B16 | EF | EF
EF_BBV01 | EF | EF
EF_BBV02 | EF | EF
EF_RP01 | EF | EF
EF_RP02 | EF | EF
EF_RP03 | EF | EF
KEF_101 | KEF | KEF
KEF_B019 | KEF | KEF
KEF_B020 | KEF | KEF
KEF_B04 | KEF | KEF
SEF_RP04 | SEF | SEF
SEF_RP05 | SEF | SEF
SEF_RP06 | SEF | SEF
SEF_RP07 | SEF | SEF
SEF_RP08 | SEF | SEF
SEF_RP09 | SEF | SEF
SEF_RP10 | SEF | SEF
SEF_RP11 | SEF | SEF
SEF_RP12 | SEF | SEF
SEF_ZoneA | SEF | SEF
SEF_ZoneB | SEF | SEF
SEF_ZoneC | SEF | SEF
TEF_101C | TEF | TEF
TEF_102C | TEF | TEF
TEF_B01A | TEF | TEF
TEF_B01B | TEF | TEF
TEF_B02A | TEF | TEF
TEF_B02B | TEF | TEF
TEF_B03A | TEF | TEF
TEF_B03B | TEF | TEF
CCU_B01 | CCU | CCU
CCU_B02 | CCU | CCU
CCU_B03 | CCU | CCU
CCU_B04 | CCU | CCU
CCU_B05 | CCU | CCU
CCU_B06 | CCU | CCU
CCU_B07 | CCU | CCU
CCU_B08 | CCU | CCU
CCU_B09 | CCU | CCU
CCU_B10 | CCU | CCU
CCU_B11 | CCU | CCU
CCU_8081 | CCU | CCU
CCU_8082 | CCU | CCU
CCU_8083 | CCU | CCU
CCU_8084 | CCU | CCU
CCU_8085 | CCU | CCU
CCU_8086 | CCU | CCU
CCU_MDFRm | CCU | CCU
CCU_Qtel | CCU | CCU
CCU_Server_Rm | CCU | CCU
CCU_AVServer_Rm | CCU | CCU | This Asset is available in Local SCADA but not in SWS (Historian)
CCU_HeritageVault | CCU | CCU
CHW_P01 | CHW Pump | Primary CHW Pumps
CHW_P02 | CHW Pump | Primary CHW Pumps
CHW_P03 | CHW Pump | Primary CHW Pumps
CHW_P04 | CHW Pump | Primary CHW Pumps
CHWPU_P01 | CHW Pump | Chilled Water Pressurization Unit Pump
CHWPU_P02 | CHW Pump | Chilled Water Pressurization Unit Pump
ELEC_Gen | Generator | Generator

## SSC Asset Register
EQUIPMENT ASSET REGISTER
Tag No. | Equipment Type | Description | Remarks
AHUB_0001 | AHU | Air Handling Unit
AHUB_0002 | AHU | Air Handling Unit
AHUB_0003 | AHU | Air Handling Unit
AHUB_0004 | AHU | Air Handling Unit |  | EQUIPMENT COUNT SUMMARY
AHUB_0005 | AHU | Air Handling Unit |  | AHU | 5
FCU0001 | FCU | Fan Coil Unit |  | FCU | 11
FCU0002 | FCU | Fan Coil Unit |  | CHW Pump | 8
FCU0003 | FCU | Fan Coil Unit |  | Variable Air Volume | 108
FCU0004 | FCU | Fan Coil Unit |  | DX Unit | 10
FCU0005 | FCU | Fan Coil Unit |  | Heat Exchanger | 5
FCU0006 | FCU | Fan Coil Unit |  | CCU | 14
FCU0007 | FCU | Fan Coil Unit |  | EF | 1
FCU0008 | FCU | Fan Coil Unit |  | KEF | 2
FCU0009 | FCU | Fan Coil Unit |  | TEF | 4
FCU0010 | FCU | Fan Coil Unit |  | GEF | 1
FCU0011 | FCU | Fan Coil Unit |  | Generator | 1
VAV0001 | VAV | Variable Air Volume |  | TOTAL | 170
VAV0002 | VAV | Variable Air Volume
VAV0003 | VAV | Variable Air Volume
VAV0004 | VAV | Variable Air Volume
VAV0005 | VAV | Variable Air Volume
VAV0006 | VAV | Variable Air Volume
VAV0007 | VAV | Variable Air Volume
VAV0008 | VAV | Variable Air Volume |  | # | Equipment type | Tag(s) in IO list | Assumption
VAV0009 | VAV | Variable Air Volume |  | 1 | DX Unit | DX/B/11 | This DX unit is not available in I/O (Local and SWS) but available in the drawings
VAV0010 | VAV | Variable Air Volume |  | 2 | DX Unit | DX/B/12 | This DX unit is not available in I/O (Local and SWS) but available in the drawings
VAV0011 | VAV | Variable Air Volume |  | 3 | DX Unit | DX/B/13 | This DX unit is not available in I/O (Local and SWS) but available in the drawings
VAV0012 | VAV | Variable Air Volume |  | 4 | DX Unit | DX/B/14 | This DX unit is not available in I/O (Local and SWS) but available in the drawings
VAV0013 | VAV | Variable Air Volume |  | 5 | DX Unit | DX/B/15 | This DX unit is not available in I/O (Local and SWS) but available in the drawings
VAV0014 | VAV | Variable Air Volume |  | 6 | DX Unit | DX/B/16 | This DX unit is not available in I/O (Local and SWS) but available in the drawings
VAV0015 | VAV | Variable Air Volume |  | 7 | DX Unit | DX/1/01 | This DX unit is not available in I/O (Local and SWS) but available in the drawings
VAV0016 | VAV | Variable Air Volume |  | 8 | DX Unit | DX/1/02 | This DX unit is not available in I/O (Local and SWS) but available in the drawings
VAV0017 | VAV | Variable Air Volume |  | 9 | DX Unit | DX/1/03 | This DX unit is not available in I/O (Local and SWS) but available in the drawings
VAV0018 | VAV | Variable Air Volume
VAV0019 | VAV | Variable Air Volume
VAV0020 | VAV | Variable Air Volume
VAV0021 | VAV | Variable Air Volume
VAV0022 | VAV | Variable Air Volume
VAV0023 | VAV | Variable Air Volume
VAV0024 | VAV | Variable Air Volume
VAV0025 | VAV | Variable Air Volume
VAV0026 | VAV | Variable Air Volume
VAV0027 | VAV | Variable Air Volume
VAV0028 | VAV | Variable Air Volume
VAV0029 | VAV | Variable Air Volume
VAV0030 | VAV | Variable Air Volume
VAV0031 | VAV | Variable Air Volume
VAV0032 | VAV | Variable Air Volume
VAV0033 | VAV | Variable Air Volume
VAV0034 | VAV | Variable Air Volume
VAV0035 | VAV | Variable Air Volume
VAV0036 | VAV | Variable Air Volume
VAV0037 | VAV | Variable Air Volume
VAV0038 | VAV | Variable Air Volume
VAV0039 | VAV | Variable Air Volume
VAV0040 | VAV | Variable Air Volume
VAV0041 | VAV | Variable Air Volume
VAV0042 | VAV | Variable Air Volume
VAV0043 | VAV | Variable Air Volume
VAV0044 | VAV | Variable Air Volume
VAV0045 | VAV | Variable Air Volume
VAV0046 | VAV | Variable Air Volume
VAV0047 | VAV | Variable Air Volume
VAV0048 | VAV | Variable Air Volume
VAV0049 | VAV | Variable Air Volume
VAV0050 | VAV | Variable Air Volume
VAV0051 | VAV | Variable Air Volume
VAV0052 | VAV | Variable Air Volume
VAV0053 | VAV | Variable Air Volume
VAV0054 | VAV | Variable Air Volume
VAV0055 | VAV | Variable Air Volume
VAV0056 | VAV | Variable Air Volume
VAV0057 | VAV | Variable Air Volume
VAV0058 | VAV | Variable Air Volume
VAV0059 | VAV | Variable Air Volume
VAV0060 | VAV | Variable Air Volume
VAV0061 | VAV | Variable Air Volume
VAV0062 | VAV | Variable Air Volume
VAV0063 | VAV | Variable Air Volume
VAV0064 | VAV | Variable Air Volume
VAV0065 | VAV | Variable Air Volume
VAV0066 | VAV | Variable Air Volume
VAV0067 | VAV | Variable Air Volume
VAV0068 | VAV | Variable Air Volume
VAV0069 | VAV | Variable Air Volume
VAV0070 | VAV | Variable Air Volume
VAV0071 | VAV | Variable Air Volume
VAV0072 | VAV | Variable Air Volume
VAV0073 | VAV | Variable Air Volume
VAV0074 | VAV | Variable Air Volume
VAV0075 | VAV | Variable Air Volume
VAV0076 | VAV | Variable Air Volume
VAV0077 | VAV | Variable Air Volume
VAV0078 | VAV | Variable Air Volume
VAV0079 | VAV | Variable Air Volume
VAV0080 | VAV | Variable Air Volume
VAV0081 | VAV | Variable Air Volume
VAV0082 | VAV | Variable Air Volume
VAV0083 | VAV | Variable Air Volume
VAV0084 | VAV | Variable Air Volume
VAV0085 | VAV | Variable Air Volume
VAV0086 | VAV | Variable Air Volume
VAV0087 | VAV | Variable Air Volume
VAV0088 | VAV | Variable Air Volume
VAV0089 | VAV | Variable Air Volume
VAV0090 | VAV | Variable Air Volume
VAV0091 | VAV | Variable Air Volume
VAV0092 | VAV | Variable Air Volume
VAV0093 | VAV | Variable Air Volume
VAV0094 | VAV | Variable Air Volume
VAV0095 | VAV | Variable Air Volume
VAV0096 | VAV | Variable Air Volume
VAV0097 | VAV | Variable Air Volume
VAV0098 | VAV | Variable Air Volume
VAV0099 | VAV | Variable Air Volume
VAV0100 | VAV | Variable Air Volume
VAV0101 | VAV | Variable Air Volume
VAV0102 | VAV | Variable Air Volume
VAV0103 | VAV | Variable Air Volume
VAV0104 | VAV | Variable Air Volume
VAV0105 | VAV | Variable Air Volume
VAV0106 | VAV | Variable Air Volume
VAV0107 | VAV | Variable Air Volume
VAV0108 | VAV | Variable Air Volume
CCU3F0301 | CCU | CCU
CCU3F0302 | CCU | CCU
CCUB0001A | CCU | CCU
CCUB0001B | CCU | CCU
CCUB0002A | CCU | CCU
CCUB0002B | CCU | CCU
CCUB0003 | CCU | CCU
CCUB0004 | CCU | CCU
CCUB0005A | CCU | CCU
CCUB0005B | CCU | CCU
CCUB0006A | CCU | CCU
CCUB0006B | CCU | CCU
CCUB0007 | CCU | CCU
CCUB0008 | CCU | CCU
TEF0101 | TEF | TEF
TEF0102 | TEF | TEF
TEF0301 | TEF | TEF
TEF0302 | TEF | TEF
CHW_HE01 | HEX | Heat Exchanger
CHW_HE02 | HEX | Heat Exchanger
CHW_HE03 | HEX | Heat Exchanger
CHW_HE04 | HEX | Heat Exchanger
CHW_HE05 | HEX | Heat Exchanger
DXB0001 | DX Unit | DX Unit - Ducted Split
DXB0002 | DX Unit | DX Unit - Ducted Split
DXB0003 | DX Unit | DX Unit - Ducted Split
DXB0004 | DX Unit | DX Unit - Ducted Split
DXB0005 | DX Unit | DX Unit - Ducted Split
DXB0006 | DX Unit | DX Unit - Floor Standing Units
DXB0007 | DX Unit | DX Unit - Floor Standing Units
DXB0008 | DX Unit | DX Unit - Floor Standing Units
DXB0009 | DX Unit | DX Unit - Ducted Split
DXB0010 | DX Unit | DX Unit - Ducted Split
MV_Generator | Generator | Generator
KEF0103 | KEF | KEF
KEF0303 | KEF | KEF
CHWP_B01 | CHW Pump | Chilled Water Pump
CHWP_B02 | CHW Pump | Chilled Water Pump
CHWP_B03 | CHW Pump | Chilled Water Pump
CHWP_B04 | CHW Pump | Chilled Water Pump
CHWP01 | CHW Pump | Chilled Water Pump
CHWP02 | CHW Pump | Chilled Water Pump
CHWP03 | CHW Pump | Chilled Water Pump
CHWP04 | CHW Pump | Chilled Water Pump
GEFB0001 | GEF | General Extract Fan
REF0001 | EF | Extract Fan

## RDC Asset Register
EQUIPMENT ASSET REGISTER
Tag No. | Equipment Type | Description | Remarks
NB_AHU8511 | AHU | Air Handling Unit
NB_AHU8512 | AHU | Air Handling Unit
NB_AHU8513 | AHU | Air Handling Unit
NB_AHU8514 | AHU | Air Handling Unit |  | EQUIPMENT COUNT SUMMARY
NB_AHU8515 | AHU | Air Handling Unit |  | AHU | 37
NB_AHU8516 | AHU | Air Handling Unit |  | ERU | 11
NB_AHU8517 | AHU | Air Handling Unit |  | FCU | 135
NB_AHU8518 | AHU | Air Handling Unit |  | CHW Pump | 9
NB_AHU8519 | AHU | Air Handling Unit |  | Variable Air Volume | 739
NB_AHU8520 | AHU | Air Handling Unit |  | Constant Air Volume | 78
NB_AHU8521 | AHU | Air Handling Unit |  | FEV | 76
RDC_NB_ERU8531 | ERU | ERU |  | VEV | 44
RDC_NB_ERU8532 | ERU | ERU |  | EAV | 51
RDC_NB_ERU8533 | ERU | ERU |  | Heat Exchanger | 7
RDC_NB_ERU8534 | ERU | ERU |  | EF | 38
RDC_NB_ERU8535 | ERU | ERU |  | Generator | 3
RDC_NB_ERU8536 | ERU | ERU |  | TOTAL | 1228
RDC_NB_ERU8537 | ERU | ERU
RDC_NB_ERU8538 | ERU | ERU
RDC_NB_ERU8539 | ERU | ERU
RDC_NB_ERU8540 | ERU | ERU
RDC_NB_ERU8541 | ERU | ERU
RDC_SB_AHU8011 | AHU | Air Handling Unit
RDC_SB_AHU8012 | AHU | Air Handling Unit
RDC_SB_AHU8021 | AHU | Air Handling Unit
RDC_SB_AHU8022 | AHU | Air Handling Unit
RDC_SB_AHU8023 | AHU | Air Handling Unit |  | # | Equipment type | Tag(s) in IO list | Assumption
RDC_SB_AHU8024 | AHU | Air Handling Unit |  | 1 | DX Unit | RDC_UB_AHU8603_DXUnit | This is the DX coil/compressor of AHU8603
RDC_SB_AHU8025 | AHU | Air Handling Unit |  | 2 | DX Unit | RDC_UB_AHU8604_DXUnit | This is the DX coil/compressor of AHU8604
RDC_SB_AHU8026 | AHU | Air Handling Unit |  | 3 | DX Unit | RDC_UB_AHU8605_DXUnit | This is the DX coil/compressor of AHU8605
RDC_SB_AHU8031 | AHU | Air Handling Unit |  | 4 | DX Unit | RDC_UB_AHU8606_DXUnit | This is the DX coil/compressor of AHU8606
RDC_SB_AHU8032 | AHU | Air Handling Unit |  | 5 | DX Unit | RDC_UB_AHU8607_DXUnit | This is the DX coil/compressor of AHU8607
RDC_SB_AHU8033 | AHU | Air Handling Unit |  | 6 | DX Unit | RDC_UB_AHU8608_DXUnit | This is the DX coil/compressor of AHU8608
RDC_SB_AHU8034 | AHU | Air Handling Unit |  | 7 | DX Unit | RDC_UB_AHU8609_DXUnit | This is the DX coil/compressor of AHU8609
RDC_SB_AHU8035 | AHU | Air Handling Unit |  | 8 | EF | RDC_SB_BUS_EFA1 | Extract fans serving the bus station
RDC_SB_AHU8036 | AHU | Air Handling Unit |  | 9 | EF | RDC_SB_BUS_EFA2 | Extract fans serving the bus station
RDC_SB_AHU8037 | AHU | Air Handling Unit |  | 10 | EF | RDC_SB_BUS_EFA3 | Extract fans serving the bus station
RDC_SB_AHU8041 | AHU | Air Handling Unit |  | 11 | EF | RDC_SB_BUS_EFA4 | Extract fans serving the bus station
RDC_SB_AHU8042 | AHU | Air Handling Unit |  | 12 | EF | RDC_SB_BUS_EFA5 | Extract fans serving the bus station
RDC_UB_AHU8601 | AHU | Air Handling Unit |  | 13 | EF | RDC_SB_BUS_EFA6 | Extract fans serving the bus station
RDC_UB_AHU8602 | AHU | Air Handling Unit |  | 14 | EF | RDC_SB_BUS_EFA7 | Extract fans serving the bus station
RDC_UB_AHU8603 | AHU | Air Handling Unit |  | 15 | EF | RDC_SB_BUS_EFA8 | Extract fans serving the bus station
RDC_UB_AHU8604 | AHU | Air Handling Unit |  | 16 | EF | RDC_SB_BUS_EFB1 | Extract fans serving the bus station
RDC_UB_AHU8605 | AHU | Air Handling Unit |  | 17 | EF | RDC_SB_BUS_EFB2 | Extract fans serving the bus station
RDC_UB_AHU8606 | AHU | Air Handling Unit |  | 18 | EF | RDC_SB_BUS_EFB3 | Extract fans serving the bus station
RDC_UB_AHU8607 | AHU | Air Handling Unit |  | 19 | EF | RDC_SB_BUS_EFB4 | Extract fans serving the bus station
RDC_UB_AHU8608 | AHU | Air Handling Unit |  | 20 | EF | RDC_SB_BUS_EFB5 | Extract fans serving the bus station
RDC_UB_AHU8609 | AHU | Air Handling Unit |  | 21 | EF | RDC_SB_BUS_EFB6 | Extract fans serving the bus station
RDC_NB_EF8511 | EF | EF |  | 22 | EF | RDC_SB_BUS_EFB7 | Extract fans serving the bus station
RDC_NB_EF8512 | EF | EF |  | 23 | EF | RDC_SB_BUS_EFB8 | Extract fans serving the bus station
RDC_NB_EF8513 | EF | EF |  | 24 | EF | RDC_SB_BUS_EFC1 | Extract fans serving the bus station
RDC_NB_EF8514 | EF | EF |  | 25 | EF | RDC_SB_BUS_EFC2 | Extract fans serving the bus station
RDC_NB_EF8551 | EF | EF |  | 26 | EF | RDC_SB_BUS_EFD1 | Extract fans serving the bus station
RDC_NB_EF8552 | EF | EF |  | 27 | EF | RDC_SB_BUS_EFD2 | Extract fans serving the bus station
RDC_NB_EF8553 | EF | EF
RDC_NB_EF8554 | EF | EF
RDC_SB_EF8041 | EF | EF
RDC_SB_EF8042 | EF | EF
RDC_SB_EF8043 | EF | EF
RDC_SB_EF8044 | EF | EF
RDC_SB_BUS_EFA1 | EF | EF
RDC_SB_BUS_EFA2 | EF | EF
RDC_SB_BUS_EFA3 | EF | EF
RDC_SB_BUS_EFA4 | EF | EF
RDC_SB_BUS_EFA5 | EF | EF
RDC_SB_BUS_EFA6 | EF | EF
RDC_SB_BUS_EFA7 | EF | EF
RDC_SB_BUS_EFA8 | EF | EF
RDC_SB_BUS_EFB1 | EF | EF
RDC_SB_BUS_EFB2 | EF | EF
RDC_SB_BUS_EFB3 | EF | EF
RDC_SB_BUS_EFB4 | EF | EF
RDC_SB_BUS_EFB5 | EF | EF
RDC_SB_BUS_EFB6 | EF | EF
RDC_SB_BUS_EFB7 | EF | EF
RDC_SB_BUS_EFB8 | EF | EF
RDC_SB_BUS_EFC1 | EF | EF
RDC_SB_BUS_EFC2 | EF | EF
RDC_SB_BUS_EFD1 | EF | EF
RDC_SB_BUS_EFD2 | EF | EF
RDC_UB_EF8641 | EF | EF
RDC_UB_EF8642 | EF | EF
RDC_UB_EF8643 | EF | EF
RDC_UB_EF8644 | EF | EF
RDC_UB_EF8645 | EF | EF
RDC_UB_EF8646 | EF | EF
RDC_NB_GF_VAV4001 | VAV | Variable Air Volume
RDC_NB_GF_VAV4005_EV4006 | VAV | Variable Air Volume
RDC_NB_GF_VAV4040 | VAV | Variable Air Volume
RDC_NB_GF_VAV4050_VEV4051 | VAV | Variable Air Volume
RDC_NB_GF_VAV4060_VEV4061 | VAV | Variable Air Volume
RDC_NB_GF_VAV4070A_VEV4073A | VAV | Variable Air Volume
RDC_NB_GF_VAV4070B_VEV4073B | VAV | Variable Air Volume
RDC_NB_GF_VAV4071A_VEV4074A | VAV | Variable Air Volume
RDC_NB_GF_VAV4071B_VEV4074B | VAV | Variable Air Volume
RDC_NB_GF_VAV4072A_VEV4075A | VAV | Variable Air Volume
RDC_NB_GF_VAV4072B_VEV4075B | VAV | Variable Air Volume
RDC_NB_GF_VAV4080A_VEV4082A | VAV | Variable Air Volume
RDC_NB_GF_VAV4080B_VEV4082B | VAV | Variable Air Volume
RDC_NB_GF_VAV4081A_VEV4083A | VAV | Variable Air Volume
RDC_NB_GF_VAV4081B_VEV4083B | VAV | Variable Air Volume
RDC_NB_GF_VAV4090_VEV4091 | VAV | Variable Air Volume
RDC_NB_GF_VAV4100_EV4101 | VAV | Variable Air Volume
RDC_NB_GF_VAV4105_EV4106 | VAV | Variable Air Volume
RDC_NB_GF_VAV4110_EV4111 | VAV | Variable Air Volume
RDC_NB_GF_VAV4115_EV4116 | VAV | Variable Air Volume
RDC_NB_GF_VAV4120_EV4121 | VAV | Variable Air Volume
RDC_NB_GF_VAV4125_EV4126 | VAV | Variable Air Volume
RDC_NB_GF_VAV4130_EV4131 | VAV | Variable Air Volume
RDC_NB_GF_VAV4135_EV4136 | VAV | Variable Air Volume
RDC_NB_GF_VAV4140_EV4141 | VAV | Variable Air Volume
RDC_NB_GF_VAV4145_EV4146 | VAV | Variable Air Volume
RDC_NB_GF_VAV4165_EV4166 | VAV | Variable Air Volume
RDC_NB_GF_VAV4180_VEV4181 | VAV | Variable Air Volume
RDC_NB_GF_VAV4190_VEV4192 | VAV | Variable Air Volume
RDC_NB_GF_VAV4191 | VAV | Variable Air Volume
RDC_NB_GF_VAV4200_VEV4201 | VAV | Variable Air Volume
RDC_NB_GF_VAV4210 | VAV | Variable Air Volume
RDC_NB_GF_VAV4211 | VAV | Variable Air Volume
RDC_NB_GF_VAV4212 | VAV | Variable Air Volume
RDC_NB_GF_VAV4225 | VAV | Variable Air Volume
RDC_NB_GF_VAV4230 | VAV | Variable Air Volume
RDC_NB_GF_VAV4235 | VAV | Variable Air Volume
RDC_NB_GF_VAV4240 | VAV | Variable Air Volume
RDC_NB_GF_VAV4245 | VAV | Variable Air Volume
RDC_NB_GF_VAV4250 | VAV | Variable Air Volume
RDC_NB_GF_VAV4255 | VAV | Variable Air Volume
RDC_NB_GF_VAV4260 | VAV | Variable Air Volume
RDC_NB_GF_VAV4265 | VAV | Variable Air Volume
RDC_NB_GF_VAV4270 | VAV | Variable Air Volume
RDC_NB_GF_VAV4275 | VAV | Variable Air Volume
RDC_NB_GF_VAV4280 | VAV | Variable Air Volume
RDC_NB_GF_VAV4285 | VAV | Variable Air Volume
RDC_NB_GF_VAV4290 | VAV | Variable Air Volume
RDC_NB_GF_VAV4295 | VAV | Variable Air Volume
RDC_NB_GF_VAV4300 | VAV | Variable Air Volume
RDC_NB_GF_VAV4305 | VAV | Variable Air Volume
RDC_NB_GF_VAV4310 | VAV | Variable Air Volume
RDC_NB_GF_VAV4312 | VAV | Variable Air Volume
RDC_NB_GF_VAV5000_EV5002 | VAV | Variable Air Volume
RDC_NB_GF_VAV5001_EV5003 | VAV | Variable Air Volume
RDC_NB_GF_VAV5010_EV5011 | VAV | Variable Air Volume
RDC_NB_GF_VAV5015_EV5016 | VAV | Variable Air Volume
RDC_NB_GF_VAV5025 | VAV | Variable Air Volume
RDC_NB_GF_VAV5030_EV5031 | VAV | Variable Air Volume
RDC_NB_GF_VAV5040_EV5041 | VAV | Variable Air Volume
RDC_NB_GF_VAV5045_EV5046 | VAV | Variable Air Volume
RDC_NB_GF_VAV5050 | VAV | Variable Air Volume
RDC_NB_GF_VAV5051 | VAV | Variable Air Volume
RDC_NB_GF_VAV5054 | VAV | Variable Air Volume
RDC_NB_GF_VAV5060_CEV5061 | VAV | Variable Air Volume
RDC_NB_GF_VAV5070 | VAV | Variable Air Volume
RDC_NB_GF_VAV5080_VEV5081 | VAV | Variable Air Volume
RDC_NB_GF_VAV5090 | VAV | Variable Air Volume
RDC_NB_GF_VAV5091 | VAV | Variable Air Volume
RDC_NB_GF_VAV5100_EV5101 | VAV | Variable Air Volume
RDC_NB_GF_VAV5105 | VAV | Variable Air Volume
RDC_NB_GF_VAV5110 | VAV | Variable Air Volume
RDC_NB_GF_VAV5115 | VAV | Variable Air Volume
RDC_NB_GF_VAV5120 | VAV | Variable Air Volume
RDC_NB_GF_VAV5125 | VAV | Variable Air Volume
RDC_NB_GF_VAV5130 | VAV | Variable Air Volume
RDC_NB_GF_VAV5135 | VAV | Variable Air Volume
RDC_NB_GF_VAV5140 | VAV | Variable Air Volume
RDC_NB_GF_VAV5145 | VAV | Variable Air Volume
RDC_NB_GF_VAV5150 | VAV | Variable Air Volume
RDC_NB_GF_VAV5152 | VAV | Variable Air Volume
RDC_NB_GF_VAV5155 | VAV | Variable Air Volume
RDC_NB_GF_VAV5156 | VAV | Variable Air Volume
RDC_NB_GF_VAV5165_EV5166 | VAV | Variable Air Volume
RDC_NB_GF_VAV5180 | VAV | Variable Air Volume
RDC_NB_GF_VAV5181 | VAV | Variable Air Volume
RDC_NB_GF_VAV5190 | VAV | Variable Air Volume
RDC_NB_GF_VAV5200 | VAV | Variable Air Volume
RDC_NB_GF_VAV5210 | VAV | Variable Air Volume
RDC_NB_GF_VAV5220 | VAV | Variable Air Volume
RDC_NB_GF_VAV5230 | VAV | Variable Air Volume
RDC_NB_GF_VAV5250_VEV5251 | VAV | Variable Air Volume
RDC_NB_GF_VAV5260_VEV5261 | VAV | Variable Air Volume
RDC_NB_GF_VAV5270A | VAV | Variable Air Volume
RDC_NB_GF_VAV5270B | VAV | Variable Air Volume
RDC_NB_GF_VAV5295_EV5296 | VAV | Variable Air Volume
RDC_NB_GF_VAV5300 | VAV | Variable Air Volume
RDC_NB_GF_VAV5305 | VAV | Variable Air Volume
RDC_NB_GF_VAV5310 | VAV | Variable Air Volume
RDC_NB_GF_VAV5315 | VAV | Variable Air Volume
RDC_NB_GF_VAV5325 | VAV | Variable Air Volume
RDC_NB_GF_VAV5330 | VAV | Variable Air Volume
RDC_NB_GF_VAV5335 | VAV | Variable Air Volume
RDC_NB_GF_VAV5340 | VAV | Variable Air Volume
RDC_NB_GF_VAV5345 | VAV | Variable Air Volume
RDC_NB_GF_VAV5355 | VAV | Variable Air Volume
RDC_NB_GF_VAV5360 | VAV | Variable Air Volume
RDC_NB_GF_VAV5365 | VAV | Variable Air Volume
RDC_NB_GF_VAV5370 | VAV | Variable Air Volume
RDC_NB_GF_VAV5380 | VAV | Variable Air Volume
RDC_NB_GF_VAV5385 | VAV | Variable Air Volume
RDC_NB_GF_VAV5390 | VAV | Variable Air Volume
RDC_NB_GF_VAV5395 | VAV | Variable Air Volume
RDC_NB_GF_VAV5400 | VAV | Variable Air Volume
RDC_NB_GF_VAV5405 | VAV | Variable Air Volume
RDC_NB_GF_VAV5410_EV5411 | VAV | Variable Air Volume
RDC_NB_GF_VAV5415 | VAV | Variable Air Volume
RDC_NB_GF_VAV6000_EV6001 | VAV | Variable Air Volume
RDC_NB_GF_VAV6010_EV6011 | VAV | Variable Air Volume
RDC_NB_GF_VAV6025_EV6026 | VAV | Variable Air Volume
RDC_NB_GF_VAV6130_EV6131 | VAV | Variable Air Volume
RDC_NB_GF_VAV6135 | VAV | Variable Air Volume
RDC_NB_GF_VAV6140 | VAV | Variable Air Volume
RDC_NB_GF_VAV6145 | VAV | Variable Air Volume
RDC_NB_GF_VAV6150 | VAV | Variable Air Volume
RDC_NB_GF_VAV6155 | VAV | Variable Air Volume
RDC_NB_GF_VAV6160 | VAV | Variable Air Volume
RDC_NB_GF_VAV6170 | VAV | Variable Air Volume
RDC_NB_GF_VAV6175 | VAV | Variable Air Volume
RDC_NB_GF_VAV6180 | VAV | Variable Air Volume
RDC_NB_GF_VAV6185_EV6186 | VAV | Variable Air Volume
RDC_NB_GF_VAV6190_EV6191 | VAV | Variable Air Volume
RDC_NB_GF_VAV6195 | VAV | Variable Air Volume
RDC_NB_GF_VAV6200_EV6201 | VAV | Variable Air Volume
RDC_NB_GF_VAV6205_EV6206 | VAV | Variable Air Volume
RDC_NB_GF_VAV6210 | VAV | Variable Air Volume
RDC_NB_GF_VAV6220_EV6221 | VAV | Variable Air Volume
RDC_NB_GF_VAV6240_EV6241 | VAV | Variable Air Volume
RDC_NB_GF_VAV6285_EV6286 | VAV | Variable Air Volume
RDC_NB_GF_VAV6295_EV6296 | VAV | Variable Air Volume
RDC_NB_GF_VAV6300 | VAV | Variable Air Volume
RDC_NB_GF_VAV6305 | VAV | Variable Air Volume
RDC_NB_GF_VAV6310 | VAV | Variable Air Volume
RDC_NB_GF_VAV6315_EV6316 | VAV | Variable Air Volume
RDC_NB_GF_VAV6320 | VAV | Variable Air Volume
RDC_NB_GF_VAV6325 | VAV | Variable Air Volume
RDC_NB_GF_VAV6330 | VAV | Variable Air Volume
RDC_NB_GF_VAV6335 | VAV | Variable Air Volume
RDC_NB_GF_VAV6340 | VAV | Variable Air Volume
RDC_NB_GF_VAV6345 | VAV | Variable Air Volume
RDC_NB_GF_VAV6350 | VAV | Variable Air Volume
RDC_NB_GF_VAV6355 | VAV | Variable Air Volume
RDC_NB_GF_VAV6360 | VAV | Variable Air Volume
RDC_NB_GF_VAV6365 | VAV | Variable Air Volume
RDC_NB_GF_VAV6370 | VAV | Variable Air Volume
RDC_NB_GF_VAV6375 | VAV | Variable Air Volume
RDC_NB_GF_VAV6380 | VAV | Variable Air Volume
RDC_NB_GF_VAV6390 | VAV | Variable Air Volume
RDC_NB_GF_VAV6395 | VAV | Variable Air Volume
RDC_NB_GF_VAV6400 | VAV | Variable Air Volume
RDC_NB_GF_VAV6405 | VAV | Variable Air Volume
RDC_NB_GF_VAV6410 | VAV | Variable Air Volume
RDC_NB_GF_VAV7000 | VAV | Variable Air Volume
RDC_NB_GF_VAV7020A | VAV | Variable Air Volume
RDC_NB_GF_VAV7020B | VAV | Variable Air Volume
RDC_NB_GF_VAV7021A | VAV | Variable Air Volume
RDC_NB_GF_VAV7021B | VAV | Variable Air Volume
RDC_NB_GF_VAV7030_VEV7031 | VAV | Variable Air Volume
RDC_NB_GF_VAV7040 | VAV | Variable Air Volume
RDC_NB_GF_VAV7050_VEV7051 | VAV | Variable Air Volume
RDC_NB_GF_VAV7060_VEV7061 | VAV | Variable Air Volume
RDC_NB_GF_VAV7070A | VAV | Variable Air Volume
RDC_NB_GF_VAV7070B | VAV | Variable Air Volume
RDC_NB_GF_VAV7071A | VAV | Variable Air Volume
RDC_NB_GF_VAV7071B | VAV | Variable Air Volume
RDC_NB_GF_VAV7080 | VAV | Variable Air Volume
RDC_NB_GF_VAV7085 | VAV | Variable Air Volume
RDC_NB_GF_VAV7090 | VAV | Variable Air Volume
RDC_NB_GF_VAV7095 | VAV | Variable Air Volume
RDC_NB_GF_VAV7100 | VAV | Variable Air Volume
RDC_NB_GF_VAV7105 | VAV | Variable Air Volume
RDC_NB_GF_VAV7110 | VAV | Variable Air Volume
RDC_NB_GF_VAV7115 | VAV | Variable Air Volume
RDC_NB_GF_VAV7120 | VAV | Variable Air Volume
RDC_NB_GF_VAV7125_EV7126 | VAV | Variable Air Volume
RDC_NB_GF_VAV7130 | VAV | Variable Air Volume
RDC_NB_GF_VAV7135 | VAV | Variable Air Volume
RDC_NB_GF_VAV7140_EV7141 | VAV | Variable Air Volume
RDC_NB_GF_VAV7145 | VAV | Variable Air Volume
RDC_NB_GF_VAV7155 | VAV | Variable Air Volume
RDC_NB_GF_VAV7165 | VAV | Variable Air Volume
RDC_NB_GF_VAV7175 | VAV | Variable Air Volume
RDC_NB_GF_VAV7176 | VAV | Variable Air Volume
RDC_NB_GF_VAV7180 | VAV | Variable Air Volume
RDC_NB_GF_VAV7185_EV7186 | VAV | Variable Air Volume
RDC_NB_GF_VAV7195 | VAV | Variable Air Volume
RDC_NB_GF_VAV7205 | VAV | Variable Air Volume
RDC_NB_GF_VAV7215_EV7216 | VAV | Variable Air Volume
RDC_NB_GF_VAV7220_CEV7221 | VAV | Variable Air Volume
RDC_NB_GF_VAV7230_VEV7231 | VAV | Variable Air Volume
RDC_NB_GF_VAV7240_VEV7241A | VAV | Variable Air Volume
RDC_NB_GF_VAV7250_VEV7251 | VAV | Variable Air Volume
RDC_NB_GF_VAV7260_VEV7261 | VAV | Variable Air Volume
RDC_NB_GF_VAV7270_VEV7271 | VAV | Variable Air Volume
RDC_NB_GF_VAV7280_VEV7281 | VAV | Variable Air Volume
RDC_NB_GF_VAV7290_VEV7291 | VAV | Variable Air Volume
RDC_NB_GF_VAV7300 | VAV | Variable Air Volume
RDC_NB_GF_VAV7310_VEV7311 | VAV | Variable Air Volume
RDC_NB_GF_VAV7320_VEV7321 | VAV | Variable Air Volume
RDC_NB_GF_VAV7330_VEV7331 | VAV | Variable Air Volume
RDC_NB_GF_VAV7340_VEV7341 | VAV | Variable Air Volume
RDC_NB_GF_VAV7350_VEV7351 | VAV | Variable Air Volume
RDC_NB_GF_VAV7360_VEV7361 | VAV | Variable Air Volume
RDC_NB_GF_VAV7370_VEV7371 | VAV | Variable Air Volume
RDC_NB_GF_VAV7385 | VAV | Variable Air Volume
RDC_NB_GF_VAV7390 | VAV | Variable Air Volume
RDC_NB_GF_VAV7395 | VAV | Variable Air Volume
RDC_NB_GF_VAV7400 | VAV | Variable Air Volume
RDC_NB_GF_VAV7405 | VAV | Variable Air Volume
RDC_NB_GF_VAV7410 | VAV | Variable Air Volume
RDC_NB_GF_VAV7415 | VAV | Variable Air Volume
RDC_NB_GF_VAV7425 | VAV | Variable Air Volume
RDC_NB_GF_VAV7430 | VAV | Variable Air Volume
RDC_NB_GF_VAV7435 | VAV | Variable Air Volume
RDC_NB_GF_VAV7440 | VAV | Variable Air Volume
RDC_NB_GF_VAV7445 | VAV | Variable Air Volume
RDC_NB_GF_VAV7460 | VAV | Variable Air Volume
RDC_NB_GF_VAV7465 | VAV | Variable Air Volume
RDC_NB_GF_VAV7470 | VAV | Variable Air Volume
RDC_NB_GF_VAV7475 | VAV | Variable Air Volume
RDC_NB_GF_VAV7480 | VAV | Variable Air Volume
RDC_NB_GF_VAV7485 | VAV | Variable Air Volume
RDC_NB_GF_VAV7490_EV7495 | VAV | Variable Air Volume
RDC_NB_GF_VAV7496 | VAV | Variable Air Volume
RDC_NB_GF_VAV7498 | VAV | Variable Air Volume
RDC_NB_GF_VAV7499 | VAV | Variable Air Volume
RDC_SB_1F_VAV | VAV | Variable Air Volume
RDC_SB_1F_VAV0506 | VAV | Variable Air Volume
RDC_SB_1F_VAV0507 | VAV | Variable Air Volume
RDC_SB_1F_VAV0508 | VAV | Variable Air Volume
RDC_SB_1F_VAV0509 | VAV | Variable Air Volume
RDC_SB_1F_VAV0510 | VAV | Variable Air Volume
RDC_SB_1F_VAV0511 | VAV | Variable Air Volume
RDC_SB_1F_VAV0512 | VAV | Variable Air Volume
RDC_SB_1F_VAV0513 | VAV | Variable Air Volume
RDC_SB_1F_VAV0514 | VAV | Variable Air Volume
RDC_SB_1F_VAV0518 | VAV | Variable Air Volume
RDC_SB_1F_VAV0519 | VAV | Variable Air Volume
RDC_SB_1F_VAV0520 | VAV | Variable Air Volume
RDC_SB_1F_VAV0521 | VAV | Variable Air Volume
RDC_SB_1F_VAV0522 | VAV | Variable Air Volume
RDC_SB_1F_VAV0523 | VAV | Variable Air Volume
RDC_SB_1F_VAV0526 | VAV | Variable Air Volume
RDC_SB_1F_VAV0527 | VAV | Variable Air Volume
RDC_SB_1F_VAV0528 | VAV | Variable Air Volume
RDC_SB_1F_VAV0529 | VAV | Variable Air Volume
RDC_SB_1F_VAV0530 | VAV | Variable Air Volume
RDC_SB_1F_VAV0531 | VAV | Variable Air Volume
RDC_SB_1F_VAV0532 | VAV | Variable Air Volume
RDC_SB_1F_VAV0533 | VAV | Variable Air Volume
RDC_SB_1F_VAV0538 | VAV | Variable Air Volume
RDC_SB_1F_VAV1501 | VAV | Variable Air Volume
RDC_SB_1F_VAV1502 | VAV | Variable Air Volume
RDC_SB_1F_VAV1503 | VAV | Variable Air Volume
RDC_SB_1F_VAV1505 | VAV | Variable Air Volume
RDC_SB_1F_VAV1506 | VAV | Variable Air Volume
RDC_SB_1F_VAV1507 | VAV | Variable Air Volume
RDC_SB_1F_VAV1508 | VAV | Variable Air Volume
RDC_SB_1F_VAV1509 | VAV | Variable Air Volume
RDC_SB_1F_VAV1510 | VAV | Variable Air Volume
RDC_SB_1F_VAV1511 | VAV | Variable Air Volume
RDC_SB_1F_VAV1512 | VAV | Variable Air Volume
RDC_SB_1F_VAV1513 | VAV | Variable Air Volume
RDC_SB_1F_VAV1514 | VAV | Variable Air Volume
RDC_SB_1F_VAV1515 | VAV | Variable Air Volume
RDC_SB_1F_VAV1516 | VAV | Variable Air Volume
RDC_SB_1F_VAV1517 | VAV | Variable Air Volume
RDC_SB_1F_VAV1518 | VAV | Variable Air Volume
RDC_SB_1F_VAV1519 | VAV | Variable Air Volume
RDC_SB_1F_VAV1520 | VAV | Variable Air Volume
RDC_SB_1F_VAV1521 | VAV | Variable Air Volume
RDC_SB_1F_VAV1522 | VAV | Variable Air Volume
RDC_SB_1F_VAV1523 | VAV | Variable Air Volume
RDC_SB_1F_VAV1524 | VAV | Variable Air Volume
RDC_SB_1F_VAV1525 | VAV | Variable Air Volume
RDC_SB_1F_VAV1526 | VAV | Variable Air Volume
RDC_SB_1F_VAV1527 | VAV | Variable Air Volume
RDC_SB_1F_VAV1528 | VAV | Variable Air Volume
RDC_SB_1F_VAV1529 | VAV | Variable Air Volume
RDC_SB_1F_VAV1530 | VAV | Variable Air Volume
RDC_SB_1F_VAV1531 | VAV | Variable Air Volume
RDC_SB_1F_VAV1532 | VAV | Variable Air Volume
RDC_SB_1F_VAV1533 | VAV | Variable Air Volume
RDC_SB_1F_VAV1534 | VAV | Variable Air Volume
RDC_SB_1F_VAV1536 | VAV | Variable Air Volume
RDC_SB_1F_VAV1539 | VAV | Variable Air Volume
RDC_SB_1F_VAV1540 | VAV | Variable Air Volume
RDC_SB_1F_VAV1542 | VAV | Variable Air Volume
RDC_SB_1F_VAV1543 | VAV | Variable Air Volume
RDC_SB_1F_VAV1544 | VAV | Variable Air Volume
RDC_SB_1F_VAV1545 | VAV | Variable Air Volume
RDC_SB_1F_VAV1546 | VAV | Variable Air Volume
RDC_SB_1F_VAV1547 | VAV | Variable Air Volume
RDC_SB_1F_VAV1548 | VAV | Variable Air Volume
RDC_SB_1F_VAV1549 | VAV | Variable Air Volume
RDC_SB_1F_VAV1550 | VAV | Variable Air Volume
RDC_SB_1F_VAV1551 | VAV | Variable Air Volume
RDC_SB_1F_VAV1552 | VAV | Variable Air Volume
RDC_SB_1F_VAV1553 | VAV | Variable Air Volume
RDC_SB_1F_VAV1554 | VAV | Variable Air Volume
RDC_SB_1F_VAV1555 | VAV | Variable Air Volume
RDC_SB_1F_VAV1556 | VAV | Variable Air Volume
RDC_SB_1F_VAV1557 | VAV | Variable Air Volume
RDC_SB_1F_VAV1558 | VAV | Variable Air Volume
RDC_SB_1F_VAV1559 | VAV | Variable Air Volume
RDC_SB_1F_VAV1560 | VAV | Variable Air Volume
RDC_SB_1F_VAV1561 | VAV | Variable Air Volume
RDC_SB_1F_VAV2501 | VAV | Variable Air Volume
RDC_SB_1F_VAV2502 | VAV | Variable Air Volume
RDC_SB_1F_VAV2503 | VAV | Variable Air Volume
RDC_SB_1F_VAV2504 | VAV | Variable Air Volume
RDC_SB_1F_VAV2505 | VAV | Variable Air Volume
RDC_SB_1F_VAV2506 | VAV | Variable Air Volume
RDC_SB_1F_VAV2508 | VAV | Variable Air Volume
RDC_SB_1F_VAV2509 | VAV | Variable Air Volume
RDC_SB_1F_VAV2510 | VAV | Variable Air Volume
RDC_SB_1F_VAV2511 | VAV | Variable Air Volume
RDC_SB_1F_VAV2512 | VAV | Variable Air Volume
RDC_SB_1F_VAV2513 | VAV | Variable Air Volume
RDC_SB_1F_VAV2514 | VAV | Variable Air Volume
RDC_SB_1F_VAV2515 | VAV | Variable Air Volume
RDC_SB_1F_VAV2516 | VAV | Variable Air Volume
RDC_SB_1F_VAV2517 | VAV | Variable Air Volume
RDC_SB_1F_VAV2518 | VAV | Variable Air Volume
RDC_SB_1F_VAV2519 | VAV | Variable Air Volume
RDC_SB_1F_VAV2520 | VAV | Variable Air Volume
RDC_SB_1F_VAV2521 | VAV | Variable Air Volume
RDC_SB_1F_VAV2522 | VAV | Variable Air Volume
RDC_SB_1F_VAV2523 | VAV | Variable Air Volume
RDC_SB_1F_VAV2524 | VAV | Variable Air Volume
RDC_SB_1F_VAV2525 | VAV | Variable Air Volume
RDC_SB_1F_VAV2526 | VAV | Variable Air Volume
RDC_SB_1F_VAV2527 | VAV | Variable Air Volume
RDC_SB_1F_VAV2528 | VAV | Variable Air Volume
RDC_SB_1F_VAV2529 | VAV | Variable Air Volume
RDC_SB_1F_VAV2530 | VAV | Variable Air Volume
RDC_SB_1F_VAV2531 | VAV | Variable Air Volume
RDC_SB_1F_VAV2532 | VAV | Variable Air Volume
RDC_SB_1F_VAV2533 | VAV | Variable Air Volume
RDC_SB_1F_VAV2534 | VAV | Variable Air Volume
RDC_SB_1F_VAV2535 | VAV | Variable Air Volume
RDC_SB_1F_VAV2536 | VAV | Variable Air Volume
RDC_SB_1F_VAV2538 | VAV | Variable Air Volume
RDC_SB_1F_VAV2539 | VAV | Variable Air Volume
RDC_SB_1F_VAV2540 | VAV | Variable Air Volume
RDC_SB_1F_VAV2541 | VAV | Variable Air Volume
RDC_SB_1F_VAV2542 | VAV | Variable Air Volume
RDC_SB_1F_VAV2543 | VAV | Variable Air Volume
RDC_SB_1F_VAV2544 | VAV | Variable Air Volume
RDC_SB_1F_VAV2545 | VAV | Variable Air Volume
RDC_SB_1F_VAV2546 | VAV | Variable Air Volume
RDC_SB_1F_VAV2547 | VAV | Variable Air Volume
RDC_SB_1F_VAV2548 | VAV | Variable Air Volume
RDC_SB_1F_VAV2549 | VAV | Variable Air Volume
RDC_SB_1F_VAV2550 | VAV | Variable Air Volume
RDC_SB_1F_VAV2551 | VAV | Variable Air Volume
RDC_SB_1F_VAV2552 | VAV | Variable Air Volume
RDC_SB_1F_VAV2553 | VAV | Variable Air Volume
RDC_SB_1F_VAV3504 | VAV | Variable Air Volume
RDC_SB_1F_VAV3505 | VAV | Variable Air Volume
RDC_SB_1F_VAV3506 | VAV | Variable Air Volume
RDC_SB_1F_VAV3507 | VAV | Variable Air Volume
RDC_SB_1F_VAV3508 | VAV | Variable Air Volume
RDC_SB_1F_VAV3509 | VAV | Variable Air Volume
RDC_SB_1F_VAV3510 | VAV | Variable Air Volume
RDC_SB_1F_VAV3511 | VAV | Variable Air Volume
RDC_SB_1F_VAV3512 | VAV | Variable Air Volume
RDC_SB_1F_VAV3513 | VAV | Variable Air Volume
RDC_SB_1F_VAV3514 | VAV | Variable Air Volume
RDC_SB_1F_VAV3515 | VAV | Variable Air Volume
RDC_SB_1F_VAV3516 | VAV | Variable Air Volume
RDC_SB_1F_VAV3517 | VAV | Variable Air Volume
RDC_SB_1F_VAV3518 | VAV | Variable Air Volume
RDC_SB_1F_VAV3519 | VAV | Variable Air Volume
RDC_SB_1F_VAV3520 | VAV | Variable Air Volume
RDC_SB_1F_VAV3521 | VAV | Variable Air Volume
RDC_SB_1F_VAV3522 | VAV | Variable Air Volume
RDC_SB_1F_VAV3523 | VAV | Variable Air Volume
RDC_SB_1F_VAV3524 | VAV | Variable Air Volume
RDC_SB_GF_VAV | VAV | Variable Air Volume
RDC_SB_GF_VAV0001 | VAV | Variable Air Volume
RDC_SB_GF_VAV0002 | VAV | Variable Air Volume
RDC_SB_GF_VAV0003 | VAV | Variable Air Volume
RDC_SB_GF_VAV0007 | VAV | Variable Air Volume
RDC_SB_GF_VAV0008 | VAV | Variable Air Volume
RDC_SB_GF_VAV0009 | VAV | Variable Air Volume
RDC_SB_GF_VAV0010 | VAV | Variable Air Volume
RDC_SB_GF_VAV0011 | VAV | Variable Air Volume
RDC_SB_GF_VAV0012 | VAV | Variable Air Volume
RDC_SB_GF_VAV0013 | VAV | Variable Air Volume
RDC_SB_GF_VAV0014 | VAV | Variable Air Volume
RDC_SB_GF_VAV0016 | VAV | Variable Air Volume
RDC_SB_GF_VAV0017 | VAV | Variable Air Volume
RDC_SB_GF_VAV0018 | VAV | Variable Air Volume
RDC_SB_GF_VAV0019 | VAV | Variable Air Volume
RDC_SB_GF_VAV0025 | VAV | Variable Air Volume
RDC_SB_GF_VAV1003_VEV1002 | VAV | Variable Air Volume
RDC_SB_GF_VAV1004 | VAV | Variable Air Volume
RDC_SB_GF_VAV1008 | VAV | Variable Air Volume
RDC_SB_GF_VAV2002 | VAV | Variable Air Volume
RDC_SB_GF_VAV2003 | VAV | Variable Air Volume
RDC_SB_GF_VAV2004 | VAV | Variable Air Volume
RDC_SB_GF_VAV2005 | VAV | Variable Air Volume
RDC_SB_GF_VAV2006 | VAV | Variable Air Volume
RDC_SB_GF_VAV2007 | VAV | Variable Air Volume
RDC_SB_GF_VAV2008 | VAV | Variable Air Volume
RDC_SB_GF_VAV2009 | VAV | Variable Air Volume
RDC_SB_GF_VAV2010 | VAV | Variable Air Volume
RDC_SB_GF_VAV2011 | VAV | Variable Air Volume
RDC_SB_GF_VAV2012 | VAV | Variable Air Volume
RDC_SB_GF_VAV2013 | VAV | Variable Air Volume
RDC_SB_GF_VAV2014 | VAV | Variable Air Volume
RDC_SB_GF_VAV2015 | VAV | Variable Air Volume
RDC_SB_GF_VAV2016 | VAV | Variable Air Volume
RDC_SB_GF_VAV2017 | VAV | Variable Air Volume
RDC_SB_GF_VAV2018 | VAV | Variable Air Volume
RDC_SB_GF_VAV2019 | VAV | Variable Air Volume
RDC_SB_GF_VAV2020 | VAV | Variable Air Volume
RDC_SB_GF_VAV2021 | VAV | Variable Air Volume
RDC_SB_GF_VAV2022 | VAV | Variable Air Volume
RDC_SB_GF_VAV2023 | VAV | Variable Air Volume
RDC_SB_GF_VAV2024 | VAV | Variable Air Volume
RDC_SB_GF_VAV2025 | VAV | Variable Air Volume
RDC_SB_GF_VAV2026 | VAV | Variable Air Volume
RDC_SB_GF_VAV2027 | VAV | Variable Air Volume
RDC_SB_GF_VAV2028 | VAV | Variable Air Volume
RDC_SB_GF_VAV2029 | VAV | Variable Air Volume
RDC_SB_GF_VAV2030 | VAV | Variable Air Volume
RDC_SB_GF_VAV2031 | VAV | Variable Air Volume
RDC_SB_GF_VAV2032 | VAV | Variable Air Volume
RDC_SB_GF_VAV2033 | VAV | Variable Air Volume
RDC_SB_GF_VAV2034 | VAV | Variable Air Volume
RDC_SB_GF_VAV2035 | VAV | Variable Air Volume
RDC_SB_GF_VAV2036 | VAV | Variable Air Volume
RDC_SB_GF_VAV2037 | VAV | Variable Air Volume
RDC_SB_GF_VAV2038 | VAV | Variable Air Volume
RDC_SB_GF_VAV2039 | VAV | Variable Air Volume
RDC_SB_GF_VAV2040 | VAV | Variable Air Volume
RDC_SB_GF_VAV2041 | VAV | Variable Air Volume
RDC_SB_GF_VAV2042 | VAV | Variable Air Volume
RDC_SB_GF_VAV2043 | VAV | Variable Air Volume
RDC_SB_GF_VAV2044 | VAV | Variable Air Volume
RDC_SB_GF_VAV2045 | VAV | Variable Air Volume
RDC_SB_GF_VAV2046 | VAV | Variable Air Volume
RDC_SB_GF_VAV2047 | VAV | Variable Air Volume
RDC_SB_GF_VAV3001 | VAV | Variable Air Volume
RDC_SB_GF_VAV3002 | VAV | Variable Air Volume
RDC_SB_GF_VAV3003 | VAV | Variable Air Volume
RDC_SB_GF_VAV3004 | VAV | Variable Air Volume
RDC_SB_GF_VAV3005 | VAV | Variable Air Volume
RDC_SB_GF_VAV3006 | VAV | Variable Air Volume
RDC_SB_GF_VAV3007 | VAV | Variable Air Volume
RDC_SB_GF_VAV3008 | VAV | Variable Air Volume
RDC_SB_GF_VAV3009 | VAV | Variable Air Volume
RDC_SB_GF_VAV3010 | VAV | Variable Air Volume
RDC_SB_GF_VAV3011 | VAV | Variable Air Volume
RDC_SB_GF_VAV3012 | VAV | Variable Air Volume
RDC_SB_GF_VAV3013 | VAV | Variable Air Volume
RDC_SB_GF_VAV3014 | VAV | Variable Air Volume
RDC_SB_GF_VAV3015 | VAV | Variable Air Volume
RDC_SB_GF_VAV3016 | VAV | Variable Air Volume
RDC_SB_GF_VAV3017 | VAV | Variable Air Volume
RDC_SB_GF_VAV3018 | VAV | Variable Air Volume
RDC_SB_GF_VAV3019 | VAV | Variable Air Volume
RDC_SB_GF_VAV3020 | VAV | Variable Air Volume
RDC_SB_GF_VAV3021 | VAV | Variable Air Volume
RDC_SB_GF_VAV3022 | VAV | Variable Air Volume
RDC_SB_GF_VAV3023 | VAV | Variable Air Volume
RDC_SB_GF_VAV3024 | VAV | Variable Air Volume
RDC_SB_GF_VAV3025 | VAV | Variable Air Volume
RDC_SB_GF_VAV3026 | VAV | Variable Air Volume
RDC_SB_GF_VAV3027 | VAV | Variable Air Volume
RDC_SB_GF_VAV3028 | VAV | Variable Air Volume
RDC_SB_GF_VAV3029 | VAV | Variable Air Volume
RDC_SB_GF_VAV3030 | VAV | Variable Air Volume
RDC_SB_GF_VAV3031 | VAV | Variable Air Volume
RDC_SB_GF_VAV3032 | VAV | Variable Air Volume
RDC_SB_GF_VAV3033 | VAV | Variable Air Volume
RDC_SB_GF_VAV3034 | VAV | Variable Air Volume
RDC_SB_GF_VAV3035 | VAV | Variable Air Volume
RDC_SB_GF_VAV3036 | VAV | Variable Air Volume
RDC_SB_GF_VAV3501 | VAV | Variable Air Volume
RDC_SB_GF_VAV3502 | VAV | Variable Air Volume
RDC_SB_GF_VAV3503 | VAV | Variable Air Volume
RDC_NB_1F_VAV4510 | VAV | Variable Air Volume
RDC_NB_1F_VAV4515_EV4516 | VAV | Variable Air Volume
RDC_NB_1F_VAV4520_EV4521 | VAV | Variable Air Volume
RDC_NB_1F_VAV4525_EV4526 | VAV | Variable Air Volume
RDC_NB_1F_VAV4530_EV4531 | VAV | Variable Air Volume
RDC_NB_1F_VAV4535_EV4536 | VAV | Variable Air Volume
RDC_NB_1F_VAV4540_EV4541 | VAV | Variable Air Volume
RDC_NB_1F_VAV4545_EV4546 | VAV | Variable Air Volume
RDC_NB_1F_VAV4550_EV4551 | VAV | Variable Air Volume
RDC_NB_1F_VAV4555_EV4556 | VAV | Variable Air Volume
RDC_NB_1F_VAV4560_EV4561 | VAV | Variable Air Volume
RDC_NB_1F_VAV4565_EV4566 | VAV | Variable Air Volume
RDC_NB_1F_VAV4570_EV4571 | VAV | Variable Air Volume
RDC_NB_1F_VAV4575_EV4576 | VAV | Variable Air Volume
RDC_NB_1F_VAV4580 | VAV | Variable Air Volume
RDC_NB_1F_VAV4600 | VAV | Variable Air Volume
RDC_NB_1F_VAV4601 | VAV | Variable Air Volume
RDC_NB_1F_VAV4620_VEV4621 | VAV | Variable Air Volume
RDC_NB_1F_VAV4630_VEV4631 | VAV | Variable Air Volume
RDC_NB_1F_VAV4650 | VAV | Variable Air Volume
RDC_NB_1F_VAV4660 | VAV | Variable Air Volume
RDC_NB_1F_VAV4665 | VAV | Variable Air Volume
RDC_NB_1F_VAV4670 | VAV | Variable Air Volume
RDC_NB_1F_VAV4675 | VAV | Variable Air Volume
RDC_NB_1F_VAV4680 | VAV | Variable Air Volume
RDC_NB_1F_VAV4685 | VAV | Variable Air Volume
RDC_NB_1F_VAV4690 | VAV | Variable Air Volume
RDC_NB_1F_VAV4695 | VAV | Variable Air Volume
RDC_NB_1F_VAV4700 | VAV | Variable Air Volume
RDC_NB_1F_VAV4705 | VAV | Variable Air Volume
RDC_NB_1F_VAV4710 | VAV | Variable Air Volume
RDC_NB_1F_VAV4715 | VAV | Variable Air Volume
RDC_NB_1F_VAV4720 | VAV | Variable Air Volume
RDC_NB_1F_VAV4725 | VAV | Variable Air Volume
RDC_NB_1F_VAV4730 | VAV | Variable Air Volume
RDC_NB_1F_VAV4735 | VAV | Variable Air Volume
RDC_NB_1F_VAV4740 | VAV | Variable Air Volume
RDC_NB_1F_VAV4745 | VAV | Variable Air Volume
RDC_NB_1F_VAV4900P | VAV | Variable Air Volume
RDC_NB_1F_VAV4910P | VAV | Variable Air Volume
RDC_NB_1F_VAV5500 | VAV | Variable Air Volume
RDC_NB_1F_VAV5501 | VAV | Variable Air Volume
RDC_NB_1F_VAV5510_EV5511 | VAV | Variable Air Volume
RDC_NB_1F_VAV5515_EV5516 | VAV | Variable Air Volume
RDC_NB_1F_VAV5520_EV5521 | VAV | Variable Air Volume
RDC_NB_1F_VAV5525_EV5526 | VAV | Variable Air Volume
RDC_NB_1F_VAV5535_EV5536 | VAV | Variable Air Volume
RDC_NB_1F_VAV5540_EV5541 | VAV | Variable Air Volume
RDC_NB_1F_VAV5550_VEV5551 | VAV | Variable Air Volume
RDC_NB_1F_VAV5560_VEV5561 | VAV | Variable Air Volume
RDC_NB_1F_VAV5570 | VAV | Variable Air Volume
RDC_NB_1F_VAV5571 | VAV | Variable Air Volume
RDC_NB_1F_VAV5580_VEV5581 | VAV | Variable Air Volume
RDC_NB_1F_VAV5590 | VAV | Variable Air Volume
RDC_NB_1F_VAV5600_VEV5601 | VAV | Variable Air Volume
RDC_NB_1F_VAV5610_VEV5611 | VAV | Variable Air Volume
RDC_NB_1F_VAV5620_VEV5622 | VAV | Variable Air Volume
RDC_NB_1F_VAV5621_VEV5623 | VAV | Variable Air Volume
RDC_NB_1F_VAV5630_VEV5631 | VAV | Variable Air Volume
RDC_NB_1F_VAV5650 | VAV | Variable Air Volume
RDC_NB_1F_VAV5655_EV5656 | VAV | Variable Air Volume
RDC_NB_1F_VAV5660 | VAV | Variable Air Volume
RDC_NB_1F_VAV5665 | VAV | Variable Air Volume
RDC_NB_1F_VAV5670 | VAV | Variable Air Volume
RDC_NB_1F_VAV5675 | VAV | Variable Air Volume
RDC_NB_1F_VAV5680 | VAV | Variable Air Volume
RDC_NB_1F_VAV5685 | VAV | Variable Air Volume
RDC_NB_1F_VAV5690 | VAV | Variable Air Volume
RDC_NB_1F_VAV5695 | VAV | Variable Air Volume
RDC_NB_1F_VAV5700 | VAV | Variable Air Volume
RDC_NB_1F_VAV5705 | VAV | Variable Air Volume
RDC_NB_1F_VAV5710 | VAV | Variable Air Volume
RDC_NB_1F_VAV5715_EV5716 | VAV | Variable Air Volume
RDC_NB_1F_VAV5730_EV5731 | VAV | Variable Air Volume
RDC_NB_1F_VAV5735_EV5736 | VAV | Variable Air Volume
RDC_NB_1F_VAV5740_EV5741 | VAV | Variable Air Volume
RDC_NB_1F_VAV5745 | VAV | Variable Air Volume
RDC_NB_1F_VAV5760_EV5761 | VAV | Variable Air Volume
RDC_NB_1F_VAV5770_VEV5771 | VAV | Variable Air Volume
RDC_NB_1F_VAV5780_VEV5781 | VAV | Variable Air Volume
RDC_NB_1F_VAV5790 | VAV | Variable Air Volume
RDC_NB_1F_VAV5792_VEV5793 | VAV | Variable Air Volume
RDC_NB_1F_VAV5794_VEV5795A | VAV | Variable Air Volume
RDC_NB_1F_VAV5800_VEV5801 | VAV | Variable Air Volume
RDC_NB_1F_VAV5810 | VAV | Variable Air Volume
RDC_NB_1F_VAV5814 | VAV | Variable Air Volume
RDC_NB_1F_VAV5835_EV5836 | VAV | Variable Air Volume
RDC_NB_1F_VAV5840 | VAV | Variable Air Volume
RDC_NB_1F_VAV5845 | VAV | Variable Air Volume
RDC_NB_1F_VAV5850 | VAV | Variable Air Volume
RDC_NB_1F_VAV5855 | VAV | Variable Air Volume
RDC_NB_1F_VAV5860 | VAV | Variable Air Volume
RDC_NB_1F_VAV5865 | VAV | Variable Air Volume
RDC_NB_1F_VAV5870 | VAV | Variable Air Volume
RDC_NB_1F_VAV5875 | VAV | Variable Air Volume
RDC_NB_1F_VAV5880 | VAV | Variable Air Volume
RDC_NB_1F_VAV5885 | VAV | Variable Air Volume
RDC_NB_1F_VAV5890 | VAV | Variable Air Volume
RDC_NB_1F_VAV5895 | VAV | Variable Air Volume
RDC_NB_1F_VAV5900 | VAV | Variable Air Volume
RDC_NB_1F_VAV5905 | VAV | Variable Air Volume
RDC_NB_1F_VAV5910 | VAV | Variable Air Volume
RDC_NB_1F_VAV5915 | VAV | Variable Air Volume
RDC_NB_1F_VAV5920 | VAV | Variable Air Volume
RDC_NB_1F_VAV5925 | VAV | Variable Air Volume
RDC_NB_1F_VAV5930 | VAV | Variable Air Volume
RDC_NB_1F_VAV5930P | VAV | Variable Air Volume
RDC_NB_1F_VAV5935 | VAV | Variable Air Volume
RDC_NB_1F_VAV5940 | VAV | Variable Air Volume
RDC_NB_1F_VAV5940P | VAV | Variable Air Volume
RDC_NB_1F_VAV6505_EV6506 | VAV | Variable Air Volume
RDC_NB_1F_VAV6510_EV6511 | VAV | Variable Air Volume
RDC_NB_1F_VAV6525_EV6526 | VAV | Variable Air Volume
RDC_NB_1F_VAV6530_VEV6531 | VAV | Variable Air Volume
RDC_NB_1F_VAV6540 | VAV | Variable Air Volume
RDC_NB_1F_VAV6550 | VAV | Variable Air Volume
RDC_NB_1F_VAV6551 | VAV | Variable Air Volume
RDC_NB_1F_VAV6560_VEV6561 | VAV | Variable Air Volume
RDC_NB_1F_VAV6570_VEV6571 | VAV | Variable Air Volume
RDC_NB_1F_VAV6590_VEV6591 | VAV | Variable Air Volume
RDC_NB_1F_VAV6600_VEV6601 | VAV | Variable Air Volume
RDC_NB_1F_VAV6610_VEV6611 | VAV | Variable Air Volume
RDC_NB_1F_VAV6620_VEV6621 | VAV | Variable Air Volume
RDC_NB_1F_VAV6630A | VAV | Variable Air Volume
RDC_NB_1F_VAV6630B | VAV | Variable Air Volume
RDC_NB_1F_VAV6631A | VAV | Variable Air Volume
RDC_NB_1F_VAV6631B | VAV | Variable Air Volume
RDC_NB_1F_VAV6650 | VAV | Variable Air Volume
RDC_NB_1F_VAV6655 | VAV | Variable Air Volume
RDC_NB_1F_VAV6660 | VAV | Variable Air Volume
RDC_NB_1F_VAV6665 | VAV | Variable Air Volume
RDC_NB_1F_VAV6670 | VAV | Variable Air Volume
RDC_NB_1F_VAV6675 | VAV | Variable Air Volume
RDC_NB_1F_VAV6680 | VAV | Variable Air Volume
RDC_NB_1F_VAV6685 | VAV | Variable Air Volume
RDC_NB_1F_VAV6690 | VAV | Variable Air Volume
RDC_NB_1F_VAV6695 | VAV | Variable Air Volume
RDC_NB_1F_VAV6700_EV6701 | VAV | Variable Air Volume
RDC_NB_1F_VAV6705 | VAV | Variable Air Volume
RDC_NB_1F_VAV6710 | VAV | Variable Air Volume
RDC_NB_1F_VAV6715 | VAV | Variable Air Volume
RDC_NB_1F_VAV6720 | VAV | Variable Air Volume
RDC_NB_1F_VAV6725_EV6726 | VAV | Variable Air Volume
RDC_NB_1F_VAV6750 | VAV | Variable Air Volume
RDC_NB_1F_VAV6760 | VAV | Variable Air Volume
RDC_NB_1F_VAV6761 | VAV | Variable Air Volume
RDC_NB_1F_VAV6800_VEV6801 | VAV | Variable Air Volume
RDC_NB_1F_VAV6810_VEV6811 | VAV | Variable Air Volume
RDC_NB_1F_VAV6820_VEV6821 | VAV | Variable Air Volume
RDC_NB_1F_VAV6830_VEV6831 | VAV | Variable Air Volume
RDC_NB_1F_VAV6840_VEV6841 | VAV | Variable Air Volume
RDC_NB_1F_VAV6850 | VAV | Variable Air Volume
RDC_NB_1F_VAV6851 | VAV | Variable Air Volume
RDC_NB_1F_VAV6870_EV6871 | VAV | Variable Air Volume
RDC_NB_1F_VAV6880 | VAV | Variable Air Volume
RDC_NB_1F_VAV6885 | VAV | Variable Air Volume
RDC_NB_1F_VAV6890_EV6891 | VAV | Variable Air Volume
RDC_NB_1F_VAV6895 | VAV | Variable Air Volume
RDC_NB_1F_VAV6900 | VAV | Variable Air Volume
RDC_NB_1F_VAV6905 | VAV | Variable Air Volume
RDC_NB_1F_VAV6910 | VAV | Variable Air Volume
RDC_NB_1F_VAV6915 | VAV | Variable Air Volume
RDC_NB_1F_VAV6920 | VAV | Variable Air Volume
RDC_NB_1F_VAV6925 | VAV | Variable Air Volume
RDC_NB_1F_VAV6930 | VAV | Variable Air Volume
RDC_NB_1F_VAV6935 | VAV | Variable Air Volume
RDC_NB_1F_VAV6940 | VAV | Variable Air Volume
RDC_NB_1F_VAV6945 | VAV | Variable Air Volume
RDC_NB_1F_VAV6950 | VAV | Variable Air Volume
RDC_NB_1F_VAV6955 | VAV | Variable Air Volume
RDC_NB_1F_VAV6960 | VAV | Variable Air Volume
RDC_NB_1F_VAV6965 | VAV | Variable Air Volume
RDC_NB_1F_VAV6967 | VAV | Variable Air Volume
RDC_NB_1F_VAV6968 | VAV | Variable Air Volume
RDC_NB_1F_VAV6970_EV6971 | VAV | Variable Air Volume
RDC_NB_1F_VAV6972 | VAV | Variable Air Volume
RDC_NB_1F_VAV6974 | VAV | Variable Air Volume
RDC_NB_1F_VAV6976 | VAV | Variable Air Volume
RDC_NB_1F_VAV6978 | VAV | Variable Air Volume
RDC_NB_1F_VAV6979P | VAV | Variable Air Volume
RDC_NB_1F_VAV6980P | VAV | Variable Air Volume
RDC_NB_1F_VAV7510_VEV7511 | VAV | Variable Air Volume
RDC_NB_1F_VAV7530_VEV7532 | VAV | Variable Air Volume
RDC_NB_1F_VAV7531_VEV7533 | VAV | Variable Air Volume
RDC_NB_1F_VAV7540_VEV7541 | VAV | Variable Air Volume
RDC_NB_1F_VAV7550_VEV7551 | VAV | Variable Air Volume
RDC_NB_1F_VAV7560_VEV7561 | VAV | Variable Air Volume
RDC_NB_1F_VAV7570_VEV7571 | VAV | Variable Air Volume
RDC_NB_1F_VAV7580_VEV7581 | VAV | Variable Air Volume
RDC_NB_1F_VAV7600_VEV7601 | VAV | Variable Air Volume
RDC_NB_1F_VAV7620 | VAV | Variable Air Volume
RDC_NB_1F_VAV7625 | VAV | Variable Air Volume
RDC_NB_1F_VAV7630 | VAV | Variable Air Volume
RDC_NB_1F_VAV7635 | VAV | Variable Air Volume
RDC_NB_1F_VAV7640 | VAV | Variable Air Volume
RDC_NB_1F_VAV7645 | VAV | Variable Air Volume
RDC_NB_1F_VAV7650 | VAV | Variable Air Volume
RDC_NB_1F_VAV7655 | VAV | Variable Air Volume
RDC_NB_1F_VAV7660 | VAV | Variable Air Volume
RDC_NB_1F_VAV7665_EV7666 | VAV | Variable Air Volume
RDC_NB_1F_VAV7670 | VAV | Variable Air Volume
RDC_NB_1F_VAV7675 | VAV | Variable Air Volume
RDC_NB_1F_VAV7680_EV7681 | VAV | Variable Air Volume
RDC_NB_1F_VAV7685 | VAV | Variable Air Volume
RDC_NB_1F_VAV7690 | VAV | Variable Air Volume
RDC_NB_1F_VAV7695 | VAV | Variable Air Volume
RDC_NB_1F_VAV7700_EV7701 | VAV | Variable Air Volume
RDC_NB_1F_VAV7705 | VAV | Variable Air Volume
RDC_NB_1F_VAV7710 | VAV | Variable Air Volume
RDC_NB_1F_VAV7730_VEV7731 | VAV | Variable Air Volume
RDC_NB_1F_VAV7740_VEV7741 | VAV | Variable Air Volume
RDC_NB_1F_VAV7750_VEV7751 | VAV | Variable Air Volume
RDC_NB_1F_VAV7770_VEV7771 | VAV | Variable Air Volume
RDC_NB_1F_VAV7780_VEV7781 | VAV | Variable Air Volume
RDC_NB_1F_VAV7800_VEV7801 | VAV | Variable Air Volume
RDC_NB_1F_VAV7810_VEV7811 | VAV | Variable Air Volume
RDC_NB_1F_VAV7820_VEV7822 | VAV | Variable Air Volume
RDC_NB_1F_VAV7821_VEV7823 | VAV | Variable Air Volume
RDC_NB_1F_VAV7830_7831 | VAV | Variable Air Volume
RDC_NB_1F_VAV7840_EV7841 | VAV | Variable Air Volume
RDC_NB_1F_VAV7845_EV7846 | VAV | Variable Air Volume
RDC_NB_1F_VAV7850 | VAV | Variable Air Volume
RDC_NB_1F_VAV7860 | VAV | Variable Air Volume
RDC_NB_1F_VAV7865 | VAV | Variable Air Volume
RDC_NB_1F_VAV7870 | VAV | Variable Air Volume
RDC_NB_1F_VAV7875 | VAV | Variable Air Volume
RDC_NB_1F_VAV7880 | VAV | Variable Air Volume
RDC_NB_1F_VAV7885 | VAV | Variable Air Volume
RDC_NB_1F_VAV7890 | VAV | Variable Air Volume
RDC_NB_1F_VAV7895 | VAV | Variable Air Volume
RDC_NB_1F_VAV7900 | VAV | Variable Air Volume
RDC_NB_1F_VAV7905 | VAV | Variable Air Volume
RDC_NB_1F_VAV7910 | VAV | Variable Air Volume
RDC_NB_1F_VAV7915 | VAV | Variable Air Volume
RDC_NB_1F_VAV7920 | VAV | Variable Air Volume
RDC_NB_1F_VAV7925 | VAV | Variable Air Volume
RDC_NB_1F_VAV7930 | VAV | Variable Air Volume
RDC_NB_1F_VAV7935 | VAV | Variable Air Volume
RDC_NB_1F_VAV7940 | VAV | Variable Air Volume
RDC_NB_1F_VAV7945 | VAV | Variable Air Volume
RDC_NB_1F_VAV7950 | VAV | Variable Air Volume
RDC_NB_1F_VAV7955 | VAV | Variable Air Volume
RDC_NB_1F_VAV7960 | VAV | Variable Air Volume
RDC_NB_1F_VAV7975P | VAV | Variable Air Volume
RDC_NB_1F_VAV7980P | VAV | Variable Air Volume
RDC_NB_1F_CAV4501 | CAV | Constant Air Volume
RDC_NB_1F_CAV4581A | CAV | Constant Air Volume
RDC_NB_1F_CAV4581B | CAV | Constant Air Volume
RDC_NB_1F_CAV4582 | CAV | Constant Air Volume
RDC_NB_1F_CAV4640_EV4641 | CAV | Constant Air Volume
RDC_NB_1F_CAV5530 | CAV | Constant Air Volume
RDC_NB_1F_CAV5640_EV5641 | CAV | Constant Air Volume
RDC_NB_1F_CAV5720_EV5721 | CAV | Constant Air Volume
RDC_NB_1F_CAV5750 | CAV | Constant Air Volume
RDC_NB_1F_CAV5755 | CAV | Constant Air Volume
RDC_NB_1F_CAV5818 | CAV | Constant Air Volume
RDC_NB_1F_CAV6500 | CAV | Constant Air Volume
RDC_NB_1F_CAV6515_EV6516 | CAV | Constant Air Volume
RDC_NB_1F_CAV6520 | CAV | Constant Air Volume
RDC_NB_1F_CAV6580 | CAV | Constant Air Volume
RDC_NB_1F_CAV6730 | CAV | Constant Air Volume
RDC_NB_1F_CAV6740_EV6741 | CAV | Constant Air Volume
RDC_NB_1F_CAV6790_CEV6791 | CAV | Constant Air Volume
RDC_NB_1F_CAV7500_EV7501 | CAV | Constant Air Volume
RDC_NB_1F_CAV7520_CEV7521 | CAV | Constant Air Volume
RDC_NB_1F_CAV7590_CEV7591 | CAV | Constant Air Volume
RDC_NB_1F_CAV7610_CEV7611 | CAV | Constant Air Volume
RDC_NB_1F_CAV7720 | CAV | Constant Air Volume
RDC_NB_1F_CAV7760_CEV7761 | CAV | Constant Air Volume
RDC_NB_1F_CAV7790_CEV7791 | CAV | Constant Air Volume
RDC_NB_GF_CAV4030 | CAV | Constant Air Volume
RDC_NB_GF_CAV4035 | CAV | Constant Air Volume
RDC_NB_GF_CAV4170 | CAV | Constant Air Volume
RDC_NB_GF_CAV4315_EV4316 | CAV | Constant Air Volume
RDC_NB_GF_CAV5005 | CAV | Constant Air Volume
RDC_NB_GF_CAV5020_EV5021 | CAV | Constant Air Volume
RDC_NB_GF_CAV5160_EV5161 | CAV | Constant Air Volume
RDC_NB_GF_CAV5170 | CAV | Constant Air Volume
RDC_NB_GF_CAV5240_CEV5241 | CAV | Constant Air Volume
RDC_NB_GF_CAV5280 | CAV | Constant Air Volume
RDC_NB_GF_CAV5290_EV5291 | CAV | Constant Air Volume
RDC_NB_GF_CAV5320 | CAV | Constant Air Volume
RDC_NB_GF_CAV5350 | CAV | Constant Air Volume
RDC_NB_GF_CAV5375 | CAV | Constant Air Volume
RDC_NB_GF_CAV6005 | CAV | Constant Air Volume
RDC_NB_GF_CAV6015_EV6016 | CAV | Constant Air Volume
RDC_NB_GF_CAV6020 | CAV | Constant Air Volume
RDC_NB_GF_CAV6280_EV6281 | CAV | Constant Air Volume
RDC_NB_GF_CAV7005_EV7006 | CAV | Constant Air Volume
RDC_NB_GF_CAV7380_EV7381 | CAV | Constant Air Volume
RDC_SB_1F_CAV0501 | CAV | Constant Air Volume
RDC_SB_1F_CAV0502 | CAV | Constant Air Volume
RDC_SB_1F_CAV0503 | CAV | Constant Air Volume
RDC_SB_1F_CAV0504 | CAV | Constant Air Volume
RDC_SB_1F_CAV0505 | CAV | Constant Air Volume
RDC_SB_1F_CAV0515 | CAV | Constant Air Volume
RDC_SB_1F_CAV0516 | CAV | Constant Air Volume
RDC_SB_1F_CAV0517 | CAV | Constant Air Volume
RDC_SB_1F_CAV0524 | CAV | Constant Air Volume
RDC_SB_1F_CAV0525 | CAV | Constant Air Volume
RDC_SB_1F_CAV0534 | CAV | Constant Air Volume
RDC_SB_1F_CAV0535 | CAV | Constant Air Volume
RDC_SB_1F_CAV1504 | CAV | Constant Air Volume
RDC_SB_1F_CAV1535 | CAV | Constant Air Volume
RDC_SB_1F_CAV1537 | CAV | Constant Air Volume
RDC_SB_1F_CAV1541 | CAV | Constant Air Volume
RDC_SB_1F_CAV2507 | CAV | Constant Air Volume
RDC_SB_GF_CAV0004 | CAV | Constant Air Volume
RDC_SB_GF_CAV0005 | CAV | Constant Air Volume
RDC_SB_GF_CAV0006 | CAV | Constant Air Volume
RDC_SB_GF_CAV0015 | CAV | Constant Air Volume
RDC_SB_GF_CAV0020 | CAV | Constant Air Volume
RDC_SB_GF_CAV0021 | CAV | Constant Air Volume
RDC_SB_GF_CAV0022 | CAV | Constant Air Volume
RDC_SB_GF_CAV0023 | CAV | Constant Air Volume
RDC_SB_GF_CAV0024 | CAV | Constant Air Volume
RDC_SB_GF_CAV1001 | CAV | Constant Air Volume
RDC_SB_GF_CAV1002 | CAV | Constant Air Volume
RDC_SB_GF_CAV1005 | CAV | Constant Air Volume
RDC_SB_GF_CAV1006 | CAV | Constant Air Volume
RDC_SB_GF_CAV1007 | CAV | Constant Air Volume
RDC_SB_GF_CAV1009 | CAV | Constant Air Volume
RDC_SB_GF_CAV2001 | CAV | Constant Air Volume
RDC_NB_1F_FCU4910 | FCU | Fan Coil Unit
RDC_NB_1F_FCU4914 | FCU | Fan Coil Unit
RDC_NB_1F_FCU4915 | FCU | Fan Coil Unit
RDC_NB_1F_FCU4916 | FCU | Fan Coil Unit
RDC_NB_1F_FCU4917 | FCU | Fan Coil Unit
RDC_NB_1F_FCU5983 | FCU | Fan Coil Unit
RDC_NB_1F_FCU5984 | FCU | Fan Coil Unit
RDC_NB_1F_FCU5985 | FCU | Fan Coil Unit
RDC_NB_1F_FCU5986 | FCU | Fan Coil Unit
RDC_NB_1F_FCU5987 | FCU | Fan Coil Unit
RDC_NB_1F_FCU5993 | FCU | Fan Coil Unit
RDC_NB_1F_FCU5994 | FCU | Fan Coil Unit
RDC_NB_1F_FCU6988 | FCU | Fan Coil Unit
RDC_NB_1F_FCU6989 | FCU | Fan Coil Unit
RDC_NB_1F_FCU6990 | FCU | Fan Coil Unit
RDC_NB_1F_FCU6991 | FCU | Fan Coil Unit
RDC_NB_1F_FCU6992 | FCU | Fan Coil Unit
RDC_NB_1F_FCU7790 | FCU | Fan Coil Unit
RDC_NB_1F_FCU7984 | FCU | Fan Coil Unit
RDC_NB_1F_FCU7985 | FCU | Fan Coil Unit
RDC_NB_1F_FCU7986 | FCU | Fan Coil Unit
RDC_NB_1F_FCU7987 | FCU | Fan Coil Unit
RDC_NB_1F_FCU7988 | FCU | Fan Coil Unit
RDC_NB_1F_FCU7989 | FCU | Fan Coil Unit
RDC_NB_2F_FCU4918 | FCU | Fan Coil Unit
RDC_NB_2F_FCU4919 | FCU | Fan Coil Unit
RDC_NB_2F_FCU5988 | FCU | Fan Coil Unit
RDC_NB_2F_FCU5989 | FCU | Fan Coil Unit
RDC_NB_2F_FCU5990 | FCU | Fan Coil Unit
RDC_NB_2F_FCU6993 | FCU | Fan Coil Unit
RDC_NB_2F_FCU6994 | FCU | Fan Coil Unit
RDC_NB_2F_FCU6995 | FCU | Fan Coil Unit
RDC_NB_2F_FCU6996 | FCU | Fan Coil Unit
RDC_NB_2F_FCU7991 | FCU | Fan Coil Unit
RDC_NB_2F_FCU7992 | FCU | Fan Coil Unit
RDC_NB_GF_FCU4911 | FCU | Fan Coil Unit
RDC_NB_GF_FCU4912 | FCU | Fan Coil Unit
RDC_NB_GF_FCU4913 | FCU | Fan Coil Unit
RDC_NB_GF_FCU4920 | FCU | Fan Coil Unit
RDC_NB_GF_FCU5980 | FCU | Fan Coil Unit
RDC_NB_GF_FCU5981 | FCU | Fan Coil Unit
RDC_NB_GF_FCU5982 | FCU | Fan Coil Unit
RDC_NB_GF_FCU5991 | FCU | Fan Coil Unit
RDC_NB_GF_FCU5992 | FCU | Fan Coil Unit
RDC_NB_GF_FCU6981 | FCU | Fan Coil Unit
RDC_NB_GF_FCU6982 | FCU | Fan Coil Unit
RDC_NB_GF_FCU6983 | FCU | Fan Coil Unit
RDC_NB_GF_FCU6984 | FCU | Fan Coil Unit
RDC_NB_GF_FCU6985 | FCU | Fan Coil Unit
RDC_NB_GF_FCU6986 | FCU | Fan Coil Unit
RDC_NB_GF_FCU6987 | FCU | Fan Coil Unit
RDC_NB_GF_FCU7981 | FCU | Fan Coil Unit
RDC_NB_GF_FCU7982 | FCU | Fan Coil Unit
RDC_NB_GF_FCU7983 | FCU | Fan Coil Unit
RDC_NB_SB_Walkway_FCU9001 | FCU | Fan Coil Unit
RDC_NB_SB_Walkway_FCU9002 | FCU | Fan Coil Unit
RDC_NB_SB_Walkway_FCU9003 | FCU | Fan Coil Unit
RDC_NB_SB_Walkway_FCU9004 | FCU | Fan Coil Unit
RDC_NB_SB_Walkway_FCU9005 | FCU | Fan Coil Unit
RDC_SB_1F_FCU0501 | FCU | Fan Coil Unit
RDC_SB_1F_FCU0502 | FCU | Fan Coil Unit
RDC_SB_1F_FCU0503 | FCU | Fan Coil Unit
RDC_SB_1F_FCU1501 | FCU | Fan Coil Unit
RDC_SB_1F_FCU1502 | FCU | Fan Coil Unit
RDC_SB_1F_FCU1503 | FCU | Fan Coil Unit
RDC_SB_1F_FCU2501 | FCU | Fan Coil Unit
RDC_SB_1F_FCU2502 | FCU | Fan Coil Unit
RDC_SB_1F_FCU2503 | FCU | Fan Coil Unit
RDC_SB_1F_FCU2504 | FCU | Fan Coil Unit
RDC_SB_1F_FCU2505 | FCU | Fan Coil Unit
RDC_SB_1F_FCU3501 | FCU | Fan Coil Unit
RDC_SB_2F_FCU0201 | FCU | Fan Coil Unit
RDC_SB_2F_FCU0202 | FCU | Fan Coil Unit
RDC_SB_2F_FCU0203 | FCU | Fan Coil Unit
RDC_SB_2F_FCU0204 | FCU | Fan Coil Unit
RDC_SB_2F_FCU0205 | FCU | Fan Coil Unit
RDC_SB_2F_FCU0206 | FCU | Fan Coil Unit
RDC_SB_2F_FCU0207 | FCU | Fan Coil Unit
RDC_SB_2F_FCU0208 | FCU | Fan Coil Unit
RDC_SB_2F_FCU1201 | FCU | Fan Coil Unit
RDC_SB_2F_FCU1202 | FCU | Fan Coil Unit
RDC_SB_2F_FCU2201 | FCU | Fan Coil Unit
RDC_SB_2F_FCU2202 | FCU | Fan Coil Unit
RDC_SB_2F_FCU2203 | FCU | Fan Coil Unit
RDC_SB_2F_FCU2204 | FCU | Fan Coil Unit
RDC_SB_2F_FCU2205 | FCU | Fan Coil Unit
RDC_SB_2F_FCU2206 | FCU | Fan Coil Unit
RDC_SB_2F_FCU2207 | FCU | Fan Coil Unit
RDC_SB_2F_FCU2208 | FCU | Fan Coil Unit
RDC_SB_2F_FCU2209 | FCU | Fan Coil Unit
RDC_SB_2F_FCU2210 | FCU | Fan Coil Unit
RDC_SB_GF_FCU0001 | FCU | Fan Coil Unit
RDC_SB_GF_FCU1001 | FCU | Fan Coil Unit
RDC_SB_GF_FCU1002 | FCU | Fan Coil Unit
RDC_SB_GF_FCU1003 | FCU | Fan Coil Unit
RDC_SB_GF_FCU1004 | FCU | Fan Coil Unit
RDC_SB_GF_FCU1005 | FCU | Fan Coil Unit
RDC_SB_GF_FCU1006 | FCU | Fan Coil Unit
RDC_SB_GF_FCU1007 | FCU | Fan Coil Unit
RDC_SB_GF_FCU1008 | FCU | Fan Coil Unit
RDC_SB_GF_FCU2001 | FCU | Fan Coil Unit
RDC_SB_GF_FCU2002 | FCU | Fan Coil Unit
RDC_SB_GF_FCU2003 | FCU | Fan Coil Unit
RDC_SB_GF_FCU2004 | FCU | Fan Coil Unit
RDC_SB_GF_FCU2005 | FCU | Fan Coil Unit
RDC_SB_GF_FCU3001 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8001 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8002 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8003 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8004 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8005 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8006 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8007 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8008 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8009 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8010 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8011 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8012 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8013 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8014 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8502 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8503 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8504 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8505 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8512 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8513 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8514 | FCU | Fan Coil Unit
RDC_UB_GF_FCU8515 | FCU | Fan Coil Unit
RDC_UB_MF_FCU8501 | FCU | Fan Coil Unit
RDC_UB_MF_FCU8506 | FCU | Fan Coil Unit
RDC_UB_MF_FCU8507 | FCU | Fan Coil Unit
RDC_UB_MF_FCU8508 | FCU | Fan Coil Unit
RDC_UB_MF_FCU8509 | FCU | Fan Coil Unit
RDC_UB_MF_FCU8510 | FCU | Fan Coil Unit
RDC_UB_MF_FCU8511 | FCU | Fan Coil Unit
RDC_NB_CHW_HEX01 | HEX | Heat Exchanger
RDC_NB_CHW_HEX02 | HEX | Heat Exchanger
RDC_SB_CHW_Hex01 | HEX | Heat Exchanger
RDC_SB_CHW_Hex02 | HEX | Heat Exchanger
RDC_UB_CHW_HEX01 | HEX | Heat Exchanger
RDC_UB_CHW_HEX02 | HEX | Heat Exchanger
RDC_UB_CHW_HEX03 | HEX | Heat Exchanger
RDC_NB_CHW_P01 | CHW Pump | Chilled Water Pump
RDC_NB_CHW_P02 | CHW Pump | Chilled Water Pump
RDC_NB_CHW_P03 | CHW Pump | Chilled Water Pump
RDC_SB_CH_Pmp01 | CHW Pump | Chilled Water Pump
RDC_SB_CH_Pmp02 | CHW Pump | Chilled Water Pump
RDC_SB_CHW_Pmp01 | CHW Pump | Chilled Water Pump
RDC_UB_CHW_Pmp01 | CHW Pump | Chilled Water Pump
RDC_UB_CHW_Pmp02 | CHW Pump | Chilled Water Pump
RDC_UB_CHW_Pmp03 | CHW Pump | Chilled Water Pump
UB_GEN1 | Generator | Generator
UB_GEN2 | Generator | Generator
UB_GEN3 | Generator | Generator
RDC_NB_1F_VEV5791 | VEV | VEV
RDC_NB_GF_VEV4041 | VEV | VEV
RDC_NB_1F_VEV5811A | VEV | VEV
RDC_NB_GF_VEV4213A | VEV | VEV
RDC_NB_1F_VEV5821 | VEV | VEV
RDC_NB_GF_VEV5052A | VEV | VEV
RDC_NB_1F_VEV6553 | VEV | VEV
RDC_NB_GF_VEV7073 | VEV | VEV
RDC_NB_GF_VEV5071 | VEV | VEV
RDC_NB_GF_VEV7023A | VEV | VEV
RDC_NB_GF_VEV5092 | VEV | VEV
RDC_NB_1F_VEV6751 | VEV | VEV
RDC_NB_GF_VEV7301 | VEV | VEV
RDC_NB_1F_VEV6763 | VEV | VEV
RDC_NB_1F_VEV4586A | VEV | VEV
RDC_NB_GF_VEV5231 | VEV | VEV
RDC_NB_1F_VEV4602 | VEV | VEV
RDC_NB_GF_VEV5182A | VEV | VEV
RDC_NB_1F_VEV5572 | VEV | VEV
RDC_NB_1F_VEV5591 | VEV | VEV
RDC_NB_1F_VEV4585A | VEV | VEV
RDC_NB_1F_VEV4585B | VEV | VEV
RDC_NB_1F_VEV4586B | VEV | VEV
RDC_NB_1F_VEV5573A | VEV | VEV
RDC_NB_1F_VEV5573B | VEV | VEV
RDC_NB_1F_VEV5811B | VEV | VEV
RDC_NB_1F_VEV5795B | VEV | VEV
RDC_NB_1F_VEV6552 | VEV | VEV
RDC_NB_1F_VEV6541 | VEV | VEV
RDC_NB_1F_VEV6762 | VEV | VEV
RDC_NB_GF_VEV4213B | VEV | VEV
RDC_NB_GF_VEV5055 | VEV | VEV
RDC_NB_GF_VEV5052B | VEV | VEV
RDC_NB_GF_VEV5182B | VEV | VEV
RDC_NB_GF_VEV5221 | VEV | VEV
RDC_NB_GF_VEV5211 | VEV | VEV
RDC_NB_GF_VEV7022B | VEV | VEV
RDC_NB_GF_VEV7022A | VEV | VEV
RDC_NB_GF_VEV7024B | VEV | VEV
RDC_NB_GF_VEV7024A | VEV | VEV
RDC_NB_GF_VEV7023B | VEV | VEV
RDC_NB_GF_VEV7072B | VEV | VEV
RDC_NB_GF_VEV7072A | VEV | VEV
RDC_NB_GF_VEV7241B | VEV | VEV
RDC_NB_GF_EAV4261 | EAV | EAV
RDC_NB_1F_EAV4500 | EAV | EAV
RDC_NB_1F_EAV6661 | EAV | EAV
RDC_NB_GF_EAV4286 | EAV | EAV
RDC_NB_1F_EAV4661 | EAV | EAV
RDC_NB_GF_EAV4311 | EAV | EAV
RDC_NB_1F_EAV6676 | EAV | EAV
RDC_NB_1F_EAV4686 | EAV | EAV
RDC_NB_1F_EAV6691 | EAV | EAV
RDC_NB_GF_EAV5026 | EAV | EAV
RDC_NB_1F_EAV4711 | EAV | EAV
RDC_NB_GF_EAV5163 | EAV | EAV
RDC_NB_1F_EAV6936 | EAV | EAV
RDC_NB_1F_EAV4736 | EAV | EAV
RDC_NB_GF_EAV6127 | EAV | EAV
RDC_NB_1F_EAV6961 | EAV | EAV
RDC_NB_1F_EAV5502 | EAV | EAV
RDC_NB_GF_EAV6141 | EAV | EAV
RDC_NB_1F_EAV6969 | EAV | EAV
RDC_NB_1F_EAV5503 | EAV | EAV
RDC_NB_GF_EAV6156 | EAV | EAV
RDC_NB_1F_EAV7631 | EAV | EAV
RDC_NB_1F_EAV5686 | EAV | EAV
RDC_NB_GF_EAV6176 | EAV | EAV
RDC_NB_1F_EAV7646 | EAV | EAV
RDC_NB_1F_EAV5747 | EAV | EAV
RDC_NB_GF_EAV6356 | EAV | EAV
RDC_NB_1F_EAV7661 | EAV | EAV
RDC_NB_1F_EAV5891 | EAV | EAV
RDC_NB_GF_EAV6381 | EAV | EAV
RDC_NB_1F_EAV7663 | EAV | EAV
RDC_NB_1F_EAV5921 | EAV | EAV
RDC_NB_GF_EAV6401 | EAV | EAV
RDC_NB_1F_EAV7711 | EAV | EAV
RDC_NB_1F_EAV5941 | EAV | EAV
RDC_NB_GF_EAV7091 | EAV | EAV
RDC_NB_1F_EAV7712 | EAV | EAV
RDC_NB_1F_EAV6528 | EAV | EAV
RDC_NB_1F_EAV7861 | EAV | EAV
RDC_NB_GF_EAV7106 | EAV | EAV
RDC_NB_1F_EAV7916 | EAV | EAV
RDC_NB_GF_EAV7121 | EAV | EAV
RDC_NB_2F_EAV4920 | EAV | EAV
RDC_NB_GF_EAV7122 | EAV | EAV
RDC_NB_2F_EAV6981 | EAV | EAV
RDC_NB_GF_EAV7396 | EAV | EAV
RDC_NB_GF_EAV4028 | EAV | EAV
RDC_NB_GF_EAV7426 | EAV | EAV
RDC_NB_GF_EAV4236 | EAV | EAV
RDC_NB_GF_EAV7461 | EAV | EAV
RDC_NB_GF_EAV7486 | EAV | EAV
RDC_NB_1F_FEV5772 | FEV | FEV
RDC_NB_1F_FEV4587 | FEV | FEV
RDC_NB_1F_FEV6731 | FEV | FEV
RDC_NB_1F_FEV5796 | FEV | FEV
RDC_NB_1F_FEV4588 | FEV | FEV
RDC_NB_1F_FEV5812 | FEV | FEV
RDC_NB_1F_FEV6764 | FEV | FEV
RDC_NB_1F_FEV4603 | FEV | FEV
RDC_NB_1F_FEV5813 | FEV | FEV
RDC_NB_1F_FEV6765 | FEV | FEV
RDC_NB_1F_FEV4604 | FEV | FEV
RDC_NB_1F_FEV6554 | FEV | FEV
RDC_NB_1F_FEV6766 | FEV | FEV
RDC_NB_1F_FEV4605 | FEV | FEV
RDC_NB_1F_FEV6555 | FEV | FEV
RDC_NB_1F_FEV6852 | FEV | FEV
RDC_NB_1F_FEV4606 | FEV | FEV
RDC_NB_1F_FEV6853 | FEV | FEV
RDC_NB_1F_FEV4622 | FEV | FEV
RDC_NB_1F_FEV6602 | FEV | FEV
RDC_NB_1F_FEV6854 | FEV | FEV
RDC_NB_1F_FEV5574 | FEV | FEV
RDC_NB_1F_FEV6632 | FEV | FEV
RDC_NB_1F_FEV6855 | FEV | FEV
RDC_NB_1F_FEV5575 | FEV | FEV
RDC_NB_1F_FEV6633 | FEV | FEV
RDC_NB_1F_FEV5624 | FEV | FEV
RDC_NB_1F_FEV6634 | FEV | FEV
RDC_NB_1F_FEV6856 | FEV | FEV
RDC_NB_1F_FEV6635 | FEV | FEV
RDC_NB_1F_FEV6857 | FEV | FEV
RDC_NB_1F_FEV6636 | FEV | FEV
RDC_NB_1F_FEV6858 | FEV | FEV
RDC_NB_1F_FEV6637 | FEV | FEV
RDC_NB_1F_FEV6859 | FEV | FEV
RDC_NB_1F_FEV6638 | FEV | FEV
RDC_NB_1F_FEV7522 | FEV | FEV
RDC_NB_1F_FEV6639 | FEV | FEV
RDC_NB_1F_FEV7602 | FEV | FEV
RDC_NB_1F_FEV7824 | FEV | FEV
RDC_NB_GF_FEV4193 | FEV | FEV
RDC_NB_GF_FEV5223 | FEV | FEV
RDC_NB_GF_FEV5073 | FEV | FEV
RDC_NB_GF_FEV4194 | FEV | FEV
RDC_NB_GF_FEV5271 | FEV | FEV
RDC_NB_GF_FEV5074 | FEV | FEV
RDC_NB_GF_FEV4214 | FEV | FEV
RDC_NB_GF_FEV5272 | FEV | FEV
RDC_NB_GF_FEV5082 | FEV | FEV
RDC_NB_GF_FEV4215 | FEV | FEV
RDC_NB_GF_FEV5273 | FEV | FEV
RDC_NB_GF_FEV5083 | FEV | FEV
RDC_NB_GF_FEV4216 | FEV | FEV
RDC_NB_GF_FEV5274 | FEV | FEV
RDC_NB_GF_FEV5093 | FEV | FEV
RDC_NB_GF_FEV5053 | FEV | FEV
RDC_NB_GF_FEV5275 | FEV | FEV
RDC_NB_GF_FEV5094 | FEV | FEV
RDC_NB_GF_FEV5062 | FEV | FEV
RDC_NB_GF_FEV5276 | FEV | FEV
RDC_NB_GF_FEV5072 | FEV | FEV
RDC_NB_GF_FEV5095A | FEV | FEV
RDC_NB_GF_FEV5277 | FEV | FEV
RDC_NB_GF_FEV5095B | FEV | FEV
RDC_NB_GF_FEV7052 | FEV | FEV
RDC_NB_GF_FEV5183 | FEV | FEV
RDC_NB_GF_FEV7053 | FEV | FEV
RDC_NB_GF_FEV5192A | FEV | FEV
RDC_NB_GF_FEV7062 | FEV | FEV
RDC_NB_GF_FEV5192B | FEV | FEV
RDC_NB_GF_FEV7074 | FEV | FEV
RDC_NB_GF_FEV5203 | FEV | FEV
RDC_NB_GF_FEV7075 | FEV | FEV
RDC_NB_GF_FEV5222 | FEV | FEV
RDC_NB_GF_FEV7232 | FEV | FEV
RDC_NB_GF_FEV7262 | FEV | FEV

## Controllable Asset Registry
Controllable Asset Registry
Tag No. | Equipment Type | Inluded/ Not Inlcuded | ROOM NAME AS PER DRAWINGS |  | ROOM NAME PER VAV / FCU LIST (WHERE DIFFERENT) | ROOM PER BMS SCREEN | BMS SCREEN (IMAGE FILE)
QNL
AHUB001 | AHU | Not Included | Basement Level Zone 4 Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
AHUB002 | AHU | Not Included | Basement Level Zone 1 Plant Room 1 B.063 | entity:QNL_B_063_PLANT_ROOM_01
AHUB003 | AHU | Not Included | Basement Level Zone 1 Plant Room 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02
AHUB004 | AHU | Not Included | Basement Level Zone 2 Plant Room 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03
AHUB005 | AHU | Not Included | Basement Level Zone 4 Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
AHUB006 | AHU | Not Included | Basement Level Zone 4 Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
AHUB007 | AHU | Not Included | Basement Level Zone 4 Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
AHUB008 | AHU | Not Included | Basement Level Zone 4 Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
AHUB009 | AHU | Not Included | Basement Level Zone 2 Plant Room 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03
AHUB010 | AHU | Not Included | Basement Level Zone 1 Plant Room 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02
AHUB011 | AHU | Not Included | Basement Level Zone 1 Plant Room 1 B.063 | entity:QNL_B_063_PLANT_ROOM_01
AHUB012 | AHU | Not Included | Basement Level Zone 1 Plant Room 1 B.063 | entity:QNL_B_063_PLANT_ROOM_01
AHUB013 | AHU | Not Included | Basement Level Zone 1 Plant Room 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02
AHUB014 | AHU | Not Included | Basement Level Zone 2 Plant Room 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03
AHUB015 | AHU | Not Included | Basement Level Zone 2 Plant Room 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03
FCU_1F_001 | FCU | Not Included | IDF ROOM T1.323 | entity:QNL_T1_323_IDF_ROOM
FCU_1F_002 | FCU | Included | ICT Room 02 L1.030 | entity:QNL_L1_030_ICT_ROOM_02
FCU_1F_003 | FCU | Not Included | IDF Room 02 L1.099 | entity:QNL_L1_099_IDF_ROOM_02 |  | IDF Rm | QNL/FF-2.jpg
FCU_1F_004 | FCU | Included | BRIDGE CEILING VOID L1.BR6 | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID
FCU_1F_005 | FCU | Included | BRIDGE CEILING VOID L1.BR6 | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID
FCU_1F_006 | FCU | Included | BRIDGE CEILING VOID L1.BR6 | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID
FCU_1F_007 | FCU | Included | BRIDGE CEILING VOID L1.BR6 | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID
FCU_1F_008 | FCU | Included | BRIDGE CEILING VOID L1.BR6 | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID
FCU_1F_009 | FCU | Included | BRIDGE CEILING VOID L1.BR5 | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID
FCU_1F_010 | FCU | Included | BRIDGE CEILING VOID L1.BR5 | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID
FCU_1F_011 | FCU | Included | BRIDGE CEILING VOID L1.BR5 | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID
FCU_1F_012 | FCU | Included | BRIDGE CEILING VOID L1.BR5 | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID
FCU_1F_013 | FCU | Included | BRIDGE CEILING VOID L1.BR6 | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID
FCU_1F_014 | FCU | Included | BRIDGE CEILING VOID L1.BR4 | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID
FCU_1F_015 | FCU | Included | BRIDGE CEILING VOID L1.BR6 | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID
FCU_1F_016 | FCU | Included | BRIDGE CEILING | entity:QNL_L1_BC1_BRIDGE_CEILING
FCU_1F_017 | FCU | Included | VOID L1.BR4 | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID
FCU_1F_018 | FCU | Included | VOID L1.BR4 | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID
FCU_1F_019 | FCU | Included | BRIDGE CEILING VOID L1.BR5 | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID
FCU_1F_020 | FCU | Included | BRIDGE CEILING VOID L1.BR3 | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID
FCU_1F_021 | FCU | Included | BRIDGE CEILING VOID L1.BR5 | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID
FCU_1F_022 | FCU | Included | BRIDGE CEILING VOID L1.BR3 | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID
FCU_1F_023 | FCU | Included | BRIDGE CEILING VOID L1.BR3 | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID
FCU_1F_024 | FCU | Included | BRIDGE CEILING VOID L1.BR3 | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID
FCU_1F_025 | FCU | Included | BRIDGE CEILING VOID L1.BR2 | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID
FCU_1F_026 | FCU | Included | BRIDGE CEILING VOID L1.BR4 | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID
FCU_1F_027 | FCU | Included | BRIDGE CEILING VOID L1.BR2 | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID
FCU_1F_028 | FCU | Included | BRIDGE CEILING VOID L1.BR4 | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID
FCU_1F_029 | FCU | Included | BRIDGE CEILING VOID L1.BR2 | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID
FCU_1F_030 | FCU | Included | BRIDGE CEILING VOID L1.BR2 | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID
FCU_1F_031 | FCU | Included | BRIDGE CEILING VOID L1.BR1 | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID
FCU_1F_032 | FCU | Included | BRIDGE CEILING VOID L1.BR1 | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID
FCU_1F_033 | FCU | Included | BRIDGE CEILING VOID L1.BR1 | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID
FCU_1F_034 | FCU | Included | BRIDGE CEILING VOID L1.BR1 | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID
FCU_1F_035 | FCU | Included | BRIDGE CEILING VOID L1.BR2 | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID
FCU_1F_036 | FCU | Included | BRIDGE CEILING VOID L1.BR2 | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID
FCU_1F_037 | FCU | Included | BRIDGE CEILING VOID L1.BR3 | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID
FCU_1F_038 | FCU | Included | BRIDGE CEILING VOID L1.BR3 | entity:QNL_L1_BR3_BRIDGE_CEILING_VOID
FCU_1F_039 | FCU | Included | BRIDGE CEILING VOID L1.BR4 | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID
FCU_1F_040 | FCU | Included | BRIDGE CEILING VOID L1.BR4 | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID
FCU_1F_041 | FCU | Included | BRIDGE CEILING | entity:QNL_L1_BC2_BRIDGE_CEILING
FCU_1F_042 | FCU | Included | VOID L1.BR5 | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID
FCU_1F_043 | FCU | Included | BRIDGE CEILING VOID L1.BR6 | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID
FCU_1F_044 | FCU | Included | BRIDGE CEILING VOID L1.BR6 | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID
FCU_1F_045 | FCU | Included | BRIDGE CEILING VOID L1.BR6 | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID
FCU_1F_046 | FCU | Included | BRIDGE CEILING VOID L1.BR6 | entity:QNL_L1_BR6_BRIDGE_CEILING_VOID
FCU_1F_047 | FCU | Included | BRIDGE CEILING VOID L1.BR1 | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID
FCU_1F_048 | FCU | Included | BRIDGE CEILING VOID L1.BR1 | entity:QNL_L1_BR1_BRIDGE_CEILING_VOID
FCU_1F_049 | FCU | Included | BRIDGE CEILING VOID L1.BR2 | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID
FCU_1F_050 | FCU | Included | BRIDGE CEILING VOID L1.BR2 | entity:QNL_L1_BR2_BRIDGE_CEILING_VOID
FCU_1F_051 | FCU | Included | BRIDGE CEILING VOID L1.BR4 | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID
FCU_1F_052 | FCU | Included | BRIDGE CEILING VOID L1.BR4 | entity:QNL_L1_BR4_BRIDGE_CEILING_VOID
FCU_1F_053 | FCU | Included | BRIDGE CEILING VOID L1.BR5 | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID
FCU_1F_054 | FCU | Included | BRIDGE CEILING VOID L1.BR5 | entity:QNL_L1_BR5_BRIDGE_CEILING_VOID
FCU_1F_055 | FCU | Included | VESTIBULE L1 | entity:QNL_L1_990_VESTIBULE
FCU_1F_056 | FCU | Included | External Book Drop L1 | entity:QNL_L1_991_EXTERNAL_BOOK_DROP
FCU_1F_057 | FCU | Included | ILL DIRECTOR L1.144 | entity:QNL_L1_144_ILL_DIRECTOR
FCU_1F_058 | FCU | Included | ILL DIRECTOR L1.145 | entity:QNL_L1_144_ILL_DIRECTOR
FCU_1F_059 | FCU | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT
FCU_1F_060 | FCU | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT |  | Restaurant | QNL/FF-2.jpg
FCU_1F_061 | FCU | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT |  | Restaurant | QNL/FF-2.jpg
FCU_1F_062 | FCU | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT
FCU_1F_063 | FCU | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT
FCU_1F_064 | FCU | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT |  | Restaurant | QNL/FF-2.jpg
FCU_1F_065 | FCU | Not Included | BRIDGE IDF L1.BI | entity:QNL_L1_BI_BRIDGE_IDF
FCU_2F_001 | FCU | Not Included | IDF ROOM T1.275 | entity:QNL_T1_275_IDF_ROOM
FCU_2F_002 | FCU | Not Included | IDF ROOM T1.276 | entity:QNL_T1_276_IDF_ROOM
FCU_2F_003 | FCU | Not Included | IDF ROOM T1.171 | entity:QNL_T1_171_IDF_ROOM
FCU_2F_004 | FCU | Not Included | IDF ROOM T1.1714 | entity:QNL_T1_1714_IDF_ROOM
FCU_2F_005 | FCU | Not Included | MDF Room L2.009 | entity:QNL_L2_009_KDF_ROOM
FCU_2F_034 | FCU | Included | Auditorium High Levlel in Ceiling Void L2.087 | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID |  | Auditorium | QNL/SF-6.jpg
FCU_2F_035 | FCU | Included | Auditorium High Levlel in Ceiling Void L2.087 | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID |  | Auditorium | QNL/SF-6.jpg
FCU_2F_036 | FCU | Included | Auditorium High Levlel in Ceiling Void L2.087 | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID |  | Auditorium | QNL/SF-6.jpg
FCU_2F_037 | FCU | Included | Auditorium High Levlel in Ceiling Void L2.087 | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID
FCU_2F_038 | FCU | Included | Auditorium Booths L2.087 | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID
FCU_2F_039 | FCU | Included | Auditorium Booths L2.087 | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID
FCU_2F_040 | FCU | Included | Auditorium Booths L2.087 | entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID
FCU_2F_041 | FCU | Included | Bridge Raised Floor L2.088 | entity:QNL_L2_088_BRIDGE_RAISED_FLOOR
FCU_2F_042 | FCU | Included | STUDY AREA L2.088 | entity:QNL_L2_088_BRIDGE_RAISED_FLOOR
FCU_2F_043 | FCU | Included | Bridge L2.088 | entity:QNL_L2_088_BRIDGE_RAISED_FLOOR
FCU_2F_044 | FCU | Included | Bridge L2.088 | entity:QNL_L2_088_BRIDGE_RAISED_FLOOR
FCU_2F_045 | FCU | Included | Group Study Room L2.081 | entity:QNL_L2_081_GROUP_STUDY_ROOM |  | Group Study Rm | QNL/SF-6.jpg
FCU_2F_046 | FCU | Included | Group Study Room L2.076 | entity:QNL_L2_076_GROUP_STUDY_ROOM |  | Group Study Rm | QNL/SF-6.jpg
FCU_2F_047 | FCU | Included | Group Study Room L2.076 | entity:QNL_L2_076_GROUP_STUDY_ROOM |  | Group Study Rm | QNL/SF-6.jpg
FCU_2F_048 | FCU | Included | INDIVIDUAL STUDY ROOM L2.070 | entity:QNL_L2_070_INDIVISTUDY_ROOM
FCU_2F_049 | FCU | Included | INDIVIDUAL STUDY ROOM L2.070 | entity:QNL_L2_070_INDIVISTUDY_ROOM |  | Indv. Study Rm | QNL/SF-6.jpg
FCU_2F_050 | FCU | Included | INDIVIDUAL STUDY ROOM L2.070 | entity:QNL_L2_070_INDIVISTUDY_ROOM |  | Indv. Study Rm | QNL/SF-6.jpg
FCU_2F_051 | FCU | Included | INDIVIDUAL STUDY ROOM L2.073 | entity:QNL_L2_073_INDIVISTUDY_ROOM |  | Indv. Study Rm | QNL/SF-6.jpg
FCU_2F_052 | FCU | Included | INDIVIDUAL STUDY ROOM L2.073 | entity:QNL_L2_073_INDIVISTUDY_ROOM |  | Indv. Study Rm | QNL/SF-6.jpg
FCU_2F_053 | FCU | Included | INDIVIDUAL STUDY ROOM L2.073 | entity:QNL_L2_073_INDIVISTUDY_ROOM
FCU_2F_054 | FCU | Included | Lounge Area L2.088 | entity:QNL_L2_088_LOUNGE_AREA |  | Lounge area | QNL/SF-6.jpg
FCU_2F_055 | FCU | Included | Lounge Area L2.088 | entity:QNL_L2_088_LOUNGE_AREA |  | Lounge area | QNL/SF-6.jpg
FCU_2F_056 | FCU | Included | North East Core T1.021 | entity:QNL_T1_021_OPEN_STUDY_TERRACE
FCU_2F_057 | FCU | Included | North East Core T1.021 | entity:QNL_T1_021_OPEN_STUDY_TERRACE
FCU_2F_058 | FCU | Included | North East Core T1.021 | entity:QNL_T1_021_OPEN_STUDY_TERRACE
FCU_2F_059 | FCU | Included | North East Core T1.021 | entity:QNL_T1_021_OPEN_STUDY_TERRACE
FCU_2F_060 | FCU | Included | North West Core T1.020 | entity:QNL_T1_020_OPEN_LOUNGE_TERRACE
FCU_2F_061 | FCU | Included | North West Core T1.020 | entity:QNL_T1_020_OPEN_LOUNGE_TERRACE
FCU_2F_062 | FCU | Included | North West Core T1.020 | entity:QNL_T1_020_OPEN_LOUNGE_TERRACE
FCU_B_001 | FCU | Not Included | IDF ROOM B.155 | entity:QNL_B_155_FACULTY_CARRELS |  | IDF Rm | QNL/BF-8.jpg
FCU_B_002 | FCU | Included | FUMIGATION B.085 | entity:QNL_B_085_FUMIGATION_ROOM
FCU_B_003 | FCU | Not Included | IDF (Corridor) B.062 | entity:QNL_B_062_IDF_CORRIDOR |  | IDF | QNL/BF-2.jpg
FCU_B_004 | FCU | Not Included | IDF FM Storage B.215 | entity:QNL_B_215_IDF_FM_STORAGE |  | FM Storage | QNL/BF-10.jpg
FCU_B_005 | FCU | Not Included | HL Plant Room B.140 | entity:QNL_B_140_HL_PLANT_ROOM
FCU_B_006 | FCU | Not Included | Fire Command ROOM B.071 | entity:QNL_B_071_FIRE_COMMAND_ROOM
FCU_B_007 | FCU | Not Included | Sprinklers Pumps ROOM B.072 | entity:QNL_B_072_SPRIMKLERS_PUMPS_&_ZONES_VALVES
FCU_B_008 | FCU | Not Included | GAS SUPPRESSION ROOM B.087 | entity:QNL_B_087_GAS_SUPPRESSION_ROOM |  |  | QNL/BF-3.jpg
FCU_B_009 | FCU | Included | PEOPLE MOVER ROOM B.088 | entity:QNL_B_088_PEOPLE_MOVER_PLANT
FCU_B_010 | FCU | Not Included | Security Contol Room B.105 | entity:QNL_B_105_SECURITY_CONTOL_ROOM
FCU_B_011 | FCU | Not Included | Plant Room 1 B.063 | entity:QNL_B_063_PLANT_ROOM_01 |  | Plant Rm 1 | QNL/BF-2.jpg
FCU_B_012 | FCU | Not Included | Plant Room 1 B.063 | entity:QNL_B_063_PLANT_ROOM_01 |  | Plant Rm 1 | QNL/BF-2.jpg
FCU_B_013 | FCU | Not Included | Plant Room 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02 |  | Plant Rm 2 | QNL/BF-2.jpg
FCU_B_014 | FCU | Not Included | Plant Room 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02 |  | Plant Rm 2 | QNL/BF-2.jpg
FCU_B_015 | FCU | Not Included | Plant Room 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03 |  | Plant Rm 3 | QNL/BF-6.jpg
FCU_B_016 | FCU | Not Included | Plant Room 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03 |  | Plant Rm 3 | QNL/BF-6.jpg
FCU_B_017 | FCU | Not Included | Plant Room 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03 |  | Plant Rm 3 | QNL/BF-6.jpg
FCU_B_018 | FCU | Not Included | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04 |  | Plant Rm 4 | QNL/BF-10.jpg
FCU_B_019 | FCU | Not Included | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04 |  | Plant Rm 4 | QNL/BF-10.jpg
FCU_B_020 | FCU | Not Included | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04 |  | Plant Rm 4 | QNL/BF-10.jpg
FCU_B_021 | FCU | Not Included | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04 |  | Plant Rm 4 | QNL/BF-10.jpg
FCU_B_022 | FCU | Included | FM Storage B.210 | entity:QNL_B_210_FM_STORAGE |  | FM Storage | QNL/BF-10.jpg
FCU_B_023 | FCU | Included | FM Storage B.210 | entity:QNL_B_210_FM_STORAGE |  | FM Storage | QNL/BF-10.jpg
FCU_B_024 | FCU | Not Included | PH Plant ROOM B.211 | entity:QNL_B_211_PH_PLANT_ROOM |  | PH Plant | QNL/BF-10.jpg
FCU_B_025 | FCU | Not Included | MISTING PUMP ROOM B.212 | entity:QNL_B_212_MISTING_PUMP_ROOM
FCU_B_026 | FCU | Not Included | MISTING PUMP ROOM B.212 | entity:QNL_B_212_MISTING_PUMP_ROOM |  | Misting System | QNL/BF-10.jpg
FCU_B_027 | FCU | Included | Sorting Shelving Room B.121 | entity:QNL_B_121_SORTING_SHELVING_ROOM
FCU_B_028 | FCU | Included | Sorting Shelving Room B.121 | entity:QNL_B_121_SORTING_SHELVING_ROOM |  | Sorting Shelving Rm | QNL/BF-2.jpg
FCU_B_029 | FCU | Included | B.145.05 | entity:QNL_B_145_LOBY_&_CSECURITY
FCU_B_030 | FCU | Included | PUMP ROOM B.226 | entity:QNL_B_226_PUMP_ROOM |  | Pump Rm 4 | QNL/BF-10.jpg
FCU_B_031 | FCU | Not Included | IDF ROOM B.215A | entity:QNL_B_215A_IDF
FCU_B_032 | FCU | Included | Shell Space-Special Collection B.132 | entity:QNL_B_132_SHELL_SPACE-SPECIAL_COLLECTION |  | Shell Space-Special Collection | QNL/BF-3.jpg
FCU_B_033 | FCU | Included | Shell Space-Special Collection B.132 | entity:QNL_B_132_SHELL_SPACE-SPECIAL_COLLECTION |  | Shell Space-Special Collection | QNL/BF-3.jpg
FCU_B_034 | FCU | Included | Shell Space-Special Collection B.132 | entity:QNL_B_132_SHELL_SPACE-SPECIAL_COLLECTION |  | Shell Space-Special Collection | QNL/BF-3.jpg
FCU_B_035 | FCU | Included | Shell Space-Special Collection B.132 | entity:QNL_B_132_SHELL_SPACE-SPECIAL_COLLECTION |  | Shell Space-Special Collection | QNL/BF-3.jpg
FCU_B_036 | FCU | Included | IT Office B.122 | entity:QNL_B_122_IT_OFFICE
FCU_B_037 | FCU | Not Included | DIGITALIZATION SERVER SPACE B.215A | entity:QNL_B_215A_IDF
FCU_B_038 | FCU | Not Included | ELEC. B.145 | entity:QNL_B_145_LOBY_&_CSECURITY
VAV0001 | VAV
VAV_1F_S11_001 | VAV | Included | Group Study Room1 L1.026 | entity:QNL_L1_026_GROUP_STUDY_ROOM1
VAV_1F_S11_002 | VAV | Included | Group Study Room2 L1.027 | entity:QNL_L1_027_GROUP_STUDY_ROOM2 |  | Study Rm2 | QNL/FF.jpg
VAV_1F_S11_003 | VAV | Included | Group Study Room3 L1.028 | entity:QNL_L1_028_GROUP_STUDY_ROOM3 |  | Cell between Study Rm2 and Study Rm 4 | QNL/FF.jpg
VAV_1F_S11_004 | VAV | Included | Information Literacy Instr 1 L1.020 | entity:QNL_L1_020_INFO_LITERACY_INSTR1 |  | Info. Literacy Instr.1 | QNL/FF.jpg
VAV_1F_S11_005 | VAV | Included | Information Literacy Instr 1 L1.020 | entity:QNL_L1_020_INFO_LITERACY_INSTR1 |  | Info. Literacy Instr.1 | QNL/FF.jpg
VAV_1F_S11_006 | VAV | Included | Infor. Lteracy Instr.2 L1.021 | entity:QNL_L1_021_INFO_LITERACY_INSTR2 |  | Info. Literacy Instr.2 | QNL/FF.jpg
VAV_1F_S11_007 | VAV | Included | Infor. Lteracy Instr.2 L1.021 | entity:QNL_L1_021_INFO_LITERACY_INSTR2
VAV_1F_S11_008 | VAV | Included | Infor. Lteracy Instr.2 L1.021 | entity:QNL_L1_021_INFO_LITERACY_INSTR2
VAV_1F_S11_009 | VAV | Included | Infor. Lteracy Instr.2 L1.021 | entity:QNL_L1_021_INFO_LITERACY_INSTR2
VAV_1F_S11_010 | VAV | Included | Infor. Lteracy Instr.2 L1.021 | entity:QNL_L1_021_INFO_LITERACY_INSTR2 |  | Info. Literacy Instr.2 | QNL/FF.jpg
VAV_1F_S11_011 | VAV | Included | Infor. Lteracy Instr.2 L1.021 | entity:QNL_L1_021_INFO_LITERACY_INSTR2
VAV_1F_S11_012 | VAV | Included | Infor. Lteracy Instr.2 L1.021 | entity:QNL_L1_021_INFO_LITERACY_INSTR2
VAV_1F_S11_013 | VAV | Included | Infor. Lteracy Instr.2 L1.021 | entity:QNL_L1_021_INFO_LITERACY_INSTR2
VAV_1F_S11_014 | VAV | Included | Computer Classroom L1.022 | entity:QNL_L1_022_COMPUTER_CLASSROOM
VAV_1F_S11_015 | VAV | Included | Computer Classroom L1.022 | entity:QNL_L1_022_COMPUTER_CLASSROOM |  | Computer Class Rm | QNL/FF.jpg
VAV_1F_S11_016 | VAV | Included | Computer Classroom L1.022 | entity:QNL_L1_022_COMPUTER_CLASSROOM |  | Computer Class Rm | QNL/FF.jpg
VAV_1F_S11_017 | VAV | Included | Computer Classroom L1.022 | entity:QNL_L1_022_COMPUTER_CLASSROOM
VAV_1F_S11_018 | VAV | Included | Computer Classroom L1.022 | entity:QNL_L1_022_COMPUTER_CLASSROOM
VAV_1F_S11_019 | VAV | Included | Computer Classroom L1.022 | entity:QNL_L1_022_COMPUTER_CLASSROOM |  | Computer Classroom L1.022 | QNL/FF.jpg
VAV_1F_S11_020 | VAV | Included | Computer Classroom L1.022 | entity:QNL_L1_022_COMPUTER_CLASSROOM |  | Computer Class Rm | QNL/FF.jpg
VAV_1F_S11_021 | VAV | Included | Computer Classroom L1.022 | entity:QNL_L1_022_COMPUTER_CLASSROOM
VAV_1F_S11_022 | VAV | Included | Group Study Room 4 L1.029 | entity:QNL_L1_029_GROUP_STUDY_ROOM4 |  | Study Rm 4 | QNL/FF.jpg
VAV_1F_S11_087 | VAV | Included | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 | entity:QNL_L1023_2_CORRIDOR |  |  | QNL/FF-3.jpg
VAV_1F_S11_088 | VAV | Included | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 | entity:QNL_L1023_2_CORRIDOR |  |  | QNL/FF.jpg
VAV_1F_S11_089 | VAV | Included | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 | entity:QNL_L1023_2_CORRIDOR
VAV_1F_S11_090 | VAV | Included | CHILDRENS LIBRARY SLOPE CORRIDOR L1.023 | entity:QNL_L1023_2_CORRIDOR
VAV_1F_S15_001 | VAV | Included | Media Studio1 L1.063 | entity:QNL_L1_063_MEDIA_STUDIO_1
VAV_1F_S15_002 | VAV | Included | Media Studio1 L1.063 | entity:QNL_L1_063_MEDIA_STUDIO_1
VAV_1F_S15_003 | VAV | Included | Media Studio2 L1.065 | entity:QNL_L1_065_MEDIA_STUDIO_1 |  | Media Studio1 | QNL/FF-3.jpg
VAV_1F_S15_004 | VAV | Included | Media Studio2 L1.065 | entity:QNL_L1_065_MEDIA_STUDIO_1 |  | Media Studio1 | QNL/FF-3.jpg
VAV_1F_S15_005 | VAV | Not Included | Head Librarian Office L1.040 | entity:QNL_L1_040_HEAD_LIBRARIAN_OFFICE
VAV_1F_S15_006 | VAV | Included | Children Library - Pre School Reading & Playing L1.047 | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING |  | Children Library | QNL/FF.jpg
VAV_1F_S15_007 | VAV | Included | Children Library - Pre School Reading & Playing L1.047 | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING |  | Children Library | QNL/FF.jpg
VAV_1F_S15_008 | VAV | Included | Children Library - Pre School Reading & Playing L1.047 | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING |  | Children Library | QNL/FF.jpg
VAV_1F_S15_009 | VAV | Included | CHILDRENS LIBRARY-PRE SCHOOL COLLECTION L1.047 | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING |  |  | QNL/FF-2.jpg
VAV_1F_S15_010 | VAV | Included | CHILDRENS LIBRARY-PRE SCHOOL COLLECTION L1.047 | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING |  |  | QNL/FF-2.jpg
VAV_1F_S15_011 | VAV | Included | CHILDRENS LIBRARY-PRE SCHOOL COLLECTION L1.047 | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING
VAV_1F_S15_012 | VAV | Included | Staff Office L1.048 | entity:QNL_L1_048_STAFF_OFFICE |  | Yellow cell south of Staff Office | QNL/FF.jpg
VAV_1F_S15_021 | VAV | Included | Prayer Room (Female) L1.104 | entity:QNL_L1_104_PRAYER_ROOM_FEMALE
VAV_1F_S15_022 | VAV | Included | Prayer Room (Female) L1.104 | entity:QNL_L1_104_PRAYER_ROOM_FEMALE |  | Prayer Rm (Female) | QNL/FF-3.jpg
VAV_1F_S15_023 | VAV | Included | Prayer Room (Male) L1.104 | entity:QNL_L1_104_PRAYER_ROOM_FEMALE
VAV_1F_S15_024 | VAV | Included | Prayer Room (Male) L1.104 | entity:QNL_L1_104_PRAYER_ROOM_FEMALE
VAV_1F_S15_025 | VAV | Included | Ablution (Women) L1.106 | entity:QNL_L1_106_ABLUTIONWOMEN
VAV_1F_S15_038 | VAV | Included | Ablution (Men) L1.105 | entity:QNL_L1_105_ABLUTIONMEN
VAV_1F_S15_039 | VAV | Included | Green Room L1.002A | entity:QNL_L1_002A_GREEM_ROOM
VAV_1F_S15_039S | VAV | Included | Staff Office L1.048 | entity:QNL_L1_048_STAFF_OFFICE |  |  | QNL/FF.jpg
VAV_1F_S15_040 | VAV | Included | Green Room L1.002A | entity:QNL_L1_002A_GREEM_ROOM
VAV_1F_S15_096 | VAV | Included | Multipurpose Room L1.041 | entity:QNL_L1_041_MULTPURPOSE_ROOM |  | Multipurpose Rm | QNL/FF.jpg
VAV_1F_S15_097 | VAV | Included | Multipurpose Room L1.041 | entity:QNL_L1_041_MULTPURPOSE_ROOM |  | Multipurpose Rm | QNL/FF.jpg
VAV_1F_S15_098 | VAV | Included | Multipurpose Room L1.041 | entity:QNL_L1_041_MULTPURPOSE_ROOM |  | Multipurpose Rm | QNL/FF-2.jpg
VAV_2F_S10_001 | VAV | Included | GULF MATERIAL L2 | entity:QNL_L2_992_GULF_MATERIAL |  |  | QNL/SF-1.jpg
VAV_2F_S10_002 | VAV | Included | GULF MATERIAL L2 | entity:QNL_L2_992_GULF_MATERIAL |  |  | QNL/SF-1.jpg
VAV_2F_S10_003 | VAV | Included | GULF MATERIAL L2 | entity:QNL_L2_992_GULF_MATERIAL |  |  | QNL/SF-1.jpg
VAV_2F_S10_004 | VAV | Included | GULF MATERIAL L2 | entity:QNL_L2_992_GULF_MATERIAL |  |  | QNL/SF-1.jpg
VAV_2F_S10_005 | VAV | Included | GULF MATERIAL L2 | entity:QNL_L2_992_GULF_MATERIAL |  |  | QNL/SF-1.jpg
VAV_2F_S10_006 | VAV | Included | GULF MATERIAL L2 | entity:QNL_L2_992_GULF_MATERIAL
VAV_2F_S12_001 | VAV | Included | OPEN READING AREA L1.001 | entity:QNL_L1_001_OPEN_READING_AREA
VAV_2F_S12_002 | VAV | Included | OPEN READING AREA L1.001 | entity:QNL_L1_001_OPEN_READING_AREA
VAV_2F_S12_003 | VAV | Included | OPEN READING AREA L1.001 | entity:QNL_L1_001_OPEN_READING_AREA |  |  | QNL/SF-1.jpg
VAV_2F_S12_004 | VAV | Included | OPEN READING AREA L1.001 | entity:QNL_L1_001_OPEN_READING_AREA
VAV_2F_S12_005 | VAV | Included | OPEN READING AREA L1.001 | entity:QNL_L1_001_OPEN_READING_AREA
VAV_2F_S12_006 | VAV | Included | OPEN READING AREA L1.001 | entity:QNL_L1_001_OPEN_READING_AREA |  |  | QNL/SF-1.jpg
VAV_2F_S12_007 | VAV | Included | OPEN READING AREA L1.001 | entity:QNL_L1_001_OPEN_READING_AREA |  |  | QNL/SF-1.jpg
VAV_2F_S12_008 | VAV | Included | OPEN READING AREA L1.001 | entity:QNL_L1_001_OPEN_READING_AREA |  |  | QNL/SF-1.jpg
VAV_2F_S12_009 | VAV | Included | OPEN READING AREA L1.001 | entity:QNL_L1_001_OPEN_READING_AREA |  |  | QNL/SF-1.jpg
VAV_2F_S12_010 | VAV | Included | BRAILLE READER L1.002 | entity:QNL_L1_002_BRAILLE_READER |  |  | QNL/SF-1.jpg
VAV_2F_S12_011 | VAV | Included | BRAILLE READER L1.002 | entity:QNL_L1_002_BRAILLE_READER |  |  | QNL/SF-1.jpg
VAV_2F_S12_012 | VAV | Included | TUTORING HEAD L1.003 | entity:QNL_L1_003_TUTORING_HEAD |  |  | QNL/SF-1.jpg
VAV_2F_S12_013 | VAV | Included | WRITING ROOM 1 L1.004 | entity:QNL_L1_004_WRITING_ROOM1 |  |  | QNL/SF-1.jpg
VAV_2F_S12_014 | VAV | Included | WRITING HEAD L1.005 | entity:QNL_L1_005_WRITING_ROOM2 |  |  | QNL/SF-1.jpg
VAV_2F_S12_015 | VAV | Included | WRITING ROOM 2 L1.005 | entity:QNL_L1_005_WRITING_ROOM2
VAV_2F_S12_016 | VAV | Included | STUDENT CARRELS L1.007 | entity:QNL_L1_007_STUDENT_CARRLES |  |  | QNL/SF-1.jpg
VAV_2F_S12_017 | VAV | Included | STUDENT CARRELS L1.007 | entity:QNL_L1_007_STUDENT_CARRLES
VAV_2F_S12_018 | VAV | Included | STUDENT CARRELS L1.007 | entity:QNL_L1_007_STUDENT_CARRLES
VAV_2F_S12_019 | VAV | Included | STUDENT CARRELS L1.007 | entity:QNL_L1_007_STUDENT_CARRLES
VAV_2F_S12_020 | VAV | Included | STUDENT CARRELS L1.007 | entity:QNL_L1_007_STUDENT_CARRLES
VAV_2F_S12_021 | VAV | Included | Breakout Space L2.010 | entity:QNL_L2_010_BREAKOUT_SPACE |  | Breakout space | QNL/SF-1.jpg
VAV_2F_S12_022 | VAV | Included | Circulation Office L2.011 | entity:QNL_L2_011_CTRCULATION_OFFICE |  | Circulation Office | QNL/SF-1.jpg
VAV_2F_S12_023 | VAV | Included | Office SpL Collection L2.012 | entity:QNL_L2_012_OFFICE_SPEC_COL
VAV_2F_S12_024 | VAV | Included | Office SpL Collection L2.013 | entity:QNL_L2_013_OFFICE_SPEC_COL
VAV_2F_S12_025 | VAV | Included | CORRIDOR L2 | entity:QNL_L2_993_CORRIDOR
VAV_2F_S12_026 | VAV | Included | Circulation Office L2.011 | entity:QNL_L2_011_CTRCULATION_OFFICE |  | Circulation Office | QNL/SF-1.jpg
VAV_2F_S12_027 | VAV | Included | Group Study Room 7 L2.017 | entity:QNL_L2_017_40_GROUP_STUDY_ROOM_7
VAV_2F_S12_028 | VAV | Included | Meeting Room L2.018 | entity:QNL_L2_018_GROUP_STUDY_ROOM_8
VAV_2F_S12_029 | VAV | Included | Group Study Room 7 L2.017 | entity:QNL_L2_017_40_GROUP_STUDY_ROOM_7 |  | Group Study Rm 7 | QNL/SF-1.jpg
VAV_2F_S12_097 | VAV | Included | Group Study Room 8 L2.018 | entity:QNL_L2_018_GROUP_STUDY_ROOM_8
VAV_2F_S13_001 | VAV | Not Included | Lib. Director's Room L2.044 | entity:QNL_L2_044_LIBDIRECTORS_ROOM |  | Lib. Director's Rm | QNL/SF-3.jpg
VAV_2F_S13_002 | VAV | Not Included | Lib. Director's Room L2.044 | entity:QNL_L2_044_LIBDIRECTORS_ROOM
VAV_2F_S13_003 | VAV | Included | Service & Lounge L2.043 | entity:QNL_L2_043_SERVICE_&_LOUNGE |  | Service & Lounge | QNL/SF-3.jpg
VAV_2F_S13_004 | VAV | Included | Transl.Spc& Space ED L2.014 | entity:QNL_L2_014_TRANS_SPC_AND_SPACE_ED |  |  | QNL/SF-1.jpg
VAV_2F_S13_005 | VAV | Included | LIBR COM REL SPC & EVENTS SPC L2.021 | entity:QNL_L2_021_LIBR_COM_REL_SPC_AND_EVENTS_SPC |  |  | QNL/SF-1.jpg
VAV_2F_S13_006 | VAV | Included | ACD PERS LIBRARIAN L2.022 | entity:QNL_L2_022_ACADEMIC_PERS_LIBRARIA |  |  | QNL/SF-1.jpg
VAV_2F_S13_007 | VAV | Included | AD ADMIN & PLANNING L2.023 | entity:QNL_L2_023_AD_ADMIN_&_PLANNING |  |  | QNL/SF-1.jpg
VAV_2F_S13_008 | VAV | Included | Office Coord L2.024 | entity:QNL_L2_024_OFFICE_COORD |  | Office Coord | QNL/SF-3.jpg
VAV_2F_S13_009 | VAV | Included | OPEN OFFICE L2.025 | entity:QNL_L2_025_OPEN_OFFICE
VAV_2F_S13_010 | VAV | Included | CORRIDOR L2 | entity:QNL_L2_993_CORRIDOR
VAV_2F_S13_011 | VAV | Included | CORRIDOR L2 | entity:QNL_L2_993_CORRIDOR
VAV_2F_S13_012 | VAV | Included | CORRIDOR L2 | entity:QNL_L2_993_CORRIDOR |  |  | QNL/SF-1.jpg
VAV_2F_S13_013 | VAV | Included | CORRIDOR L2 | entity:QNL_L2_993_CORRIDOR |  |  | QNL/SF-1.jpg
VAV_2F_S13_014 | VAV | Included | CORRIDOR L2 | entity:QNL_L2_993_CORRIDOR
VAV_2F_S13_015 | VAV | Included | CORRIDOR L2 | entity:QNL_L2_993_CORRIDOR
VAV_2F_S13_016 | VAV | Not Included | VIP Waiting ROOM L2.048 | entity:QNL_L2_048_VIP_WATING
VAV_2F_S14_001 | VAV | Included | PUBLIC SERVICES L1.080 | entity:QNL_L1_080_PUBLIC_SERVICE
VAV_2F_S14_002 | VAV | Included | PUBLIC SERVICES L1.080 | entity:QNL_L1_080_PUBLIC_SERVICE
VAV_2F_S14_003 | VAV | Included | PUBLIC SERVICES L1.080 | entity:QNL_L1_080_PUBLIC_SERVICE
VAV_2F_S14_004 | VAV | Included | PUBLIC SERVICES L1.080 | entity:QNL_L1_080_PUBLIC_SERVICE
VAV_2F_S14_005 | VAV | Included | BIBLIOGRAPHER 1 L1.081 | entity:QNL_L1_081_BIBLIOGRANHER1 |  |  | QNL/SF-3.jpg
VAV_2F_S14_006 | VAV | Included | BIBLIOGRAPHER 2 L1.082 | entity:QNL_L1_082_BIBLIOGRAPHER2 |  |  | QNL/SF-3.jpg
VAV_2F_S14_007 | VAV | Included | SPEC COLL & ARCH L1.083 | entity:QNL_L1_083_SPEC_COLL&ARCH |  |  | QNL/SF-3.jpg
VAV_2F_S14_008 | VAV | Included | R&L SERVICES L1.084 | entity:QNL_L1_084_R&L_SERVICES |  |  | QNL/SF-3.jpg
VAV_2F_S14_009 | VAV | Included | AD. PUBLIC SERVICE L1.085 | entity:QNL_L1_085_ADPUBLIC_SERVICE |  |  | QNL/SF-3.jpg
VAV_2F_S14_010 | VAV | Included | REF LIBRARIAN L1.086 | entity:QNL_L1_086_REF_LIBRARIAN_1 |  |  | QNL/SF-3.jpg
VAV_2F_S14_011 | VAV | Included | REF LIBRARIAN L1.087 | entity:QNL_L1_087_REF_LIBRARIAN_2 |  |  | QNL/SF-3.jpg
VAV_2F_S14_012 | VAV | Included | REF LIBRARIAN L1.088 | entity:QNL_L1_088_REF_LIBRARIAN_3 |  |  | QNL/SF-3.jpg
VAV_2F_S14_013 | VAV | Included | REF LIBRARIAN L1.089 | entity:QNL_L1_089_REF_LIBRARIAN_4 |  |  | QNL/SF-3.jpg
VAV_2F_S14_014 | VAV | Included | REF LIBRARIAN L1.090 | entity:QNL_L1_090_REF_LIBRARIAN_5 |  |  | QNL/SF-3.jpg
VAV_2F_S14_015 | VAV | Included | REF LIBRARIAN L1.091 | entity:QNL_L1_091_REF_LIBRARIAN_6 |  |  | QNL/SF-3.jpg
VAV_2F_S14_016 | VAV | Included | REF LIBRARIAN L1.092 | entity:QNL_L1_092_REF_LIBRARIAN_7
VAV_2F_S14_017 | VAV | Included | REF LIBRARIAN L1.093 | entity:QNL_L1_093_REF_LIBRARIAN_8 |  |  | QNL/SF-3.jpg
VAV_2F_S14_018 | VAV | Included | REF LIBRARIAN L1.094 | entity:QNL_L1_094_REF_LIBRARIAN_9 |  |  | QNL/SF-3.jpg
VAV_2F_S14_019 | VAV | Included | REF LIBRARIAN L1.095 | entity:QNL_L1_095_REF_LIBRARIAN_10 |  |  | QNL/SF-3.jpg
VAV_2F_S14_020 | VAV | Included | REF LIBRARIAN L1.096 | entity:QNL_L1_096_REF_LIBRARIAN_11 |  |  | QNL/SF-3.jpg
VAV_2F_S14_021 | VAV | Included | REF LIBRARIAN L1.097 | entity:QNL_L1_097_REF_LIBRARIAN_12 |  |  | QNL/SF-3.jpg
VAV_2F_S15_001 | VAV | Not Included | VIP Room L2.051 | entity:QNL_L2_051_VIP_ROOM
VAV_2F_S15_002 | VAV | Not Included | VIP Room L2.051 | entity:QNL_L2_051_VIP_ROOM |  | VIP Rm | QNL/SF-3.jpg
VAV_2F_S15_003 | VAV | Not Included | VIP Room L2.051 | entity:QNL_L2_051_VIP_ROOM
VAV_2F_S15_004 | VAV | Not Included | VIP Room L2.051 | entity:QNL_L2_051_VIP_ROOM
VAV_2F_S15_005 | VAV | Not Included | MAJLIS-VIP Meeting L2.046 | entity:QNL_L2_046_VIP_MEETING |  |  | QNL/SF-3.jpg
VAV_B_S10_001 | VAV | Included | DIGITISATION AREA B.200 | entity:QNL_B_200_DIGITIZATION
VAV_B_S10_002 | VAV | Included | DIGITISATION AREA B.200 | entity:QNL_B_200_DIGITIZATION
VAV_B_S10_003 | VAV | Included | DIGITISATION AREA B.200 | entity:QNL_B_200_DIGITIZATION
VAV_B_S10_004 | VAV | Included | DIGITISATION AREA B.200 | entity:QNL_B_200_DIGITIZATION
VAV_B_S10_005 | VAV | Included | DIGITISATION AREA B.200 | entity:QNL_B_200_DIGITIZATION
VAV_B_S10_006 | VAV | Included | DIGITISATION AREA B.200 | entity:QNL_B_200_DIGITIZATION
VAV_B_S10_007 | VAV | Included | DIGITISATION AREA B.200 | entity:QNL_B_200_DIGITIZATION
VAV_B_S10_008 | VAV | Included | DIGITISATION AREA B.200 | entity:QNL_B_200_DIGITIZATION
VAV_B_S10_009 | VAV | Included | TECHNICAL SERVICES B.203 | entity:QNL_B_204_TECHNICAL_SERVICES
VAV_B_S10_010 | VAV | Included | TECHNICAL SERVICES B.204 | entity:QNL_B_204_TECHNICAL_SERVICES |  | Technical Services | QNL/BF-5.jpg
VAV_B_S10_011 | VAV | Included | TECHNICAL SERVICES B.204 | entity:QNL_B_204_TECHNICAL_SERVICES |  | Technical Services | QNL/BF-5.jpg
VAV_B_S10_012 | VAV | Included | CR6 CONVERSATION WORK AREA B.209 | entity:QNL_B_209_CONSERVATION_WORK_AREA
VAV_B_S10_013 | VAV | Included | CR6 CONVERSATION WORK AREA B.209 | entity:QNL_B_209_CONSERVATION_WORK_AREA
VAV_B_S10_014 | VAV | Included | CR6 CONVERSATION WORK AREA B.209 | entity:QNL_B_209_CONSERVATION_WORK_AREA
VAV_B_S10_015 | VAV | Included | INSTRUCTION OUTREACH B.206 | entity:QNL_B_206_INSTRUCTION_OUTREACH
VAV_B_S10_016 | VAV | Included | MULTIMEDIA PRESENTATION B.205 | entity:QNL_B_205_INSTRUCTION_PRESENTATION |  | Instruction Presentation | QNL/BF-5.jpg
VAV_B_S10_017 | VAV | Included | MULTIMEDIA PRESENTATION B.205 | entity:QNL_B_205_INSTRUCTION_PRESENTATION |  | Instruction Presentation | QNL/BF-5.jpg
VAV_B_S10_018 | VAV | Included | MULTIMEDIA PRESENTATION B.205 | entity:QNL_B_205_INSTRUCTION_PRESENTATION
VAV_B_S10_019 | VAV | Included | CR6 PROF LIBRARIAN B.208 | entity:QNL_B_208_PROF_LIBRARIAN
VAV_B_S10_020 | VAV | Included | Reserchers Reading Area B.207 | entity:QNL_B_207_PRESEARCHERS_READING_AREA |  | Researchers Reading Area | QNL/BF-7.jpg
VAV_B_S10_021 | VAV | Included | Reserchers Reading Area B.207 | entity:QNL_B_207_PRESEARCHERS_READING_AREA |  | Researchers Reading Area | QNL/BF-7.jpg
VAV_B_S10_022 | VAV | Included | Reserchers Reading Area B.207 | entity:QNL_B_207_PRESEARCHERS_READING_AREA |  | Researchers Reading Area | QNL/BF-7.jpg
VAV_B_S10_023 | VAV | Included | Reserchers Reading Area B.207 | entity:QNL_B_207_PRESEARCHERS_READING_AREA |  | Researchers Reading Area | QNL/BF-7.jpg
VAV_B_S10_024 | VAV | Included | DIGITISATION AREA B.200 | entity:QNL_B_200_DIGITIZATION |  | Digitization | QNL/BF-5.jpg
VAV_B_S11_001 | VAV | Included | Break Out Area B.001A | entity:QNL_B_001A_BREAK_OUT_AREA |  | Break Out Area | QNL/BF.jpg
VAV_B_S11_002 | VAV | Included | Break Out Area B.001A | entity:QNL_B_001A_BREAK_OUT_AREA |  | Break Out Area | QNL/BF.jpg
VAV_B_S11_003 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF.jpg
VAV_B_S11_004 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF.jpg
VAV_B_S11_005 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF.jpg
VAV_B_S11_006 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF.jpg
VAV_B_S11_007 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF.jpg
VAV_B_S11_008 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF-1.jpg
VAV_B_S11_009 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF-1.jpg
VAV_B_S11_010 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Break Out Area | QNL/BF-1.jpg
VAV_B_S11_011 | VAV | Included | Break Out Area B.001A | entity:QNL_B_001A_BREAK_OUT_AREA |  | Break Out Area | QNL/BF.jpg
VAV_B_S11_012 | VAV | Included | Break Out Area B.001A | entity:QNL_B_001A_BREAK_OUT_AREA |  | Break Out Area | QNL/BF.jpg
VAV_B_S11_013 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF.jpg
VAV_B_S11_014 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF.jpg
VAV_B_S11_015 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF.jpg
VAV_B_S11_016 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF.jpg
VAV_B_S11_017 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF.jpg
VAV_B_S11_018 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF-1.jpg
VAV_B_S11_019 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF-1.jpg
VAV_B_S11_020 | VAV | Included | Tech, Services & Collections Office B.001 | entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE |  | Tech.Services & Collections Office | QNL/BF-1.jpg
VAV_B_S11_021 | VAV | Included | Reception & Lounge B.009 | entity:QNL_B_009_RECEPTION_&_LOUNGE |  | Tech.Services & Collections Office | QNL/BF.jpg
VAV_B_S11_022 | VAV | Included | Corridor Leading To Reception & Lounge B.009 | entity:QNL_B_009_RECEPTION_&_LOUNGE |  | Corridor east of Receving Area | QNL/BF.jpg
VAV_B_S11_023 | VAV | Included | Corridor Leading To Reception & Lounge B.009 | entity:QNL_B_009_RECEPTION_&_LOUNGE |  | Corridor east of Receving Area | QNL/BF-2.jpg
VAV_B_S11_024 | VAV | Included | Kitchen B.002 | entity:QNL_B_002_KITCHEN |  | Kitchen | QNL/BF.jpg
VAV_B_S11_025 | VAV | Included | Storage B.028 | entity:QNL_B_028_STORAGE |  | Storage | QNL/BF.jpg
VAV_B_S11_026 | VAV | Not Included | Finance Cooridinator & Business Support officer B.003 | entity:QNL_B_003_FINANCE_COORDINATOR_&_BUSINESS_SUPPORT_OFCR |  | Finance Cooridinator & Business Support officer | QNL/BF.jpg
VAV_B_S11_027 | VAV | Not Included | AD TECH SERVICES DIRECTOR B.003 | entity:QNL_B_003_FINANCE_COORDINATOR_&_BUSINESS_SUPPORT_OFCR
VAV_B_S11_028 | VAV | Included | Analogue Resources B.004 | entity:QNL_B_004_ANALOG_RESOURCES |  | Analog Resource | QNL/BF.jpg
VAV_B_S11_029 | VAV | Included | Digital Resources B.005 | entity:QNL_B_005_DIGITAL_RESOURCES
VAV_B_S11_030 | VAV | Included | Budget & Payment 1 B.006 | entity:QNL_B_006_BUDGET_&_PAYMENT_1 |  | Budget & Payment | QNL/BF.jpg
VAV_B_S11_031 | VAV | Included | Budget & Payment 2 B.007 | entity:QNL_B_007_BUDGET_&_PAYMENT_2 |  | Budget & Payment | QNL/BF.jpg
VAV_B_S11_032 | VAV | Included | Ad Collection B.024 | entity:QNL_B_024_AD_COLLECTIONS |  | Ad Collection | QNL/BF.jpg
VAV_B_S11_033 | VAV | Included | Ad Collection B.024 | entity:QNL_B_024_AD_COLLECTIONS |  | Ad Collection | QNL/BF.jpg
VAV_B_S11_034 | VAV | Included | Engineering B.020 | entity:QNL_B_020_ENGINEERING
VAV_B_S11_035 | VAV | Included | Arabic Sudies B.021 | entity:QNL_B_021_ARABIC_STUDIES
VAV_B_S11_036 | VAV | Included | Licensing Expert B.022 | entity:QNL_B_022_LICENSING_EXPERT
VAV_B_S11_037 | VAV | Included | Art & Humanities B.023 | entity:QNL_B_023_ARTS_&_HUMANITIES |  |  | QNL/BF-1.jpg
VAV_B_S11_038 | VAV | Included | Procurement SPC B.027 | entity:QNL_B_027_PROCUREMENT_SPC_PROCUREMENT_OFCR |  | Procurement SPC | QNL/BF.jpg
VAV_B_S11_039 | VAV | Included | Business Computing B.026 | entity:QNL_B_026_BUSINESS_&_COMPUTING
VAV_B_S11_040 | VAV | Included | Social Sciences B.025 | entity:QNL_B_025_SOCIAL_SCIENCES
VAV_B_S11_041 | VAV | Included | Literature Language B.029 | entity:QNL_B_029_LITERATURE_&_ANGUAGE
VAV_B_S11_042 | VAV | Included | GENERAL B.030 | entity:QNL_B_030_SNR_P_COORDINATOR_&_P_COORDINATOR
VAV_B_S11_043 | VAV | Included | Receiving Area B.008 | entity:QNL_B_008_RECEIVING_AREA |  |  | QNL/BF.jpg
VAV_B_S11_044 | VAV | Included | Receiving Area B.008 | entity:QNL_B_008_RECEIVING_AREA |  |  | QNL/BF.jpg
VAV_B_S11_045 | VAV | Included | Receiving Area B.008 | entity:QNL_B_008_RECEIVING_AREA |  | Receving Area | QNL/BF.jpg
VAV_B_S11_046 | VAV | Included | Receiving Area B.008 | entity:QNL_B_008_RECEIVING_AREA |  |  | QNL/BF.jpg
VAV_B_S13_001 | VAV | Included | Meeting Room B.034 | entity:QNL_B_034_MEETING_ROOM |  | Meeting Rm | QNL/BF-1.jpg
VAV_B_S13_002 | VAV | Included | Meeting Room B.034 | entity:QNL_B_034_MEETING_ROOM |  | Meeting Rm | QNL/BF-1.jpg
VAV_B_S13_003 | VAV | Included | Processing Room B.103 | entity:QNL_B_103_PROCESSING_ROOM |  | Processing Rm | QNL/BF-5.jpg
VAV_B_S13_004 | VAV | Included | Processing Room B.103 | entity:QNL_B_103_PROCESSING_ROOM |  | Processing Rm | QNL/BF-5.jpg
VAV_B_S13_005 | VAV
VAV_B_S13_006 | VAV | Included | Fumigation Room B.085 | entity:QNL_B_085_FUMIGATION_ROOM
VAV_B_S13_007 | VAV | Included | Shipping CLIRK B.101 | entity:QNL_B_101_SHIPPING_CLERK |  | Shipping Clerk | QNL/BF-5.jpg
VAV_B_S13_008 | VAV | Not Included | SECURITY CONTROL ROOM B.105 | entity:QNL_B_105_SECURITY_CONTOL_ROOM |  | Security Store | QNL/BF-5.jpg
VAV_B_S14_001 | VAV | Included | Office B.040 | entity:QNL_B_040_OFFICE |  | Office | QNL/BF-4.jpg
VAV_B_S14_002 | VAV | Included | Office Dig Init B.056 | entity:QNL_B_056_OFFICE_DIG_INIT
VAV_B_S14_003 | VAV | Included | Office AD For LIT B.057 | entity:QNL_B_057_OFFICE_AD_FOR_LIT |  |  | QNL/BF-4.jpg
VAV_B_S14_004 | VAV | Included | Digitization Room B.041 | entity:QNL_B_041_DIGITIZATION_ROOM
VAV_B_S14_005 | VAV | Included | Digitization Room B.041 | entity:QNL_B_041_DIGITIZATION_ROOM
VAV_B_S14_006 | VAV | Included | Digitization Room B.041 | entity:QNL_B_041_DIGITIZATION_ROOM
VAV_B_S14_007 | VAV | Included | Shell Space B.58 | entity:QNL_B_058_SHELL_SPACE
VAV_B_S14_008 | VAV | Included | Digitization Room B.041 | entity:QNL_B_041_DIGITIZATION_ROOM |  | Digitization Rm | QNL/BF-4.jpg
VAV_B_S14_009 | VAV | Included | Office AD For LIT B.057 | entity:QNL_B_057_OFFICE_AD_FOR_LIT |  |  | QNL/BF-4.jpg
VAV_B_S14_010 | VAV | Included | Digitization Room B.041 | entity:QNL_B_041_DIGITIZATION_ROOM
VAV_B_S14_011 | VAV | Included | Digitization Room B.041 | entity:QNL_B_041_DIGITIZATION_ROOM
VAV_B_S14_012 | VAV | Included | Digitization Room B.041 | entity:QNL_B_041_DIGITIZATION_ROOM
VAV_B_S14_013 | VAV | Included | Shell Space B.58 | entity:QNL_B_058_SHELL_SPACE
VAV_B_S14_014 | VAV | Included | Shell Space B.59 | entity:QNL_B_59_SHELL_SPACE
VAV_B_S14_015 | VAV | Included | Digitization Room B.041 | entity:QNL_B_041_DIGITIZATION_ROOM
VAV_B_S14_016 | VAV | Included | Digitization Room B.041 | entity:QNL_B_041_DIGITIZATION_ROOM
VAV_B_S14_040 | VAV | Included | BOH Kitchen B.044 | entity:QNL_B_044_BOH_KITCHEN
VAV_B_S14_041 | VAV | Included | Fine Binding B.044 | entity:QNL_B_044_BOH_KITCHEN
VAV_B_S14_042 | VAV | Included | Binding & Preservation B.043 | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE
VAV_B_S14_043 | VAV | Included | Binding & Preservation B.043 | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE
VAV_B_S14_044 | VAV | Included | Binding & Preservation B.043 | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE
VAV_B_S14_045 | VAV | Included | Binding & Preservation B.043 | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE
VAV_B_S14_046 | VAV | Included | Binding & Preservation B.043 | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE
VAV_B_S14_047 | VAV | Included | Fine Binding B.044 | entity:QNL_B_044_BOH_KITCHEN
VAV_B_S14_048 | VAV | Included | Binding & Preservation B.043 | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE
VAV_B_S14_049 | VAV | Included | Binding & Preservation B.043 | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE
VAV_B_S14_050 | VAV | Included | Binding & Preservation B.043 | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE
VAV_B_S14_051 | VAV | Included | Binding & Preservation B.043 | entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE
VAV_B_S15_001 | VAV | Included | Prof. Librarian B.153 | entity:QNL_B_153_PROF_LIBRARIAN
VAV_B_S15_002 | VAV | Not Included | Lobby and Security B.145 | entity:QNL_B_145_LOBY_&_CSECURITY
VAV_B_S15_003 | VAV | Not Included | Lobby and Security B.145 | entity:QNL_B_145_LOBY_&_CSECURITY
VAV_B_S15_004 | VAV | Not Included | Lobby and Security B.145 | entity:QNL_B_145_LOBY_&_CSECURITY
VAV_B_S15_005 | VAV | Included | Prof. Librarian B.153 | entity:QNL_B_153_PROF_LIBRARIAN
VAV_B_S15_006 | VAV | Included | Prof. Librarian B.153 | entity:QNL_B_153_PROF_LIBRARIAN
VAV_B_S15_007 | VAV | Not Included | HC SECURITY ROOM B.152 | entity:QNL_B_152_SECURITY_ROOM
VAV_B_S15_008 | VAV | Included | RESEARCH & DOC RECORD MGMT B.151 | entity:QNL_B_151_RESEARCH_&_DOC-RCRDS_MGMT
VAV_B_S15_009 | VAV | Not Included | HC DIRECTOR HEAD B.149 | entity:QNL_B_149_DIRECTOR_HEAD
VAV_B_S15_010 | VAV | Not Included | HC DIRECTOR HEAD B.149 | entity:QNL_B_149_DIRECTOR_HEAD |  |  | QNL/BF-8.jpg
VAV_B_S15_011 | VAV | Not Included | VIP Majlis B.149 | entity:QNL_B_149_DIRECTOR_HEAD |  |  | QNL/BF-8.jpg
VAV_B_S15_012 | VAV | Not Included | VIP Majlis B.149 | entity:QNL_B_149_DIRECTOR_HEAD
VAV_B_S15_013 | VAV | Included | RESEARCH & DOC RECORD MGMT B.151 | entity:QNL_B_151_RESEARCH_&_DOC-RCRDS_MGMT
CAV_1F_S11_001 | CAV | Included | CORRIDOR L1.023 | entity:QNL_L1_023_CORRIDOR
CAV_1F_S11_002 | CAV | Included | CORRIDOR L1.023 | entity:QNL_L1_023_CORRIDOR |  |  | QNL/FF.jpg
CAV_1F_S11_006 | CAV | Included | CHILDRENS LIBRRY CIRCULATION NW GLAZED L1.047 | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING
CAV_1F_S11_007 | CAV | Included | CORRIDOR L1.023 | entity:QNL_L1_023_CORRIDOR
CAV_1F_S11_008 | CAV | Included | CHILDRENS LIBRRY CIRCULATION NW GLAZED L1.047 | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING
CAV_1F_S11_009 | CAV | Included | CHILDRENS LIBRRY CIRCULATION NW GLAZED L1.047 | entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING
CAV_1F_S15_002 | CAV | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT |  | Restaurant | QNL/FF-2.jpg
CAV_1F_S15_004 | CAV | Included | AERIAL PLATFORM PARKING L1.100 | entity:QNL_L1_100_AERIAL_PLATFORM_PARKING
CAV_1F_S15_005 | CAV | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT |  | Restaurant | QNL/FF-2.jpg
CAV_1F_S15_006 | CAV | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT
CAV_1F_S15_010 | CAV | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT
CAV_1F_S15_011 | CAV | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT |  | Restaurant | QNL/FF-2.jpg
CAV_1F_S15_012 | CAV | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT |  | Restaurant | QNL/FF-2.jpg
CAV_1F_S15_013 | CAV | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT |  | Restaurant | QNL/FF-2.jpg
CAV_1F_S15_014 | CAV | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT
CAV_1F_S15_015 | CAV | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT |  | Restaurant | QNL/FF-2.jpg
CAV_1F_S15_016 | CAV | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT |  | Restaurant | QNL/FF-2.jpg
CAV_1F_S15_017 | CAV | Included | Restaurant L1.150 | entity:QNL_L1_150_RESTAURANT |  | Restaurant | QNL/FF-2.jpg
CAV_1F_S15_018 | CAV | Included | AREAL PLATFORM PARK L1.100 | entity:QNL_L1_100_AERIAL_PLATFORM_PARKING
CAV_1F_S15_019 | CAV | Included | FURNITURE STORE L1.153 | entity:QNL_L1_153_FURNITURE_STORAGE |  |  | QNL/FF-3.jpg
CAV_B_S12_001 | CAV | Included | Plant Room 1 B.063 | entity:QNL_B_063_PLANT_ROOM_01 |  | Plant Rm 1 | QNL/BF-2.jpg
CAV_B_S12_002 | CAV | Not Included | Plant Room 1 B.063 | entity:QNL_B_063_PLANT_ROOM_01 |  | Plant Rm 1 | QNL/BF-2.jpg
CAV_B_S12_003 | CAV | Not Included | Plant Room 1 B.063 | entity:QNL_B_063_PLANT_ROOM_01 |  | Plant Rm 1 | QNL/BF-2.jpg
CAV_B_S13_001 | CAV | Included | Corridor 2 B.064 | entity:QNL_B_064_CORRIDOR_2 |  | Corridor 2 | QNL/BF-2.jpg
CAV_B_S13_002 | CAV | Included | Corridor 2 B.064 | entity:QNL_B_064_CORRIDOR_2 |  | Corridor 2 | QNL/BF-2.jpg
CAV_B_S13_003 | CAV | Included | Corridor 2 B.064 | entity:QNL_B_064_CORRIDOR_2
CAV_B_S13_004 | CAV | Included | Corridor 2 B.064 | entity:QNL_B_064_CORRIDOR_2 |  | Corridor 2 | QNL/BF-5.jpg
CAV_B_S13_005 | CAV | Included | Corridor 2 B.064 | entity:QNL_B_064_CORRIDOR_2 |  | Corridor 2 | QNL/BF-5.jpg
CAV_B_S13_006 | CAV | Included | CORRIDOR 4 B.035 | entity:QNL_B_035_CORRIDOR_4 |  |  | QNL/BF-2.jpg
CAV_B_S13_007 | CAV | Included | CORRIDOR 4 B.035 | entity:QNL_B_035_CORRIDOR_4 |  | Corridor 4 | QNL/BF-1.jpg
CAV_B_S13_008 | CAV | Included | CORRIDOR 4 B.035 | entity:QNL_B_035_CORRIDOR_4 |  |  | QNL/BF-3.jpg
CAV_B_S13_009 | CAV | Included | IT STORAGE B.104 | entity:QNL_B_104_STORAGE |  | Storage | QNL/BF-5.jpg
CAV_B_S13_010 | CAV | Not Included | Plant Room 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02 |  | Plant Rm 2 | QNL/BF-2.jpg
CAV_B_S13_011 | CAV | Not Included | Plant Room 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02 |  | Plant Rm 2 | QNL/BF-2.jpg
CAV_B_S13_012 | CAV | Not Included | Plant Room 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02 |  | Plant Rm 2 | QNL/BF-2.jpg
CAV_B_S13_013 | CAV | Not Included | GAS SUPPRESSION B.087 | entity:QNL_B_087_GAS_SUPPRESSION_ROOM |  | Gas Suppression | QNL/BF-3.jpg
CAV_B_S13_014 | CAV | Included | Corridor 2 B.064 | entity:QNL_B_064_CORRIDOR_2 |  |  | QNL/BF-3.jpg
CAV_B_S13_015 | CAV | Not Included | Server Room B.089 | entity:QNL_B_089_SERVER_ROOM |  | Server Rm | QNL/BF-3.jpg
CAV_B_S13_020 | CAV | Not Included | UPS BATTERY ROOM B.084 | entity:QNL_B_084_UPS_BATTERY_ROOM
CAV_B_S13_021 | CAV | Not Included | Sprinklers Pumps & Zones Valves B.072 | entity:QNL_B_072_SPRIMKLERS_PUMPS_&_ZONES_VALVES |  | Sprinkler Pump | QNL/BF-3.jpg
CAV_B_S13_050 | CAV | Not Included | PLANT ROOM B.104A | entity:QNL_B_104A_PLANT_ROOM
CAV_B_S14_001 | CAV | Included | OFFICE B.040 | entity:QNL_B_040_OFFICE |  |  | QNL/BF-4.jpg
CAV_B_S14_002 | CAV | Included | CORRIDOR 3 B.052 | entity:QNL_B_052_CORRIDOR_3
CAV_B_S14_003 | CAV | Not Included | PLANT ROOM 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03
CAV_B_S14_004 | CAV | Not Included | PLANT ROOM 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03 |  | Plant Rm 3 | QNL/BF-6.jpg
CAV_B_S14_005 | CAV | Not Included | PLANT ROOM 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03
CAV_B_S14_006 | CAV | Included | Referigerate Store Kitchen Lobby B.044 | entity:QNL_B_044_BOH_KITCHEN |  |  | QNL/BF-4.jpg
CAV_B_S14_007 | CAV | Included | Washing Area & Fine Binding B.044 | entity:QNL_B_044_BOH_KITCHEN
CAV_B_S15_001 | CAV | Included | Corridor 5 B.063 | entity:QNL_B_063_PLANT_ROOM_01
CAV_B_S15_002 | CAV | Included | Corridor 5 B.063 | entity:QNL_B_063_PLANT_ROOM_01
CAV_B_S15_003 | CAV | Included | Corridor 5 B.063 | entity:QNL_B_063_PLANT_ROOM_01
DX_B01 | DX Unit |  | MV ROOM B.081 | entity:QNL_B_081_MV_ROOM |  | Corridor 4 | QNL/BF-1.jpg
DX_B02 | DX Unit |  | MV ROOM B.081 | entity:QNL_B_081_MV_ROOM |  | Corridor 4 | QNL/BF-1.jpg
DX_B03 | DX Unit |  | TRANSFORMER ROOM B.082 | entity:QNL_B_082_TRANSFORMER_ROOM |  | Emergency Lighting Battery Rm | QNL/BF-1.jpg
DX_B04 | DX Unit |  | TRANSFORMER ROOM B.082 | entity:QNL_B_082_TRANSFORMER_ROOM
DX_B05 | DX Unit |  | HV ROOM B.083 | entity:QNL_B_083_HV_ROOM
DX_B06 | DX Unit |  | HV ROOM B.083 | entity:QNL_B_083_HV_ROOM |  | Loading Area (pink, south-west) | QNL/BF-4.jpg
DX_B07 | DX Unit |  | EMERGENCY LIGHTING BATTERY ROOM B.095 | entity:QNL_B_095_EMERGENCY_LIGHTING_BATTERY_ROOM |  | Emergency Lighting Battery Rm
DX_B08 | DX Unit |  | UPS BATTERY ROOM B.084 | entity:QNL_B_084_UPS_BATTERY_ROOM |  | Emergency Lighting Battery Rm
DX_B09 | DX Unit |  | UPS BATTERY ROOM B.084 | entity:QNL_B_084_UPS_BATTERY_ROOM
DX_B10 | DX Unit |  | SECURITY & BMS B.102 | entity:QNL_B_102_SECURITY_&_BMS |  | Processing Rm | QNL/BF-5.jpg
DX_B11 | DX Unit |  | ITTIGATION CONTROL ROOM B.046_ITT | entity:QNL_B046_ITT_ITTIGATION_CONTROL_ROOM |  | Security Equip. B.107 | QNL/BF-5.jpg
DX_B12 | DX Unit |  | SECURITY EQUIPMENT ROOM B.107 | entity:QNL_B_107_SECURITY_EQUIPMENT_ROOM
DX_B13 | DX Unit |  | TRASH CHAMBER B.093 | entity:QNL_B_093_TRANSH_CHAMBER
DX_B14 | DX Unit |  | TRANSFORMER ROOM B.082 | entity:QNL_B_082_TRANSFORMER_ROOM |  | Emergency Lighting Battery Rm | QNL/BF-1.jpg
DX_B15 | DX Unit |  | TRASH CHAMBER B.093 | entity:QNL_B_093_TRANSH_CHAMBER
DX_B16 | DX Unit |  | EMERGENCY LIGHTING BATTERY ROOM B.095 | entity:QNL_B_095_EMERGENCY_LIGHTING_BATTERY_ROOM
DX_B17 | DX Unit |  | REFRIGERATE STORE B.045A | entity:QNL_B_045A_REFRIGERATE_STORE
DX_B18 | DX Unit |  | REFRIGERATE STORE B.045A | entity:QNL_B_045A_REFRIGERATE_STORE
DX_B19 | DX Unit |  | REFRIGERATE STORE B.045A | entity:QNL_B_045A_REFRIGERATE_STORE
DX_B20 | DX Unit |  | STORAGE B.092 | entity:QNL_B_092_STORAGE
DX_B21 | DX Unit |  | IDF Roof RP.001 | entity:QNL_P_004_PLANT_ZONE
DX_B22 | DX Unit |  | REST ROOM SECURITY B.106_RES | entity:QNL_B106_RES_REST_ROOM_SECURITY
DX_B23 | DX Unit |  | SECURITY EQUIPMENT ROOM B.107 | entity:QNL_B_107_SECURITY_EQUIPMENT_ROOM
DX_B24 | DX Unit |  | IDF Roof RP.001 | entity:QNL_P_004_PLANT_ZONE
HEX01 | HEX |  | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
HEX02 | HEX |  | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
HEX03 | HEX |  | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
HEX04 | HEX |  | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
HEX05 | HEX |  | PH PLANT B.211 | entity:QNL_B_211_PH_PLANT_ROOM
EF_201 | EF |  | L-3 L1.L-3 | entity:QNL_L1-L-3_L-3
EF_B05 | EF |  | FUMIGATION B.085 | entity:QNL_B_085_FUMIGATION_ROOM
EF_B06 | EF |  | DIGITIZATION CENTER B.055 | entity:QNL_B_055_DIGITIZATION_CENTER
EF_B07 | EF |  | Loading Room B.109 | entity:QNL_B_109_LOADING_AREA |  | Loading Area (north-west grey band) | QNL/BF-4.jpg
EF_B08 | EF |  | Loading Room B.109 | entity:QNL_B_109_LOADING_AREA
EF_B09 | EF |  | Generator B.080 | entity:QNL_B_080_GENERATOR
EF_B10 | EF |  | Trash room B.093 | entity:QNL_B_093_TRANSH_CHAMBER
EF_B11 | EF |  | Fuel pump room B.091 | entity:QNL_B_091_FUEL_ROOM
EF_B12 | EF |  | IDF ROOM B.214 | entity:QNL_B_214_IDF_ROOM
EF_B13 | EF |  | Sprinklers Pumps B.072 | entity:QNL_B_072_SPRIMKLERS_PUMPS_&_ZONES_VALVES |  | Plant Rm 2 | QNL/BF-2.jpg
EF_B14 | EF |  | Fire Command B.071 | entity:QNL_B_071_FIRE_COMMAND_ROOM |  | Corridor 2 | QNL/BF-2.jpg
EF_B15 | EF |  | Loading Room B.109 | entity:QNL_B_109_LOADING_AREA
EF_B16 | EF |  | Loading Room B.109 | entity:QNL_B_109_LOADING_AREA
EF_BBV01 | EF |  | Plant Room 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02
EF_BBV02 | EF |  | Plant Room 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02 |  | Plant Rm 2 | QNL/BF-2.jpg
EF_RP01 | EF |  | Plant Zone P.002 | entity:QNL_P_002_PLANT_ZONE
EF_RP02 | EF |  | Plant Zone P.004 | entity:QNL_P_004_PLANT_ZONE
EF_RP03 | EF |  | Plant Zone P.007 | entity:QNL_P_007_PLANT_ZONE |  | Plant Zone | QNL/RF-3.jpg
KEF_101 | KEF |  | RESTAURANT L1.067 | entity:QNL_L1_067_RESTAURANT
KEF_B019 | KEF |  | MEP KITCHEN B.049 | entity:QNL_B_049_MEP_KITCHEN
KEF_B020 | KEF |  | CORRIDOR 3 B.052 | entity:QNL_B_052_CORRIDOR_3
KEF_B04 | KEF |  | BREAKOUT AREA B.001A | entity:QNL_B_001A_BREAK_OUT_AREA
SEF_RP04 | SEF |  | Plant Zone P.002 | entity:QNL_P_002_PLANT_ZONE
SEF_RP05 | SEF |  | Plant Zone P.002 | entity:QNL_P_002_PLANT_ZONE
SEF_RP06 | SEF |  | Plant Zone P.002 | entity:QNL_P_002_PLANT_ZONE
SEF_RP07 | SEF |  | Plant Zone P.004 | entity:QNL_P_004_PLANT_ZONE
SEF_RP08 | SEF |  | Plant Zone P.004 | entity:QNL_P_004_PLANT_ZONE
SEF_RP09 | SEF |  | Plant Zone P.004 | entity:QNL_P_004_PLANT_ZONE
SEF_RP10 | SEF |  | Plant Zone P.007 | entity:QNL_P_007_PLANT_ZONE |  | Plant Zone | QNL/RF-3.jpg
SEF_RP11 | SEF |  | Plant Zone P.006 | entity:QNL_P_006_PLANT_ZONE |  | Plant Zone | QNL/RF-3.jpg
SEF_RP12 | SEF |  | Plant Zone P.006 | entity:QNL_P_006_PLANT_ZONE |  | Plant Zone | QNL/RF-3.jpg
SEF_ZoneA | SEF |  | Plant Zone P.002 | entity:QNL_P_002_PLANT_ZONE
SEF_ZoneB | SEF |  | Plant Zone P.004 | entity:QNL_P_004_PLANT_ZONE
SEF_ZoneC | SEF |  | Plant Zone P.007 | entity:QNL_P_007_PLANT_ZONE
TEF_101C | TEF |  | ELEC SHAFT L1.E2 | entity:QNL_L1-E2_ELEC_SHAFT
TEF_102C | TEF |  | ELEC SHAFT L1.E1 | entity:QNL_L1-E1_ELEC_SHAFT
TEF_B01A | TEF |  | PLANT ROOM 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03
TEF_B01B | TEF |  | PLANT ROOM 3 B.110 | entity:QNL_B_110_PLANT_ROOM_03
TEF_B02A | TEF |  | PLANT ROOM 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02
TEF_B02B | TEF |  | PLANT ROOM 2 B.070 | entity:QNL_B_070_PLANT_ROOM_02
TEF_B03A | TEF |  | COMPACT SHELVING-MAIN COLLECTION B.120 | entity:QNL_B_120_COMPACT_SHELVING_-MAIN_COLLECTION
TEF_B03B | TEF |  | COMPACT SHELVING-MAIN COLLECTION B.120 | entity:QNL_B_120_COMPACT_SHELVING_-MAIN_COLLECTION
CCU_B01 | CCU |  | QTEL ROOM B.048 | entity:QNL_B_048_QTEL_ROOM
CCU_B02 | CCU |  | QTEL ROOM B.048 | entity:QNL_B_048_QTEL_ROOM
CCU_B03 | CCU |  | TELECOM ROOM B.050 | entity:QNL_B_050_TELECOM_ROOM
CCU_B04 | CCU |  | TELECOM ROOM B.050 | entity:QNL_B_050_TELECOM_ROOM
CCU_B05 | CCU |  | SERVER ROOM B.089 | entity:QNL_B_089_SERVER_ROOM
CCU_B06 | CCU |  | SERVER ROOM B.089 | entity:QNL_B_089_SERVER_ROOM
CCU_B07 | CCU |  | SERVER ROOM B.089 | entity:QNL_B_089_SERVER_ROOM
CCU_B08 | CCU |  | VAULT_B.141_VAU | entity:QNL_B141_VAU_VAULT
CCU_B09 | CCU |  | VAULT_B.141_VAU | entity:QNL_B141_VAU_VAULT
CCU_B10 | CCU |  | IDF B.222 | entity:QNL_B_222_IDF
CCU_B11 | CCU |  | IDF B.222 | entity:QNL_B_222_IDF
CCU_8081 | CCU
CCU_8082 | CCU
CCU_8083 | CCU
CCU_8084 | CCU
CCU_8085 | CCU
CCU_8086 | CCU
CCU_MDFRm | CCU
CCU_Qtel | CCU
CCU_Server_Rm | CCU
CCU_AVServer_Rm | CCU
CCU_HeritageVault | CCU
CHW_P01 | CHW Pump |  | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
CHW_P02 | CHW Pump |  | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
CHW_P03 | CHW Pump |  | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
CHW_P04 | CHW Pump |  | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
CHWPU_P01 | CHW Pump |  | Plant Room 4 B.220 | entity:QNL_B_220_PLANT_ROOM_04
CHWPU_P02 | CHW Pump
ELEC_Gen | Generator |  | Generator B.080 | entity:QNL_B_080_GENERATOR
ahu-8601
ahu-8601
ahu-8601
ahu-8601
ahu-8601
ahu-8601
ahu-8601
ahu-8601
ahu-8601
ahu-8601
ahu-8601
ahu-8601
ahu-8601
ahu-8601
Note on D75: Ahmad Sharaf Al Masri: HMI reads 56.3 C on IMG_9601.jpeg - by far the highest reading seen across all QNL drawings, against 19.6 C on FCU-1F-058 directly beneath it. Almost certainly a failed sensor; worth raising with the BMS team.
Note on D118: Ahmad Sharaf Al Masri: IMG_9592.jpeg (Basement Zone-3-P2): FCU-B-001 is drawn outside the plan outline on the left with no leader line to any room. Nearest labels are 'IDF Rooom' and 'VIP Restroom', both of which would make this Not Included (technical / executive). Key Plan name used per the agreed rule - please confirm.
Note on D155: Ahmad Sharaf Al Masri: FCU-B-038 shows '??????' instead of a temperature on the HMI (no sensor reading). Room name taken from its yellow leader line pointing into the Pantry.
Note on D185: Ahmad Sharaf Al Masri: HMI reads 34.1 C on IMG_9599.jpeg - well above the ~17-20 C of the adjacent media studios. Consistent with an unconditioned store, but worth checking.
Note on D331: Ahmad Sharaf Al Masri: CONFLICT: previously recorded as 'Plant Room 1 / Plant Room 2 (IMG_9588.jpeg)', Not Included. Honeywell BMS VAV Summary Type-01 (IMG_9563.jpeg) groups VAV/B/S11/022 (Master) and /023 (Slave) together under 'Basement Zone 1 Corridor Leading To Reception & Lounge B009'. Updated to match the BMS and changed to Included. Verify against the basement drawing before final sign-off.
Note on D367: Ahmad Sharaf Al Masri: HMI label on IMG_9589.jpeg reads 'VAV-B-S11-005'. Positionally it sits between VAV-B-S14-004 and VAV-B-S14-006 in the Digitization Room, and VAV_B_S11_005 (row 1075) is already assigned to Tech, Services & Collections Office from IMG_9587.jpeg. Recorded here as S14_005 - please confirm the correct HMI tag.
Note on D399: Ahmad Sharaf Al Masri: Flagged for the executive-room rule, not for the room name. 'Asst. Head' is a management office - confirm whether it counts as an executive room (Not Included) or a senior staff office (currently Included).
Note on D400: Ahmad Sharaf Al Masri: Flagged for the executive-room rule, not for the room name. 'Asst. Head' is a management office - confirm whether it counts as an executive room (Not Included) or a senior staff office (currently Included).
Note on D459: Ahmad Sharaf Al Masri: No B083 in the room-name list supplied (list jumps B082 TRANSFORMER ROOM to B084 UPS BATTERY ROOM). Name needed.
Note on D460: Ahmad Sharaf Al Masri: No B083 in the room-name list supplied (list jumps B082 TRANSFORMER ROOM to B084 UPS BATTERY ROOM). Name needed.
Note on D471: Ahmad Sharaf Al Masri: No B045 / B045A in the room-name list supplied. Name needed.
Note on D472: Ahmad Sharaf Al Masri: No B045 / B045A in the room-name list supplied. Name needed.
Note on D473: Ahmad Sharaf Al Masri: No B045 / B045A in the room-name list supplied. Name needed.
Note on D475: Ahmad Sharaf Al Masri: DX/RP/21 is a Roof unit (Zone C) — no room number on HMI.
Note on D476: Ahmad Sharaf Al Masri: Ambiguous: list has two B106 entries - 'REST ROOM SECURITY B106_RES' and 'SECURITY STORES SECURITY UPS B106_SEC'. Confirm which applies to DX_B22.
Note on D478: Ahmad Sharaf Al Masri: DX/RP/21 is a Roof unit (Zone C) — no room number on HMI.
Note on D533: Ahmad Sharaf Al Masri: Ambiguous: list has two B141 entries - 'HL PLANT ROOM B141_HLP' and 'VAULT B141_VAU'. Confirm which applies to CCU_B08.
Note on D534: Ahmad Sharaf Al Masri: Ambiguous: list has two B141 entries - 'HL PLANT ROOM B141_HLP' and 'VAULT B141_VAU'. Confirm which applies to CCU_B09.

## SSC Room Names with Equip.
Name | Number | entity to use in Ontology | Equipment located in Entity
VENT PLANT | B1.014 | entity:SSC_B1_014_VENT_PLANT | #REF! | #REF!
CHILLED WATER | B1.013 | entity:SSC_B1_013_CHILLED_WATER | #REF! | #REF!
GENERATOR | B1.012 | entity:SSC_B1_012_GENERATOR | #REF!
STAIR-1 | B1.ST-1 | entity:SSC_B1_ST-1_STAIR-1 | #REF!
ENTRANCE | B1.015 | entity:SSC_B1_015_ENTRANCE | #REF!
LIFT | B1.P-1 | entity:SSC_B1_P-1_P1 | #REF!
LIFT | B1.P-2 | entity:SSC_B1_P-2_P2 | #REF!
SPRINKLER & WATER | B1.016 | entity:SSC_B1_016_SPRINKLER_&_WATER | #REF!
SER-2 | B1.038 | entity:SSC_B1_038_SER-2 | #REF!
MDF-2 | B1.017 | entity:SSC_B1_017_MDF-2 | #REF!
FM STORAGE | B1.019 | entity:SSC_B1_019_FM_STORAGE | #REF!
CONDENSER ROOM | B1.018 | entity:SSC_B1_018_CONDENSER_ROOM | #REF!
FILE STORAGE | B1.028 | entity:SSC_B1_028_FILE_STORAGE | #REF!
CORRIDOR | B1.030 | entity:SSC_B1_030_CORRIDOR | #REF!
CORRIDOR | B1.031 | entity:SSC_B1_031_CORRIDOR | #REF!
CORRIDOR | B1.029 | entity:SSC_B1_029_CORRIDOR | #REF!
CORRIDOR | B1.027 | entity:SSC_B1_027_CORRIDOR | #REF!
CORRIDOR | B1.034 | entity:SSC_B1_034_CORRIDOR | #REF!
CORRIDOR | B1.035 | entity:SSC_B1_035_CORRIDOR | #REF!
VENT PLANT | B1.008 | entity:SSC_B1_008_VENT_PLANT | #REF!
STAIR-2 | B1.ST-2 | entity:SSC_B1_ST-2_STAIR-2 | #REF!
STORAGE | B1.036 | entity:SSC_B1_036_STORAGE | #REF!
JANITORS CLOSET | B1.011 | entity:SSC_B1_011_JANITORS_CLOSET | #REF!
VESTIBULE | B1.010 | entity:SSC_B1_010_VESTIBULE | #REF!
TOILET | B1.009 | entity:SSC_B1_009_TOILET | #REF!
SERVICE DOCK | B1.007 | entity:SSC_B1_007_SERVICE_DOCK | #REF!
UPS | B1.005 | entity:SSC_B1_005_UPS | #REF!
SERVICE AREA | B1.006 | entity:SSC_B1_006_SERVICE_AREA | #REF!
MAIN SEC. CONTROL ROOM | B1.025 | entity:SSC_B1_025_MAIN_SEC_CONTROL_ROOM | #REF!
SSP | B1.022 | entity:SSC_B1_022_SSP | #REF!
QTEL | B1.023 | entity:SSC_B1_023_Q_TEL | #REF!
MDF/SER-1 | B1.026 | entity:SSC_B1_026_MDF_SER-1 | #REF!
BIN STORAGE | B1.024 | entity:SSC_B1_024_BIN_STORAGE | #REF!
BMS | B1.039 | entity:SSC_B1_039_BMS | #REF!
FM STORAGE | B1.021 | entity:SSC_B1_021_FM_STORAGE | #REF!
CORRIDOR | B1.032 | entity:SSC_B1_032_CORRIDOR | #REF!
FM STORAGE | B1.020 | entity:SSC_B1_020_FM_STORAGE | #REF!
FM STORAGE | B1.001 | entity:SSC_B1_001_FM_STORAGE | #REF!
HV | B1.002 | entity:SSC_B1_002_HV_ROOM | #REF!
TRANSFORMER | B1.003 | entity:SSC_B1_003_TRANSFORMER | #REF!
MV SWITCH ROOM | B1.004 | entity:SSC_B1_004_MV_SWITCH_ROOM | #REF!
STAIR-9 | 01.ST-9 | entity:SSC_01_ST-9_STAIR-9 | #REF!
OUTDOOR AREA | 1.037 | entity:SSC_01_037_OUTDOOR_AREA | #REF!
SHELL SPACE | 1.014 | entity:SSC_01_014_SHELL_SPACE | #REF! | #REF! | #REF!
STAIR-3 | 01.ST-3 | entity:SSC_01_ST-3_STAIR-3 | #REF!
SHELL SPACE | 1.015 | entity:SSC_01_015_SHELL_SPACE | #REF! | #REF! | #REF!
STAIR-8 | 01.ST-8 | entity:SSC_01_ST-8_STAIR-8 | #REF!
SHELL SPACE | 1.016 | entity:SSC_01_016_SHELL_SPACE | #REF!
STORAGE | 1.041 | entity:SSC_01_041_STORAGE_ROOM | #REF!
FEMALE TOILET | 1.017 | entity:SSC_01_017_FEMALE_TOILET | #REF!
CORRIDOR | 1.018 | entity:SSC_01_018_CORRIDOR | #REF!
SHELL SPACE | 1.002 | entity:SSC_01_002_SHELL_SPACE | #REF! | #REF! | #REF! | #REF!
ABLUTION ROOM | 1.022 | entity:SSC_01_022_ABLUTION_ROOM | #REF!
ABLUTION ROOM | 1.021 | entity:SSC_01_021_ABLUTION_ROOM | #REF!
CORRIDOR | 1.023 | entity:SSC_01_023_CORRIDOR | #REF!
CORRIDOR | 1.02 | entity:SSC_01_020_CORRIDOR | #REF!
CORRIDOR | 1.024 | entity:SSC_01_024_CORRIDOR | #REF!
IDF - 2 | 1.039 | entity:SSC_01_039_IDF_2 | #REF! | #REF!
IDF - 1 | 1.027 | entity:SSC_01_027_IDF_1 | #REF! | #REF!
FURNITURE STORAGE | 1.026 | entity:SSC_01_026_STORAGE_ROOM | #REF!
MALE TOILET | 1.025 | entity:SSC_01_025_MALE_TOILET | #REF!
PRAYER ROOM | 1.019 | entity:SSC_01_019_PRAYER_ROOM | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
CORRIDOR | 1.001 | entity:SSC_01_001_CORRIDOR | #REF! | #REF! | #REF!
OPEN SPACE | 1.003 | entity:SSC_01_003_OPEN_SPACE | #REF! | #REF! | #REF! | #REF!
SHELL SPACE | 1.029 | entity:SSC_01_029_ROOM_NO_42 | #REF! | #REF! | #REF!
STORAGE | 1.012 | entity:SSC_01_012_STORAGE | #REF!
LIFT | 01.P-2 | entity:SSC_01_P-2_P-2 | #REF!
LIFT | 01.P-1 | entity:SSC_01_P-1_P-1 | #REF!
CORRIDOR | 1.013 | entity:SSC_01_013_CORRIDOR | #REF!
STAIR-1 | 01.ST-1 | entity:SSC_01_ST-1_STAIR-1 | #REF!
AUDITORIUM MEETING ROOM | 1.009 | entity:SSC_01_009_AUDITORIUM | #REF!
STORAGE AREA | 1.038 | entity:SSC_01_038_STORAGE_AREA | #REF!
A / V ROOM | 1.008 | entity:SSC_01_008_AV_ROOM | #REF! | #REF!
FEMALE TOILET | 1.007 | entity:SSC_01_007_FEMALE_TOILET | #REF!
MALE TOILET | 1.006 | entity:SSC_01_006_MALE_TOILET | #REF!
KITCHEN | 1.005 | entity:SSC_01_005_KITCHEN | #REF!
CORRIDOR | 1.004 | entity:SSC_01_004_CORRIDOR | #REF!
STAIR-4 | 01.ST-4 | entity:SSC_01_ST-4_STAIR_4 | #REF!
AIR LOCK | 1.011 | entity:SSC_01_011_AIR_LOCK | #REF!
CORRIDOR | 1.01 | entity:SSC_01_010_CORRIDOR | #REF! | #REF!
STAIR-5 | 01.ST-5 | entity:SSC_01_ST-5_STAIR-5 | #REF!
STORAGE | 1.03 | entity:SSC_01_030_STORAGE | #REF!
TOILET | 1.031 | entity:SSC_01_031_TOILET | #REF!
VESTIBULE | 1.032 | entity:SSC_01_032_VESTIBULE | #REF!
JANITORS CLOSET | 1.033 | entity:SSC_01_033_JANITORS_CLOSET | #REF!
CORRIDOR | 1.035 | entity:SSC_01_035_CORRIDOR | #REF!
AIR LOCK | 1.034 | entity:SSC_01_034_AIR_LOCK | #REF!
STAIR-10 | ST-10 | entity:SSC_ST-10_STAIR-10 | #REF!
OUTDOOR AREA | 1.036 | entity:SSC_01_036_OUTDOOR_AREA | #REF!
STAIR-2 | 01.ST-2 | entity:SSC_01_ST-2_STAIR-2 | #REF!
CORRIDOR | 1.028 | entity:SSC_01_028_CORRIDOR | #REF! | #REF!
RESEARCHER'S OFFICE | 3.015 | entity:SSC_03_015_RESEARCHERS_OFFICE | #REF!
VISITOR'S CUBICLE | 3.014 | entity:SSC_03_014_VISITORS_CUBICLE | #REF!
RESEARCHER'S OFFICE | 3.013 | entity:SSC_03_013_RESEARCHERS_OFFICE | #REF!
RESEARCHER'S OFFICE | 3.012 | entity:SSC_03_012_RESEARCHERS_OFFICE | #REF!
VISITOR'S CUBICLE | 3.011 | entity:SSC_03_011_VISITORS_CUBICLE | #REF!
RESEARCHER'S OFFICE | 3.01 | entity:SSC_03_010_RESEARCHERS_OFFICE | #REF!
RESEARCHER'S OFFICE | 3.009 | entity:SSC_03_009_RESEARCHERS_OFFICE | #REF!
VISITOR'S CUBICLE | 3.008 | entity:SSC_03_008_VISITORS_CUBICLE | #REF!
OPERATIONS MANAGER | 3.007 | entity:SSC_03_007_OPERATIONS_MANAGER | #REF!
MEETING ROOM | 3.006 | entity:SSC_03_006_MEETING_ROOM | #REF! | #REF!
RESEARCHER'S OFFICE | 3.005 | entity:SSC_03_005_RESEARCHERS_OFFICE | #REF!
VISITOR'S CUBICLE | 3.004 | entity:SSC_03_004_VISITORS_CUBICLE | #REF!
RESEARCHER'S OFFICE | 3.003 | entity:SSC_03_003_RESEARCHERS_OFFICE | #REF!
DIRECTOR'S MEETING ROOM | 3.002 | entity:SSC_03_002_DIRECTORS_MEETING_ROOM | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DIRECTOR'S OFFICE | 3.001 | entity:SSC_03_001_DIRECTORS_OFFICE | #REF!
RESEARCHER'S OFFICE | 3.017 | entity:SSC_03_017_RESEARCHERS_OFFICE | #REF!
VISITOR'S CUBICLE | 3.018 | entity:SSC_03_018_VISITORS_CUBICLE | #REF!
IT MANAGER'S OFFICE | 3.019 | entity:SSC_03_019_IT_MANAGERS_OFFICE | #REF!
RESEARCHER'S OFFICE | 3.02 | entity:SSC_03_020_RESEARCHERS_OFFICE | #REF!
VISITOR'S CUBICLE | 3.021 | entity:SSC_03_021_VISITORS_CUBICLE | #REF!
RESEARCHER'S OFFICE | 3.022 | entity:SSC_03_022_RESEARCHERS_OFFICE | #REF!
RESEARCHER'S OFFICE | 3.023 | entity:SSC_03_023_RESEARCHERS_OFFICE | #REF!
VISITOR'S CUBICLE | 3.024 | entity:SSC_03_024_VISITORS_CUBICLE | #REF!
SECRETARIAL AREA | 3.025 | entity:SSC_03_025_SECRETARIAL_AREA | #REF!
MEETING ROOM | 3.026 | entity:SSC_03_026_MEETING_ROOM | #REF! | #REF! | #REF!
RESEARCHER'S OFFICE | 3.027 | entity:SSC_03_027_RESEARCHERS_OFFICE | #REF!
VISITOR'S CUBICLE | 3.028 | entity:SSC_03_028_VISITORS_CUBICLE | #REF!
RESEARCHER'S OFFICE | 3.029 | entity:SSC_03_029_RESEARCHERS_OFFICE | #REF!
ASSOC. DIRECTOR'S MEETING ROOM | 3.03 | entity:SSC_03_030_ASSOC_DIRECTORS_MEETING_ROOM | #REF!
ASSOC. DIRECTOR'S OFFICE | 3.031 | entity:SSC_03_031_ASSOC_DIRECTORS_OFFICE | #REF!
GENERAL OFFICE AREA | 3.032 | entity:SSC_03_032_GENERAL_OFFICE_AREA | #REF!
PRINTING | 3.033 | entity:SSC_03_033_PRINTING | #REF!
STAIR-2 | 03.ST-2 | entity:SSC_03_ST-2_STAIR-2 | #REF!
STORAGE | 3.046 | entity:SSC_03_046_STORAGE | #REF!
JANITOR'S CLOSET | 3.045 | entity:SSC_03_045_JANITORS_CLOSET | #REF!
BALCONY | 3.047 | entity:SSC_03_047_BALCONY | #REF!
LOUNGE | 3.016 | entity:SSC_03_016_LOUNGE | #REF! | #REF!
IT SERVER ROOM | 3.038 | entity:SSC_03_038_SERVER_ROOM | #REF!
IT OFFICE | 3.049 | entity:SSC_03_049_IT_OFFICE | #REF!
FEMALE TOILET | 3.039 | entity:SSC_03_039_FEMALE_TOILET | #REF!
MALE TOILET | 3.037 | entity:SSC_03_037_MALE_TOILET | #REF!
KITCHEN | 3.036 | entity:SSC_03_036_KITCHEN | #REF!
STAIR-1 | 03.ST-1 | entity:SSC_03_ST-1_STAIR-1 | #REF!
LIFT | 03.P-2 | entity:SSC_03_P-2_LIFT | #REF!
LIFT | 03.P-1 | entity:SSC_03_P-1_LIFT | #REF!
CORRIDOR | 3.04 | entity:SSC_03_040_CORRIDOR | #REF!
CORRIDOR | 3.041 | entity:SSC_03_041_CORRIDOR | #REF!
CORRIDOR | 3.034 | entity:SSC_03_034_CORRIDOR | #REF! | #REF! | #REF! | #REF!
CORRIDOR | 3.042 | entity:SSC_03_042_CORRIDOR | #REF! | #REF!
STUDY LIBRARY AREA | 3.035 | entity:SSC_03_035_STUDY_LIBRARY_AREA | #REF!
CORRIDOR | 3.044 | entity:SSC_03_044_CORRIDOR | #REF!
EXTERIOR COURTYARD | 3.043 | entity:SSC_03_043_EXTERIOR_COURTYARD | #REF!
BALCONY | 3.048 | entity:SSC_03_048_BALCONY | #REF!
PODIUM | 03.F7.1 | entity:SSC_03_F7_1_PODIUM | #REF!
EXECUTIVE CONFERENCE ROOM | 2.005 | entity:SSC_02_005_EXECUTIVE_CONFERENCE_ROOM | #REF! | #REF! | #REF!
CONFERENCE ROOM | 2.006 | entity:SSC_02_006_CONFERENCE_ROOM | #REF! | #REF!
LIFT | 02.P-1 | entity:SSC_02_P-1_LIFT | #REF!
LIFT | 02.P-2 | entity:SSC_02_P-2_LIFT | #REF!
MEZZANINE | 2.007 | entity:SSC_02_007_MEZZANINE | #REF!
TOILET | 2.008 | entity:SSC_02_008_TOILET | #REF!
VESTIBULE | 2.01 | entity:SSC_02_010_VESTIBULE | #REF!
STAIR-2 | 02.ST-2 | entity:SSC_02_ST-2_STAIR-2 | #REF!
LOBBY | 2.002 | entity:SSC_02_002_LOBBY | #REF! | #REF! | #REF! | #REF!
FOYER | 2.001 | entity:SSC_02_001_FOYER | #REF! | #REF!
CORRIDOR | 2.004 | entity:SSC_02_004_CORRIDOR | #REF!
CORRIDOR | 2.003 | entity:SSC_02_003_CORRIDOR | #REF!
STAIR-1 | 02.ST-1 | entity:SSC_02_ST-1_STAIR-1 | #REF!
STAIR-8 | 02.ST-8 | entity:SSC_02_ST-8_STAIR-8 | #REF!

## HQ Room Names with Equip.
Room Entity Name | Room Number Used | Room Space (cleaned) |  | Equipment Match Audit
entity:HQ_B1.606_SECURE_STORAGE | B1.606 | SECURE_STORAGE | #REF! | Rooms listed (col A) | 1040
entity:HQ_B1.001_AHU_4 | B1.001 | AHU_4 | #REF! | Equipment names returned | 1040
entity:HQ_B1.002_SECURITY_UPS_ROOM | B1.002 | SECURITY_UPS_ROOM | #REF! | Rooms with no equipment | 0
entity:HQ_B1.003_CONTROL_ROOM | B1.003 | CONTROL_ROOM | #REF! | Equipment in source register | 1
entity:HQ_B1.005_MDF_1_ROOM | B1.005 | MDF_1_ROOM | #REF! | Distinct equipment returned | #VALUE!
entity:HQ_B1.006_AHU_1 | B1.006 | AHU_1 | #REF! | Duplicate room entries (col A) | 0
entity:HQ_B1.007_COOLING_EQUIPMENT | B1.007 | COOLING_EQUIPMENT | #REF! | Duplicated equipment returns (D:L) | #REF!
entity:HQ_B1.008_FM_STORAGE | B1.008 | FM_STORAGE | #REF! | Unplaced (in register, not on a room) | #VALUE!
entity:HQ_B1.009_MV_SWITCH_ROOM | B1.009 | MV_SWITCH_ROOM | #REF!
entity:HQ_B1.010_TRANSFORMER_SUBSTATION | B1.010 | TRANSFORMER_SUBSTATION | #REF!
entity:HQ_B1.011_HV_INTAKE | B1.011 | HV_INTAKE | #REF!
entity:HQ_B1.012_GENERATOR | B1.012 | GENERATOR | #REF!
entity:HQ_B1.013_Q-TEL_INCOMING | B1.013 | Q-TEL_INCOMING | #REF!
entity:HQ_B1.014_SUPPORT_SPACE_DRY_WASTE_STORAGE | B1.014 | SUPPORT_SPACE_DRY_WASTE_STORAGE | #REF!
entity:HQ_B1.015_SUPPORT_SPACE_LOADING | B1.015 | SUPPORT_SPACE_LOADING | #REF!
entity:HQ_B1.016_AHU_2 | B1.016 | AHU_2 | #REF!
entity:HQ_B1.017_WATER_SERVICES | B1.017 | WATER_SERVICES | #REF!
entity:HQ_B1.018_PA_ROOM | B1.018 | PA_ROOM | #REF!
entity:HQ_B1.019_AHU | B1.019 | AHU | #REF!
entity:HQ_B1.020_CHILLED_WATER | B1.020 | CHILLED_WATER | #REF!
entity:HQ_B1.021_FILING_STORAGE | B1.021 | FILING_STORAGE | #REF!
entity:HQ_B1.022_AHU_3 | B1.022 | AHU_3 | #REF!
entity:HQ_B1.023_CBS_ROOM | B1.023 | CBS_ROOM | #REF!
entity:HQ_B1.024_SUPPORT_SPACE_WASTE_BIN_WASH_UP_AREA | B1.024 | SUPPORT_SPACE_WASTE_BIN_WASH_UP_AREA | #REF!
entity:HQ_B1.025_COOLING_EQUIPMENT_ROOM | B1.025 | COOLING_EQUIPMENT_ROOM | #REF!
entity:HQ_B1.026_UPS_ROOM | B1.026 | UPS_ROOM | #REF!
entity:HQ_B1.101_AUDITORIUM_BACKSTAGE | B1.101 | AUDITORIUM_BACKSTAGE | #REF!
entity:HQ_B1.102_SERVER_ROOM | B1.102 | SERVER_ROOM | #REF!
entity:HQ_B1.103_STAFF_LOBBY | B1.103 | STAFF_LOBBY | #REF!
entity:HQ_B1.106_VVIP_PARKING_6_CAR_SPOTS | B1.106 | VVIP_PARKING_6_CAR_SPOTS | #REF!
entity:HQ_B1.107_DOCK_MASTER_OFFICE | B1.107 | DOCK_MASTER_OFFICE | #REF!
entity:HQ_B1.108_SUPPORT_SPACE_WET_WASTE_STORAGE | B1.108 | SUPPORT_SPACE_WET_WASTE_STORAGE | #REF!
entity:HQ_B1.110_SUPPORT_SPACE_MAIL_ROOM | B1.110 | SUPPORT_SPACE_MAIL_ROOM | #REF!
entity:HQ_B1.111_CHANGING_ROOM | B1.111 | CHANGING_ROOM | #REF!
entity:HQ_B1.112_CHANGING_ROOM | B1.112 | CHANGING_ROOM | #REF!
entity:HQ_B1.113_SHEIKHA_LOBBY_SECURITY_ROOM | B1.113 | SHEIKHA_LOBBY_SECURITY_ROOM | #REF!
entity:HQ_B1.114_FILING_STORAGE | B1.114 | FILING_STORAGE | #REF!
entity:HQ_B1.115_VVIP_PARKING_4_CAR_SPOTS | B1.115 | VVIP_PARKING_4_CAR_SPOTS | #REF!
entity:HQ_B1.116_SHEIKHA_LOBBY | B1.116 | SHEIKHA_LOBBY | #REF!
entity:HQ_B1.117_CHAUFFEUR_ROOM | B1.117 | CHAUFFEUR_ROOM | #REF!
entity:HQ_B1.118_SHEIKHA_LOBBY_PANTRYRG_LOUNGE | B1.118 | SHEIKHA_LOBBY_PANTRYRG_LOUNGE | #REF!
entity:HQ_B1.119_ELECTRICAL_CABINET | B1.119 | ELECTRICAL_CABINET | #REF!
entity:HQ_B1.120_MDF_2_ROOM | B1.120 | MDF_2_ROOM | #REF!
entity:HQ_B1.121_MAINTENANCE_ROOM | B1.121 | MAINTENANCE_ROOM | #REF!
entity:HQ_B1.122_SUPPORT_SPACE_FOOD_STORAGE | B1.122 | SUPPORT_SPACE_FOOD_STORAGE | #REF!
entity:HQ_B1.123_SUPPORT_SPACE_FOOD_STORAGE | B1.123 | SUPPORT_SPACE_FOOD_STORAGE | #REF!
entity:HQ_B1.401_MALE_TOILET | B1.401 | MALE_TOILET | #REF!
entity:HQ_B1.402_FEMALE_TOILET | B1.402 | FEMALE_TOILET | #REF!
entity:HQ_B1.403_TOILET | B1.403 | TOILET | #REF!
entity:HQ_B1.511_VESTIBULE | B1.511 | VESTIBULE | #REF!
entity:HQ_B1.512_IDF_ROOM | B1.512 | IDF_ROOM | #REF!
entity:HQ_B1.541_VESTIBULE | B1.541 | VESTIBULE | #REF!
entity:HQ_B1.542_VESTIBULE | B1.542 | VESTIBULE | #REF!
entity:HQ_B1.543_VESTIBULE | B1.543 | VESTIBULE | #REF!
entity:HQ_B1.544_SUPPORT_SPACE_STORAGE | B1.544 | SUPPORT_SPACE_STORAGE | #REF!
entity:HQ_B1.602_CORRIDOR | B1.602 | CORRIDOR | #REF!
entity:HQ_B1.603_CORRIDOR | B1.603 | CORRIDOR | #REF!
entity:HQ_B1.604_CORRIDOR | B1.604 | CORRIDOR | #REF!
entity:HQ_B1.605_CORRIDOR | B1.605 | CORRIDOR | #REF!
entity:HQ_B1.P 1_P_1 | B1.P 1 | P_1 | #REF!
entity:HQ_B1.P 2_P_2 | B1.P 2 | P_2 | #REF!
entity:HQ_B1.P 3_P_3 | B1.P 3 | P_3 | #REF!
entity:HQ_B1.P-4_P-4 | B1.P-4 | P-4 | #REF!
entity:HQ_B1.P-5_P-5 | B1.P-5 | P-5 | #REF!
entity:HQ_B1.P-6_P-6 | B1.P-6 | P-6 | #REF!
entity:HQ_B1.S 1_S_1 | B1.S 1 | S_1 | #REF!
entity:HQ_B1.ST-1_ST-1 | B1.ST-1 | ST-1 | #REF!
entity:HQ_B1.ST-2_ST-2 | B1.ST-2 | ST-2 | #REF!
entity:HQ_B1.ST-4_ST-4 | B1.ST-4 | ST-4 | #REF!
entity:HQ_B1.ST-L6_ST-L6 | B1.ST-L6 | ST-L6 | #REF!
entity:HQ_G.002_PR_&_MARKET_MANAGER | G.002 | PR_&_MARKET_MANAGER | #REF!
entity:HQ_G.003_PR_&_MARKET_MANAGER | G.003 | PR_&_MARKET_MANAGER | #REF!
entity:HQ_G.004_PR_&_MARKET_MANAGER | G.004 | PR_&_MARKET_MANAGER | #REF!
entity:HQ_G.005_EMERGENCY_CONTROL_CENTER | G.005 | EMERGENCY_CONTROL_CENTER | #REF!
entity:HQ_G.006_AUDITORIUM_STAIRS_LOBBY | G.006 | AUDITORIUM_STAIRS_LOBBY | #REF!
entity:HQ_G.007_VIP_DROP_OFF_ENTRANCE | G.007 | VIP_DROP_OFF_ENTRANCE | #REF!
entity:HQ_G.008_CONTROL_ROOM | G.008 | CONTROL_ROOM | #REF!
entity:HQ_G.009_PR_&_MARKET_MANAGER | G.009 | PR_&_MARKET_MANAGER | #REF!
entity:HQ_G.010_PR_&_MARKET_STAFF | G.010 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.011_PR_&_MARKET_MANAGER | G.011 | PR_&_MARKET_MANAGER | #REF!
entity:HQ_G.012_PR_&_MARKET_STAFF | G.012 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.013_PR_&_MARKET_STAFF | G.013 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.014_VISITOR_CENT_OFFICE | G.014 | VISITOR_CENT_OFFICE | #REF!
entity:HQ_G.015_PR_&_MARKET_STAFF | G.015 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.016_PANTRY | G.016 | PANTRY | #REF!
entity:HQ_G.017_COPY_PRINT | G.017 | COPY_PRINT | #REF!
entity:HQ_G.018_PR_&_MARKET_STAFF | G.018 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.019_PR_&_MARKET_STAFF | G.019 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.020_PR_&_MARKET_STAFF | G.020 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.021_PR_&_MARKET_STAFF | G.021 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.022_PR_&_MARKET!_SECRETARY | G.022 | PR_&_MARKET!_SECRETARY | #REF!
entity:HQ_G.023_PR_&_MARKET_STAFF | G.023 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.024_PEDESTRIAN_ENTRANCE | G.024 | PEDESTRIAN_ENTRANCE | #REF!
entity:HQ_G.025_VIP_LOUNGE | G.025 | VIP_LOUNGE | #REF!
entity:HQ_G.026_FINANCE_CASHIER | G.026 | FINANCE_CASHIER | #REF!
entity:HQ_G.027_PANTRY | G.027 | PANTRY | #REF!
entity:HQ_G.028_PR_&_MARKET_DIRECTOR_ENSUIT | G.028 | PR_&_MARKET_DIRECTOR_ENSUIT | #REF!
entity:HQ_G.029_PR_&_MARKET_STAFF | G.029 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.03_PR_&_MARKET_STAFF | G.03 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.031_PR_&_MARKET_STAFF | G.031 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.032_PR_&_MARKET_STAFF | G.032 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.033_PR_&_MARKET_STAFF | G.033 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.034_PR_&_MARKET_STAFF | G.034 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.035_PR_&_MARKET_STAFF | G.035 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.036_PR_&_MARKET_STAFF | G.036 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.037_PR_&_MARKET_STAFF | G.037 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.038_PR_&_MARKET_STAFF | G.038 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.039_PR_&_MARKET_STAFF | G.039 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.101_CONFERENCE_ROOM | G.101 | CONFERENCE_ROOM | #REF!
entity:HQ_G.102_AUDITORIUM | G.102 | AUDITORIUM | #REF!
entity:HQ_G.103_BMS | G.103 | BMS | #REF!
entity:HQ_G.104_LOBBY | G.104 | LOBBY | #REF!
entity:HQ_G.105_SHOP | G.105 | SHOP | #REF!
entity:HQ_G.106_STORAGE_ROOM | G.106 | STORAGE_ROOM | #REF!
entity:HQ_G.107_E-TOWER_LOBBY | G.107 | E-TOWER_LOBBY | #REF!
entity:HQ_G.108_CONSULTANT_SPACE_TRAINEES | G.108 | CONSULTANT_SPACE_TRAINEES | #REF!
entity:HQ_G.11_STORAGE_ROOM | G.11 | STORAGE_ROOM | #REF!
entity:HQ_G.401_FEMALE_TOILET | G.401 | FEMALE_TOILET | #REF!
entity:HQ_G.402_MALE_TOILET | G.402 | MALE_TOILET | #REF!
entity:HQ_G.403_FEM_FEMALE_TOILET | G.403_FEM | FEMALE_TOILET | #REF!
entity:HQ_G.403_MAL_MALE_TOILET | G.403_MAL | MALE_TOILET | #REF!
entity:HQ_G.405_TOILET | G.405 | TOILET | #REF!
entity:HQ_G.511_VESTIBULE | G.511 | VESTIBULE | #REF!
entity:HQ_G.512_IDF_ROOM | G.512 | IDF_ROOM | #REF!
entity:HQ_G.521_STAIR_VESTIBULE | G.521 | STAIR_VESTIBULE | #REF!
entity:HQ_G.531_IDF_ROOM | G.531 | IDF_ROOM | #REF!
entity:HQ_G.532_ELECTRICAL_CLOSET_1 | G.532 | ELECTRICAL_CLOSET_1 | #REF!
entity:HQ_G.533_ELECTRICAL_CLOSET_2 | G.533 | ELECTRICAL_CLOSET_2 | #REF!
entity:HQ_G.541_STAIR_VESTIBULES | G.541 | STAIR_VESTIBULES | #REF!
entity:HQ_G.542_STAIR_VESTIBULE | G.542 | STAIR_VESTIBULE | #REF!
entity:HQ_G.544_VESTIBULE | G.544 | VESTIBULE | #REF!
entity:HQ_G.601_CORRIDOR | G.601 | CORRIDOR | #REF!
entity:HQ_G.FF-1_FF-1 | G.FF-1 | FF-1 | #REF!
entity:HQ_G.P-1_P-1 | G.P-1 | P-1 | #REF!
entity:HQ_G.P-2_P-2 | G.P-2 | P-2 | #REF!
entity:HQ_G.P-3_P-3 | G.P-3 | P-3 | #REF!
entity:HQ_G.P-4_P-4 | G.P-4 | P-4 | #REF!
entity:HQ_G.P-5_P-5 | G.P-5 | P-5 | #REF!
entity:HQ_G.P-6_P-6 | G.P-6 | P-6 | #REF!
entity:HQ_G.S-1_S-1 | G.S-1 | S-1 | #REF!
entity:HQ_G.ST-1_ST-1 | G.ST-1 | ST-1 | #REF!
entity:HQ_G.ST-2_ST-2 | G.ST-2 | ST-2 | #REF!
entity:HQ_G.ST-3_ST-3 | G.ST-3 | ST-3 | #REF!
entity:HQ_G.ST-4_ST-4 | G.ST-4 | ST-4 | #REF!
entity:HQ_1.001_FINANCE_CLERICAL_SECRETARIES | 1.001 | FINANCE_CLERICAL_SECRETARIES | #REF!
entity:HQ_1.002_FINANCE_MANAGERS | 1.002 | FINANCE_MANAGERS | #REF!
entity:HQ_1.003_FINANCE_MANAGER | 1.003 | FINANCE_MANAGER | #REF!
entity:HQ_1.004_FINANCE_MANAGER | 1.004 | FINANCE_MANAGER | #REF!
entity:HQ_1.005_FINANCE_SECRETARY | 1.005 | FINANCE_SECRETARY | #REF!
entity:HQ_1.006_FINANCE_PROFSTAFF | 1.006 | FINANCE_PROFSTAFF | #REF!
entity:HQ_1.007_FINANCE_CLERICAL_PROFSTAFF | 1.007 | FINANCE_CLERICAL_PROFSTAFF | #REF!
entity:HQ_1.009_FINANCE_MANAGER | 1.009 | FINANCE_MANAGER | #REF!
entity:HQ_1.011_FINANCE_MANAGER | 1.011 | FINANCE_MANAGER | #REF!
entity:HQ_1.012_FINANCE_MANAGER | 1.012 | FINANCE_MANAGER | #REF!
entity:HQ_1.013_FINANCE_MANAGER | 1.013 | FINANCE_MANAGER | #REF!
entity:HQ_1.014_FINANCE_PROFSTAFF | 1.014 | FINANCE_PROFSTAFF | #REF!
entity:HQ_1.015_FINANCE_PROFSTAFF | 1.015 | FINANCE_PROFSTAFF | #REF!
entity:HQ_1.016_FINANCE_SECRETARY | 1.016 | FINANCE_SECRETARY | #REF!
entity:HQ_1.017_FINANCE_DIRECTOR_ENSUIT | 1.017 | FINANCE_DIRECTOR_ENSUIT | #REF!
entity:HQ_1.018_FINANCE_MANAGER | 1.018 | FINANCE_MANAGER | #REF!
entity:HQ_1.019_FINANCE_MANAGER | 1.019 | FINANCE_MANAGER | #REF!
entity:HQ_1.02_FINANCE_MANAGER | 1.02 | FINANCE_MANAGER | #REF!
entity:HQ_1.021_FINANCE_SECRETARY | 1.021 | FINANCE_SECRETARY | #REF!
entity:HQ_1.022_FINANCE_SECRETARY | 1.022 | FINANCE_SECRETARY | #REF!
entity:HQ_1.023_FINANCE_AUDITOR | 1.023 | FINANCE_AUDITOR | #REF!
entity:HQ_1.024_FINANCE_AUDITOR | 1.024 | FINANCE_AUDITOR | #REF!
entity:HQ_1.025_FINANCE_PROFSTAFF | 1.025 | FINANCE_PROFSTAFF | #REF!
entity:HQ_1.026_FINANCE_PROFSTAFF | 1.026 | FINANCE_PROFSTAFF | #REF!
entity:HQ_1.027_FINANCE_AUDITOR | 1.027 | FINANCE_AUDITOR | #REF!
entity:HQ_1.028_FINANCE_MANAGER | 1.028 | FINANCE_MANAGER | #REF!
entity:HQ_1.101_STAFF_LOUNGE | 1.101 | STAFF_LOUNGE | #REF!
entity:HQ_1.102_PRAYER_ROOM_VESTIBULE | 1.102 | PRAYER_ROOM_VESTIBULE | #REF!
entity:HQ_1.103_ABLUTION_ROOM | 1.103 | ABLUTION_ROOM | #REF!
entity:HQ_1.104_ABLUTION_ROOM | 1.104 | ABLUTION_ROOM | #REF!
entity:HQ_1.105_PRAYER_ROOM | 1.105 | PRAYER_ROOM | #REF!
entity:HQ_1.106_FINANCE_CASHIER | 1.106 | FINANCE_CASHIER | #REF!
entity:HQ_1.108_FINANCE_MEETING_ROOM | 1.108 | FINANCE_MEETING_ROOM | #REF!
entity:HQ_1.109_CONSULTANT_SPACE_TRAINEES | 1.109 | CONSULTANT_SPACE_TRAINEES | #REF!
entity:HQ_1.11_CONFERENCE_ROOM | 1.11 | CONFERENCE_ROOM | #REF!
entity:HQ_1.111_FINANCE_RECORD_STORAGE | 1.111 | FINANCE_RECORD_STORAGE | #REF!
entity:HQ_1.112_PRINT_COPY | 1.112 | PRINT_COPY | #REF!
entity:HQ_1.113_PANTRY | 1.113 | PANTRY | #REF!
entity:HQ_1.114_STAFF_LOUNGE_STORAGE | 1.114 | STAFF_LOUNGE_STORAGE | #REF!
entity:HQ_1.115_FINANCE_AUDITOR | 1.115 | FINANCE_AUDITOR | #REF!
entity:HQ_1.116_FINANCE_SECURE_ROOM | 1.116 | FINANCE_SECURE_ROOM | #REF!
entity:HQ_1.117_FINANCE_AUDITOR | 1.117 | FINANCE_AUDITOR | #REF!
entity:HQ_1.403_MALE_TOILET | 1.403 | MALE_TOILET | #REF!
entity:HQ_1.404_FEMALE_TOILET | 1.404 | FEMALE_TOILET | #REF!
entity:HQ_1.405_TOILET | 1.405 | TOILET | #REF!
entity:HQ_1.512_IDF_ROOM | 1.512 | IDF_ROOM | #REF!
entity:HQ_1.521_VESTIBULE | 1.521 | VESTIBULE | #REF!
entity:HQ_1.531_IDF_ROOM | 1.531 | IDF_ROOM | #REF!
entity:HQ_1.532_ELECTRICAL_CLOSET_1 | 1.532 | ELECTRICAL_CLOSET_1 | #REF!
entity:HQ_1.533_ELECTRICAL_CLOSET_2 | 1.533 | ELECTRICAL_CLOSET_2 | #REF!
entity:HQ_1.541_VESTIBULE | 1.541 | VESTIBULE | #REF!
entity:HQ_1.601_CORRIDOR | 1.601 | CORRIDOR | #REF!
entity:HQ_1.602_CORRIDOR | 1.602 | CORRIDOR | #REF!
entity:HQ_1.603_CORRIDOR | 1.603 | CORRIDOR | #REF!
entity:HQ_1.701_STAFF_CAFETERIA | 1.701 | STAFF_CAFETERIA | #REF!
entity:HQ_1.702_FOOD_HEAT_UP | 1.702 | FOOD_HEAT_UP | #REF!
entity:HQ_1.703_COSHSTORE | 1.703 | COSHSTORE | #REF!
entity:HQ_1.704_REFUSE_HOLDING_A | 1.704 | REFUSE_HOLDING_A | #REF!
entity:HQ_1.705_PREP | 1.705 | PREP | #REF!
entity:HQ_1.706_WASHING_AREA | 1.706 | WASHING_AREA | #REF!
entity:HQ_1.FF-1_FF-1 | 1.FF-1 | FF-1 | #REF!
entity:HQ_1.P-1_P-1 | 1.P-1 | P-1 | #REF!
entity:HQ_1.P-2_P-2 | 1.P-2 | P-2 | #REF!
entity:HQ_1.P-3_P-3 | 1.P-3 | P-3 | #REF!
entity:HQ_1.P-4_P-4 | 1.P-4 | P-4 | #REF!
entity:HQ_1.P-5_P-5 | 1.P-5 | P-5 | #REF!
entity:HQ_1.P-6_P-6 | 1.P-6 | P-6 | #REF!
entity:HQ_1.S-1_S-1 | 1.S-1 | S-1 | #REF!
entity:HQ_1.ST-1_ST-1 | 1.ST-1 | ST-1 | #REF!
entity:HQ_1.ST-2_ST-2 | 1.ST-2 | ST-2 | #REF!
entity:HQ_1.ST-3_ST-3 | 1.ST-3 | ST-3 | #REF!
entity:HQ_1.ST-4_ST-4 | 1.ST-4 | ST-4 | #REF!
entity:HQ_2.001_STORAGE_ROOM | 2.001 | STORAGE_ROOM | #REF!
entity:HQ_2.002_DOHA_DEBATE_EXECUTIVE | 2.002 | DOHA_DEBATE_EXECUTIVE | #REF!
entity:HQ_2.003_DOHA_DEBATE_EXECUTIVE | 2.003 | DOHA_DEBATE_EXECUTIVE | #REF!
entity:HQ_2.004_DOHA_DEBATE_SECRETARY | 2.004 | DOHA_DEBATE_SECRETARY | #REF!
entity:HQ_2.005_DOHA_DEBATE_EXECUTIVE | 2.005 | DOHA_DEBATE_EXECUTIVE | #REF!
entity:HQ_2.006_DOHA_DEBATE_EXECUTIVE | 2.006 | DOHA_DEBATE_EXECUTIVE | #REF!
entity:HQ_2.007_DOHA_DEBATE_EXECUTIVE | 2.007 | DOHA_DEBATE_EXECUTIVE | #REF!
entity:HQ_2.008_DOHA_DEBATE_EXECUTIVE | 2.008 | DOHA_DEBATE_EXECUTIVE | #REF!
entity:HQ_2.009_SUPPSERVSECRETARY | 2.009 | SUPPSERVSECRETARY | #REF!
entity:HQ_2.01_SUPPSERVADMINIST | 2.01 | SUPPSERVADMINIST | #REF!
entity:HQ_2.011_SUPPSERVADMINIST | 2.011 | SUPPSERVADMINIST | #REF!
entity:HQ_2.012_SUPPSERVADMINIST | 2.012 | SUPPSERVADMINIST | #REF!
entity:HQ_2.013_SUPPSERVSECRETARY | 2.013 | SUPPSERVSECRETARY | #REF!
entity:HQ_2.014_SUPPSERVADMINIST | 2.014 | SUPPSERVADMINIST | #REF!
entity:HQ_2.015_SUPPSERVADMINIST | 2.015 | SUPPSERVADMINIST | #REF!
entity:HQ_2.016_SUPPSERVADMINIST | 2.016 | SUPPSERVADMINIST | #REF!
entity:HQ_2.017_SUPPSERVSECRETARY | 2.017 | SUPPSERVSECRETARY | #REF!
entity:HQ_2.018_SUPPSERVDIRECTOR_ENSUIT | 2.018 | SUPPSERVDIRECTOR_ENSUIT | #REF!
entity:HQ_2.019_SUPPSERVADMINIST | 2.019 | SUPPSERVADMINIST | #REF!
entity:HQ_2.02_SUPPSERVADMINIST | 2.02 | SUPPSERVADMINIST | #REF!
entity:HQ_2.021_SUPPSERVADMINIST | 2.021 | SUPPSERVADMINIST | #REF!
entity:HQ_2.022_SUPPSERVSECRETARY | 2.022 | SUPPSERVSECRETARY | #REF!
entity:HQ_2.023_SUPPSERVADMINIST | 2.023 | SUPPSERVADMINIST | #REF!
entity:HQ_2.024_SUPPSERVADMINIST | 2.024 | SUPPSERVADMINIST | #REF!
entity:HQ_2.025_SUPPSERVADMINIST | 2.025 | SUPPSERVADMINIST | #REF!
entity:HQ_2.026_SUPPSERVSECRETARY | 2.026 | SUPPSERVSECRETARY | #REF!
entity:HQ_2.027_SUPPSERVADMINIST | 2.027 | SUPPSERVADMINIST | #REF!
entity:HQ_2.028_SUPPSERVADMINIST | 2.028 | SUPPSERVADMINIST | #REF!
entity:HQ_2.029_SUPPSERVADMINIST | 2.029 | SUPPSERVADMINIST | #REF!
entity:HQ_2.03_SUPPSERVSECRETARY | 2.03 | SUPPSERVSECRETARY | #REF!
entity:HQ_2.031_SUPPSERVADMINIST | 2.031 | SUPPSERVADMINIST | #REF!
entity:HQ_2.032_SUPPSERVADMINIST | 2.032 | SUPPSERVADMINIST | #REF!
entity:HQ_2.033_SUPPSERVADMINIST | 2.033 | SUPPSERVADMINIST | #REF!
entity:HQ_2.034_SUPPSERVSECRETARY | 2.034 | SUPPSERVSECRETARY | #REF!
entity:HQ_2.035_SUPPSERVADMINIST | 2.035 | SUPPSERVADMINIST | #REF!
entity:HQ_2.036_SUPPSERVADMINIST | 2.036 | SUPPSERVADMINIST | #REF!
entity:HQ_2.102_CONSULTANTS_SPACE-OTHERS | 2.102 | CONSULTANTS_SPACE-OTHERS | #REF!
entity:HQ_2.103_PRINT_COPY | 2.103 | PRINT_COPY | #REF!
entity:HQ_2.104_CONSULTANTS_SPACE-OTHERS | 2.104 | CONSULTANTS_SPACE-OTHERS | #REF!
entity:HQ_2.105_LOUNGE | 2.105 | LOUNGE | #REF!
entity:HQ_2.106_PANTRY | 2.106 | PANTRY | #REF!
entity:HQ_2.107_JANITORS_CLOSET | 2.107 | JANITORS_CLOSET | #REF!
entity:HQ_2.108_SUPPSERVMEETING_ROOM | 2.108 | SUPPSERVMEETING_ROOM | #REF!
entity:HQ_2.109_SHELL_SPACE | 2.109 | SHELL_SPACE | #REF!
entity:HQ_2.11_SHELL_SPACE | 2.11 | SHELL_SPACE | #REF!
entity:HQ_2.111_ELECTRICAL_CABINET | 2.111 | ELECTRICAL_CABINET | #REF!
entity:HQ_2.201_SPA_MALE_RELAXATION | 2.201 | SPA_MALE_RELAXATION | #REF!
entity:HQ_2.202_SPA_MALE_TREATMENT_3 | 2.202 | SPA_MALE_TREATMENT_3 | #REF!
entity:HQ_2.203_SPA_MALE_TREATMENT_2 | 2.203 | SPA_MALE_TREATMENT_2 | #REF!
entity:HQ_2.204_SPA_MALE_TREATMENT_1 | 2.204 | SPA_MALE_TREATMENT_1 | #REF!
entity:HQ_2.205_SPA_MALE_CHANGING_ROOM | 2.205 | SPA_MALE_CHANGING_ROOM | #REF!
entity:HQ_2.206_SPA_ENTRANCE | 2.206 | SPA_ENTRANCE | #REF!
entity:HQ_2.207_SPA_LOUNGE_BAR | 2.207 | SPA_LOUNGE_BAR | #REF!
entity:HQ_2.208_SPA_FITNESS_DTUDIO | 2.208 | SPA_FITNESS_DTUDIO | #REF!
entity:HQ_2.209_SPA_OFFICE | 2.209 | SPA_OFFICE | #REF!
entity:HQ_2.21_SPA_STAFF_WAITING_AREA | 2.21 | SPA_STAFF_WAITING_AREA | #REF!
entity:HQ_2.211_SPA_FEMALE_BEAUTY_SALON | 2.211 | SPA_FEMALE_BEAUTY_SALON | #REF!
entity:HQ_2.212_SPA_FM_TREATMENT_1 | 2.212 | SPA_FM_TREATMENT_1 | #REF!
entity:HQ_2.213_SPA_CHANGING_ROOM | 2.213 | SPA_CHANGING_ROOM | #REF!
entity:HQ_2.214_SPA_FM_TREATMENT_2 | 2.214 | SPA_FM_TREATMENT_2 | #REF!
entity:HQ_2.215_SPA_FM_TREATMENT_3 | 2.215 | SPA_FM_TREATMENT_3 | #REF!
entity:HQ_2.216_SPA_FM_RELAXATION | 2.216 | SPA_FM_RELAXATION | #REF!
entity:HQ_2.217_SPA_STORAGE | 2.217 | SPA_STORAGE | #REF!
entity:HQ_2.218_SPA_STORAGE | 2.218 | SPA_STORAGE | #REF!
entity:HQ_2.219_SPA_STORAGE | 2.219 | SPA_STORAGE | #REF!
entity:HQ_2.22_SPA_STERILIZATION_ROOM | 2.22 | SPA_STERILIZATION_ROOM | #REF!
entity:HQ_2.301_SPA_LAUNDRY | 2.301 | SPA_LAUNDRY | #REF!
entity:HQ_2.302_SPA_PLANTROOM | 2.302 | SPA_PLANTROOM | #REF!
entity:HQ_2.303_SPA_LAUNDRY | 2.303 | SPA_LAUNDRY | #REF!
entity:HQ_2.304_SPA_MALE_HEAT_EXP | 2.304 | SPA_MALE_HEAT_EXP | #REF!
entity:HQ_2.305_SPA_JACUZZI | 2.305 | SPA_JACUZZI | #REF!
entity:HQ_2.306_SPA_HAMMAM | 2.306 | SPA_HAMMAM | #REF!
entity:HQ_2.307_SPA_SHOWER | 2.307 | SPA_SHOWER | #REF!
entity:HQ_2.308_SPA_SCRUB | 2.308 | SPA_SCRUB | #REF!
entity:HQ_2.309_SPA_SAUNA | 2.309 | SPA_SAUNA | #REF!
entity:HQ_2.31_SPA_TECHNIC | 2.31 | SPA_TECHNIC | #REF!
entity:HQ_2.311_SPA_FM_HEAT_EXP | 2.311 | SPA_FM_HEAT_EXP | #REF!
entity:HQ_2.312_SPA_SAUNA | 2.312 | SPA_SAUNA | #REF!
entity:HQ_2.313_SPA_SCRUB | 2.313 | SPA_SCRUB | #REF!
entity:HQ_2.314_SPA_SHOWER | 2.314 | SPA_SHOWER | #REF!
entity:HQ_2.315_SPA_HAMMAM | 2.315 | SPA_HAMMAM | #REF!
entity:HQ_2.316_SPA_JACUZZI | 2.316 | SPA_JACUZZI | #REF!
entity:HQ_2.317_SPA_TECHNIC | 2.317 | SPA_TECHNIC | #REF!
entity:HQ_2.318_SPA_TECHNIC | 2.318 | SPA_TECHNIC | #REF!
entity:HQ_2.401_MALE_TOILET | 2.401 | MALE_TOILET | #REF!
entity:HQ_2.402_FEMALE_TOILET | 2.402 | FEMALE_TOILET | #REF!
entity:HQ_2.403_MALE_TOILET | 2.403 | MALE_TOILET | #REF!
entity:HQ_2.404_FEMALE_TOILET | 2.404 | FEMALE_TOILET | #REF!
entity:HQ_2.405_TOILET | 2.405 | TOILET | #REF!
entity:HQ_2.406_SPA_STAFF_FEMALE_WC | 2.406 | SPA_STAFF_FEMALE_WC | #REF!
entity:HQ_2.407_SPA_STAFF_MALE_WC | 2.407 | SPA_STAFF_MALE_WC | #REF!
entity:HQ_2.512_MECHANICAL_ROOM | 2.512 | MECHANICAL_ROOM | #REF!
entity:HQ_2.521_VESTIBULE | 2.521 | VESTIBULE | #REF!
entity:HQ_2.531_IDF_ROOM | 2.531 | IDF_ROOM | #REF!
entity:HQ_2.532_ELECTRICAL_CLOSET_1 | 2.532 | ELECTRICAL_CLOSET_1 | #REF!
entity:HQ_2.533_ELECTRICAL_CLOSET_2 | 2.533 | ELECTRICAL_CLOSET_2 | #REF!
entity:HQ_2.541_VESTIBULE | 2.541 | VESTIBULE | #REF!
entity:HQ_2.601_S-TOWER_CORRIDOR | 2.601 | S-TOWER_CORRIDOR | #REF!
entity:HQ_2.602_SPA_CORRIDOR | 2.602 | SPA_CORRIDOR | #REF!
entity:HQ_2.603_SPA_LOBBY | 2.603 | SPA_LOBBY | #REF!
entity:HQ_2.604_SPA_CORRIDOR | 2.604 | SPA_CORRIDOR | #REF!
entity:HQ_2.FF-1_FF-1 | 2.FF-1 | FF-1 | #REF!
entity:HQ_2.P-1_P-1 | 2.P-1 | P-1 | #REF!
entity:HQ_2.P-2_P-2 | 2.P-2 | P-2 | #REF!
entity:HQ_2.P-3_P-3 | 2.P-3 | P-3 | #REF!
entity:HQ_2.P-4_P-4 | 2.P-4 | P-4 | #REF!
entity:HQ_2.P-5_P-5 | 2.P-5 | P-5 | #REF!
entity:HQ_2.P-6_P-6 | 2.P-6 | P-6 | #REF!
entity:HQ_2.S-1_S-1 | 2.S-1 | S-1 | #REF!
entity:HQ_2.ST-1_ST-1 | 2.ST-1 | ST-1 | #REF!
entity:HQ_2.ST-2_ST-2 | 2.ST-2 | ST-2 | #REF!
entity:HQ_2.ST-3_ST-3 | 2.ST-3 | ST-3 | #REF!
entity:HQ_2.ST-4_ST-4 | 2.ST-4 | ST-4 | #REF!
entity:HQ_3.001_LOUNGE | 3.001 | LOUNGE | #REF!
entity:HQ_3.002_HR_IMMIG_STAFF | 3.002 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.003_HR_IMMIG_STAFF | 3.003 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.004_HR_IMMIG_STAFF | 3.004 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.005_HR_IMMIG_STAFF | 3.005 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.006_HR_IMMIG_STAFF | 3.006 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.007_HR_IMMIG_STAFF | 3.007 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.008_HR_IMMIG_STAFF | 3.008 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.009_HR_IMMIG_STORAGE | 3.009 | HR_IMMIG_STORAGE | #REF!
entity:HQ_3.01_HR_IMMIG_STAFF | 3.01 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.011_HR_IMMIG_STAFF | 3.011 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.012_HR_IMMIG_STAFF | 3.012 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.013_HR_IMMIG_STAFF | 3.013 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.014_HR_IMMIG_STAFF | 3.014 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.015_HR_IMMIG_STAFF | 3.015 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.016_HR_IMMIG_STAFF | 3.016 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.017_HR_IMMIG_STAFF | 3.017 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.018_HR_IMMIG_STAFF | 3.018 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.019_HR_IMMIG_STAFF | 3.019 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.02_HR_IMMIG_STAFF | 3.02 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.021_HR_IMMIG_STAFF | 3.021 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.022_HR_IMMIG_SECRETARY | 3.022 | HR_IMMIG_SECRETARY | #REF!
entity:HQ_3.023_HR_IMMIG_STAFF | 3.023 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.024_HR_IMMIG_STAFF | 3.024 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.025_HR_IMMIG_STAFF | 3.025 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.026_HR_IMMIG_STAFF | 3.026 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.027_HR_IMMIG_STAFF | 3.027 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.028_HR_IMMIG_STAFF | 3.028 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.029_HR_IMMIG_STAFF | 3.029 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.03_HR_IMMIG_STAFF | 3.03 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.031_HR_IMMIG_STAFF | 3.031 | HR_IMMIG_STAFF | #REF!
entity:HQ_3.032_HR_IMMIG_SECRETARY | 3.032 | HR_IMMIG_SECRETARY | #REF!
entity:HQ_3.033_MEETING_ROOM | 3.033 | MEETING_ROOM | #REF!
entity:HQ_3.101_SHELL_SPACE | 3.101 | SHELL_SPACE | #REF!
entity:HQ_3.102_CONSULTANT_SPACE_TRAINEES | 3.102 | CONSULTANT_SPACE_TRAINEES | #REF!
entity:HQ_3.103_PRINT_COPY | 3.103 | PRINT_COPY | #REF!
entity:HQ_3.104_HR_IMMIG_SECRETARY | 3.104 | HR_IMMIG_SECRETARY | #REF!
entity:HQ_3.106_PANTRY | 3.106 | PANTRY | #REF!
entity:HQ_3.107_JANITORS_CLOSET | 3.107 | JANITORS_CLOSET | #REF!
entity:HQ_3.108_SHELL_SPACE | 3.108 | SHELL_SPACE | #REF!
entity:HQ_3.109_ELECTRICAL_CABINET | 3.109 | ELECTRICAL_CABINET | #REF!
entity:HQ_3.201_PROC&CONTRDIRENSUIT | 3.201 | PROC&CONTRDIRENSUIT | #REF!
entity:HQ_3.203_COPYPRINT | 3.203 | COPYPRINT | #REF!
entity:HQ_3.204_PANTRY | 3.204 | PANTRY | #REF!
entity:HQ_3.205_HR_IMMIG_IMMIGRATION | 3.205 | HR_IMMIG_IMMIGRATION | #REF!
entity:HQ_3.206_HR_IMMIG_MANAGER | 3.206 | HR_IMMIG_MANAGER | #REF!
entity:HQ_3.207_HR_IMMIG_MANAGER | 3.207 | HR_IMMIG_MANAGER | #REF!
entity:HQ_3.208_HR_IMMIG_MANAGER | 3.208 | HR_IMMIG_MANAGER | #REF!
entity:HQ_3.209_HR_IMMIG_MANAGER | 3.209 | HR_IMMIG_MANAGER | #REF!
entity:HQ_3.21_HR_IMMIG_OFFICERS | 3.21 | HR_IMMIG_OFFICERS | #REF!
entity:HQ_3.211_HR_IMMIG_MANAGER | 3.211 | HR_IMMIG_MANAGER | #REF!
entity:HQ_3.212_HR_IMMIG_SECRETARIES | 3.212 | HR_IMMIG_SECRETARIES | #REF!
entity:HQ_3.213_HR_IMMIG_DIRENSUIT | 3.213 | HR_IMMIG_DIRENSUIT | #REF!
entity:HQ_3.214_IT_SECRETARY | 3.214 | IT_SECRETARY | #REF!
entity:HQ_3.215_IT_DIRENSUIT | 3.215 | IT_DIRENSUIT | #REF!
entity:HQ_3.216_PROC&CONTRSECRETARY | 3.216 | PROC&CONTRSECRETARY | #REF!
entity:HQ_3.301_PROC&CONTRMEETING_ROOM | 3.301 | PROC&CONTRMEETING_ROOM | #REF!
entity:HQ_3.302_HR_IMMIG_MEETING_ROOM | 3.302 | HR_IMMIG_MEETING_ROOM | #REF!
entity:HQ_3.401_MALE_TOILET | 3.401 | MALE_TOILET | #REF!
entity:HQ_3.402_FEMALE_TOILET | 3.402 | FEMALE_TOILET | #REF!
entity:HQ_3.403_MALE_TOILET | 3.403 | MALE_TOILET | #REF!
entity:HQ_3.404_FEMALE_TOILET | 3.404 | FEMALE_TOILET | #REF!
entity:HQ_3.405_MALE_TOILET | 3.405 | MALE_TOILET | #REF!
entity:HQ_3.406_FEMALE_TOILET | 3.406 | FEMALE_TOILET | #REF!
entity:HQ_3.407_TOILET | 3.407 | TOILET | #REF!
entity:HQ_3.408_TOILET | 3.408 | TOILET | #REF!
entity:HQ_3.409_TOILET | 3.409 | TOILET | #REF!
entity:HQ_3.511_VESTIBULE | 3.511 | VESTIBULE | #REF!
entity:HQ_3.512_IDF_ROOM | 3.512 | IDF_ROOM | #REF!
entity:HQ_3.521_VESTIBULE | 3.521 | VESTIBULE | #REF!
entity:HQ_3.531_IDF_ROOM | 3.531 | IDF_ROOM | #REF!
entity:HQ_3.532_ELECTRICAL_CLOSET_1 | 3.532 | ELECTRICAL_CLOSET_1 | #REF!
entity:HQ_3.533_ELECTRICAL_CLOSET_12 | 3.533 | ELECTRICAL_CLOSET_12 | #REF!
entity:HQ_3.541_VESTIBULE | 3.541 | VESTIBULE | #REF!
entity:HQ_3.601_S-TOWER_CORRIDOR | 3.601 | S-TOWER_CORRIDOR | #REF!
entity:HQ_3.602_E-TOWER_CORRIDOR | 3.602 | E-TOWER_CORRIDOR | #REF!
entity:HQ_3.603_CORRIDOR_BRIDGE | 3.603 | CORRIDOR_BRIDGE | #REF!
entity:HQ_3.FF-1_FF-1 | 3.FF-1 | FF-1 | #REF!
entity:HQ_3.P-1_P-1 | 3.P-1 | P-1 | #REF!
entity:HQ_3.P-2_P-2 | 3.P-2 | P-2 | #REF!
entity:HQ_3.P-3_P-3 | 3.P-3 | P-3 | #REF!
entity:HQ_3.P-4_P-4 | 3.P-4 | P-4 | #REF!
entity:HQ_3.P-5_P-5 | 3.P-5 | P-5 | #REF!
entity:HQ_3.P-6_P-6 | 3.P-6 | P-6 | #REF!
entity:HQ_3.S-1_S-1 | 3.S-1 | S-1 | #REF!
entity:HQ_3.ST-1_ST-1 | 3.ST-1 | ST-1 | #REF!
entity:HQ_3.ST-2_ST-2 | 3.ST-2 | ST-2 | #REF!
entity:HQ_3.ST-3_ST-3 | 3.ST-3 | ST-3 | #REF!
entity:HQ_3.ST-4_ST-4 | 3.ST-4 | ST-4 | #REF!
entity:HQ_4.002_STRPLDIRMANAGER | 4.002 | STRPLDIRMANAGER | #REF!
entity:HQ_04.004_ENS_STRPLDIRENSUIT | 04.004_ENS | STRPLDIRENSUIT | #REF!
entity:HQ_04.004_EXE_STRPLDIREXECSECRETARY | 04.004_EXE | STRPLDIREXECSECRETARY | #REF!
entity:HQ_4.005_STRPLDIRMEETING_ROOM | 4.005 | STRPLDIRMEETING_ROOM | #REF!
entity:HQ_4.006_STRPLDIRMANAGER | 4.006 | STRPLDIRMANAGER | #REF!
entity:HQ_4.007_STRPLDIRMANAGER | 4.007 | STRPLDIRMANAGER | #REF!
entity:HQ_4.008_STRPLDIRMANAGER | 4.008 | STRPLDIRMANAGER | #REF!
entity:HQ_4.009_STRPLDIRHEAD_OF_PL | 4.009 | STRPLDIRHEAD_OF_PL | #REF!
entity:HQ_4.01_STRPLDIRHEAD_OF_PL | 4.01 | STRPLDIRHEAD_OF_PL | #REF!
entity:HQ_4.011_STRPLDIRHEAD_OF_PL | 4.011 | STRPLDIRHEAD_OF_PL | #REF!
entity:HQ_4.012_STRPLDIRHEAD_OF_PL | 4.012 | STRPLDIRHEAD_OF_PL | #REF!
entity:HQ_4.013_STRPLDIRHEAD_OF_PL | 4.013 | STRPLDIRHEAD_OF_PL | #REF!
entity:HQ_4.014_STRPLDIRMANAGER | 4.014 | STRPLDIRMANAGER | #REF!
entity:HQ_4.101_SHELL_SPACE | 4.101 | SHELL_SPACE | #REF!
entity:HQ_4.102_SHELL_SPACE | 4.102 | SHELL_SPACE | #REF!
entity:HQ_04.103_ELE_ELECTRICAL_CABINET | 04.103_ELE | ELECTRICAL_CABINET | #REF!
entity:HQ_04.103_STO_STORAGE_SPACE | 04.103_STO | STORAGE_SPACE | #REF!
entity:HQ_4.104_WAITING_LOUNGE | 4.104 | WAITING_LOUNGE | #REF!
entity:HQ_04.105_JAN_JANITORS_CLOSET | 04.105_JAN | JANITORS_CLOSET | #REF!
entity:HQ_04.105_PAN_PANTRY | 04.105_PAN | PANTRY | #REF!
entity:HQ_4.107_STRPLDIRTECHNSTAFF | 4.107 | STRPLDIRTECHNSTAFF | #REF!
entity:HQ_4.108_STRPLDIRARCHIVE_ROOM | 4.108 | STRPLDIRARCHIVE_ROOM | #REF!
entity:HQ_4.109_VP_EDU_STORAGE | 4.109 | VP_EDU_STORAGE | #REF!
entity:HQ_4.201_SHELL_SPACE | 4.201 | SHELL_SPACE | #REF!
entity:HQ_4.202_PRINT_COPY | 4.202 | PRINT_COPY | #REF!
entity:HQ_4.203_PANTRY | 4.203 | PANTRY | #REF!
entity:HQ_4.204_SHELL_SPACE | 4.204 | SHELL_SPACE | #REF!
entity:HQ_4.205_VP_ADM_MANAGER | 4.205 | VP_ADM_MANAGER | #REF!
entity:HQ_4.206_VP_ADM_MANAGER | 4.206 | VP_ADM_MANAGER | #REF!
entity:HQ_4.207_VP_ADM_SUPPSECRET | 4.207 | VP_ADM_SUPPSECRET | #REF!
entity:HQ_4.208_VP_ADM_EXECSECRET | 4.208 | VP_ADM_EXECSECRET | #REF!
entity:HQ_4.209_VP_ADM_MANAGER | 4.209 | VP_ADM_MANAGER | #REF!
entity:HQ_4.21_VP_ADM_MANAGER | 4.21 | VP_ADM_MANAGER | #REF!
entity:HQ_4.211_VP_ADM_MANAGER | 4.211 | VP_ADM_MANAGER | #REF!
entity:HQ_4.212_VP_ADM_PERSASSIST | 4.212 | VP_ADM_PERSASSIST | #REF!
entity:HQ_4.213_VP_ADM_ENSUIT | 4.213 | VP_ADM_ENSUIT | #REF!
entity:HQ_4.214_GSM_ROOM | 4.214 | GSM_ROOM | #REF!
entity:HQ_4.301_VP_ADM_MEETING_ROOM | 4.301 | VP_ADM_MEETING_ROOM | #REF!
entity:HQ_4.401_MALE_TOILET | 4.401 | MALE_TOILET | #REF!
entity:HQ_4.402_FEMALE_TOILET | 4.402 | FEMALE_TOILET | #REF!
entity:HQ_4.403_MALE_TOILET | 4.403 | MALE_TOILET | #REF!
entity:HQ_4.404_FEMALE_TOILET | 4.404 | FEMALE_TOILET | #REF!
entity:HQ_4.405_TOILET | 4.405 | TOILET | #REF!
entity:HQ_4.406_TOILET | 4.406 | TOILET | #REF!
entity:HQ_4.511_VESTIBULE | 4.511 | VESTIBULE | #REF!
entity:HQ_4.512_IDF_ROOM | 4.512 | IDF_ROOM | #REF!
entity:HQ_4.514_VESTIBULE | 4.514 | VESTIBULE | #REF!
entity:HQ_4.521_VESTIBULE | 4.521 | VESTIBULE | #REF!
entity:HQ_4.531_IDF_ROOM | 4.531 | IDF_ROOM | #REF!
entity:HQ_4.532_ELECTRICAL_CLOSET | 4.532 | ELECTRICAL_CLOSET | #REF!
entity:HQ_4.533_ELECTRICAL_CLOSET_2 | 4.533 | ELECTRICAL_CLOSET_2 | #REF!
entity:HQ_4.601_S-TOWER_CORRIDOR | 4.601 | S-TOWER_CORRIDOR | #REF!
entity:HQ_4.602_BRIDGE | 4.602 | BRIDGE | #REF!
entity:HQ_4.603_E-TOWER_CORRIDOR | 4.603 | E-TOWER_CORRIDOR | #REF!
entity:HQ_4.604_PRINT_COPY | 4.604 | PRINT_COPY | #REF!
entity:HQ_4.701_VP_ADM_TERRACE | 4.701 | VP_ADM_TERRACE | #REF!
entity:HQ_4.702_TERRACE | 4.702 | TERRACE | #REF!
entity:HQ_4.703_TERRACE | 4.703 | TERRACE | #REF!
entity:HQ_4.P-1_P-1 | 4.P-1 | P-1 | #REF!
entity:HQ_4.P-2_P-2 | 4.P-2 | P-2 | #REF!
entity:HQ_4.P-3_P-3 | 4.P-3 | P-3 | #REF!
entity:HQ_4.P-4_P-4 | 4.P-4 | P-4 | #REF!
entity:HQ_4.P-5_P-5 | 4.P-5 | P-5 | #REF!
entity:HQ_4.P-6_P-6 | 4.P-6 | P-6 | #REF!
entity:HQ_4.S-1_S-1 | 4.S-1 | S-1 | #REF!
entity:HQ_4.ST-1_ST-1 | 4.ST-1 | ST-1 | #REF!
entity:HQ_4.ST-2_ST-2 | 4.ST-2 | ST-2 | #REF!
entity:HQ_4.ST-3_ST-3 | 4.ST-3 | ST-3 | #REF!
entity:HQ_4.ST-4_ST-4 | 4.ST-4 | ST-4 | #REF!
entity:HQ_5.001_VP_EDU_ASSISTANT | 5.001 | VP_EDU_ASSISTANT | #REF!
entity:HQ_5.002_VP_EDU_OFFDIRENSUIT | 5.002 | VP_EDU_OFFDIRENSUIT | #REF!
entity:HQ_5.003_VP_EDU_SECRETARY | 5.003 | VP_EDU_SECRETARY | #REF!
entity:HQ_5.004_VP_EDU_ASSISTANT | 5.004 | VP_EDU_ASSISTANT | #REF!
entity:HQ_5.005_VP_EDU_OFFICERS | 5.005 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.006_VP_EDU_OFFICERS | 5.006 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.007_VP_EDU_OFFICERS | 5.007 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.008_VP_EDU_ASSISTANT | 5.008 | VP_EDU_ASSISTANT | #REF!
entity:HQ_5.009_VP1_VP_EDU_OFFICERS | 5.009_VP1 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.009_VP1_VP_EDU_ASSISTANT | 5.009_VP1 | VP_EDU_ASSISTANT | #REF!
entity:HQ_5.010_VP_EDU_OFFICERS | 5.010 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.011_VP_EDU_ASSISTANT | 5.011 | VP_EDU_ASSISTANT | #REF!
entity:HQ_5.012_VP_EDU_OFFICE_DIRECTOR_ENSUIT | 5.012 | VP_EDU_OFFICE_DIRECTOR_ENSUIT | #REF!
entity:HQ_5.013_VP_EDU_SECRETARY | 5.013 | VP_EDU_SECRETARY | #REF!
entity:HQ_5.014_VP_EDU_ASSISTANT | 5.014 | VP_EDU_ASSISTANT | #REF!
entity:HQ_5.015_VP_EDU_ASSISTANT | 5.015 | VP_EDU_ASSISTANT | #REF!
entity:HQ_5.016_VP_EDU_ASSISTANT | 5.016 | VP_EDU_ASSISTANT | #REF!
entity:HQ_5.017_VP_EDU_ASSISTANT | 5.017 | VP_EDU_ASSISTANT | #REF!
entity:HQ_5.018_VP_EDU_OFFICERS | 5.018 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.019_VP_EDU_OFFICERS | 5.019 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.020_VP_EDU_OFFICERS | 5.020 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.021_VP_EDU_OFFICERS | 5.021 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.022_VP_EDU_OFFICERS | 5.022 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.023_VP_EDU_OFFICERS | 5.023 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.024_VP_EDU_SECRETARY | 5.024 | VP_EDU_SECRETARY | #REF!
entity:HQ_5.025_VP_EDU_OFFICE_DIRECTOR_ENSUIT | 5.025 | VP_EDU_OFFICE_DIRECTOR_ENSUIT | #REF!
entity:HQ_5.026_VP_EDU_ASSISTANT | 5.026 | VP_EDU_ASSISTANT | #REF!
entity:HQ_5.027_VP_EDU_OFFICERS | 5.027 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.101_VP_EDU_SECRET | 5.101 | VP_EDU_SECRET | #REF!
entity:HQ_5.102_MEETING_ROOM | 5.102 | MEETING_ROOM | #REF!
entity:HQ_5.103_PRINT_COPY | 5.103 | PRINT_COPY | #REF!
entity:HQ_5.104_VP_EDU_LOUNGE_WAITING | 5.104 | VP_EDU_LOUNGE_WAITING | #REF!
entity:HQ_5.105_PANTRY | 5.105 | PANTRY | #REF!
entity:HQ_5.106_JANITORS_CLOSET | 5.106 | JANITORS_CLOSET | #REF!
entity:HQ_5.107_VP_EDUCATION_SUPPSECRET | 5.107 | VP_EDUCATION_SUPPSECRET | #REF!
entity:HQ_5.108_VP_EDU_ASSISTANT | 5.108 | VP_EDU_ASSISTANT | #REF!
entity:HQ_5.109_ELECTRICAL_CABINET | 5.109 | ELECTRICAL_CABINET | #REF!
entity:HQ_5.201_VP_EDU_MEMBERS_OF_EDU | 5.201 | VP_EDU_MEMBERS_OF_EDU | #REF!
entity:HQ_5.202_VP_EDU_MEMBERS_OF_EDU | 5.202 | VP_EDU_MEMBERS_OF_EDU | #REF!
entity:HQ_5.203_VP_EDU_MEMBERS_OF_EDU | 5.203 | VP_EDU_MEMBERS_OF_EDU | #REF!
entity:HQ_5.204_PANTRY | 5.204 | PANTRY | #REF!
entity:HQ_5.205_VP_EDU_MEETING_ROOM | 5.205 | VP_EDU_MEETING_ROOM | #REF!
entity:HQ_5.206_VP_EDU_MEMBERS_OF_EDU | 5.206 | VP_EDU_MEMBERS_OF_EDU | #REF!
entity:HQ_5.207_VP_EDU_MEMBERS_OF_EDU | 5.207 | VP_EDU_MEMBERS_OF_EDU | #REF!
entity:HQ_5.208_VP_EDU_MEMBERS_OF_EDU | 5.208 | VP_EDU_MEMBERS_OF_EDU | #REF!
entity:HQ_5.209_VP_EDU_MEMBERS_OF_EDU | 5.209 | VP_EDU_MEMBERS_OF_EDU | #REF!
entity:HQ_5.210_VP_EDU_ENSUIT | 5.210 | VP_EDU_ENSUIT | #REF!
entity:HQ_5.211_VP_EDU_CHPEXECSECRET | 5.211 | VP_EDU_CHPEXECSECRET | #REF!
entity:HQ_5.212_VP_EDU_MEMBERS_OF_EDU | 5.212 | VP_EDU_MEMBERS_OF_EDU | #REF!
entity:HQ_5.213_VP_EDU_OFFICE_DIRECTOR_ENSUIT | 5.213 | VP_EDU_OFFICE_DIRECTOR_ENSUIT | #REF!
entity:HQ_5.301_PLANT_ROOM | 5.301 | PLANT_ROOM | #REF!
entity:HQ_5.401_MALE_TOILET | 5.401 | MALE_TOILET | #REF!
entity:HQ_5.402_FEMALE_TOILET | 5.402 | FEMALE_TOILET | #REF!
entity:HQ_5.403_MALE_TOILET | 5.403 | MALE_TOILET | #REF!
entity:HQ_5.404_FEMALE_TOILET | 5.404 | FEMALE_TOILET | #REF!
entity:HQ_5.405_TOILET | 5.405 | TOILET | #REF!
entity:HQ_5.406_TOILET | 5.406 | TOILET | #REF!
entity:HQ_5.407_TOILET | 5.407 | TOILET | #REF!
entity:HQ_5.408_TOILET | 5.408 | TOILET | #REF!
entity:HQ_5.409_TOILET | 5.409 | TOILET | #REF!
entity:HQ_5.511_VESTIBULE | 5.511 | VESTIBULE | #REF!
entity:HQ_5.512_IDF_ROOM | 5.512 | IDF_ROOM | #REF!
entity:HQ_5.521_VESTIBULE | 5.521 | VESTIBULE | #REF!
entity:HQ_5.531_IDF_ROOM | 5.531 | IDF_ROOM | #REF!
entity:HQ_5.532_ELECTRICAL_CLOSET_1 | 5.532 | ELECTRICAL_CLOSET_1 | #REF!
entity:HQ_5.533_ELECTRICAL_CLOSET_2 | 5.533 | ELECTRICAL_CLOSET_2 | #REF!
entity:HQ_5.541_VESTIBULE | 5.541 | VESTIBULE | #REF!
entity:HQ_5.601_S-TOWER_CORRIDOR | 5.601 | S-TOWER_CORRIDOR | #REF!
entity:HQ_5.602_BRIDGE | 5.602 | BRIDGE | #REF!
entity:HQ_5.604_BRIDGE | 5.604 | BRIDGE | #REF!
entity:HQ_5.701_TERRACE | 5.701 | TERRACE | #REF!
entity:HQ_5.P-1_P-1 | 5.P-1 | P-1 | #REF!
entity:HQ_5.P-2_P-2 | 5.P-2 | P-2 | #REF!
entity:HQ_5.P-3_P-3 | 5.P-3 | P-3 | #REF!
entity:HQ_5.P-4_P-4 | 5.P-4 | P-4 | #REF!
entity:HQ_5.P-5_P-5 | 5.P-5 | P-5 | #REF!
entity:HQ_5.P-6_P-6 | 5.P-6 | P-6 | #REF!
entity:HQ_5.S-1_S-1 | 5.S-1 | S-1 | #REF!
entity:HQ_5.ST-1_ST-1 | 5.ST-1 | ST-1 | #REF!
entity:HQ_5.ST-2_ST-2 | 5.ST-2 | ST-2 | #REF!
entity:HQ_5.ST-3_ST-3 | 5.ST-3 | ST-3 | #REF!
entity:HQ_5.ST-4_ST-4 | 5.ST-4 | ST-4 | #REF!
entity:HQ_6.001_ACA_AUDIT_ARCHIVE | 6.001 | ACA_AUDIT_ARCHIVE | #REF!
entity:HQ_6.002_INTAUDIT_ARCHIVE_ROOM | 6.002 | INTAUDIT_ARCHIVE_ROOM | #REF!
entity:HQ_6.003_INTAUDIT_SUPPAUDIT | 6.003 | INTAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.004_INTAUDIT_SUPPAUDIT | 6.004 | INTAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.005_INTAUDIT_SUPPAUDIT | 6.005 | INTAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.006_INTAUDIT_SUPPAUDIT | 6.006 | INTAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.007_INTAUDIT_SUPPAUDIT | 6.007 | INTAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.008_INTAUDIT_SUPPAUDIT | 6.008 | INTAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.009_INTAUDIT_SUPPAUDIT | 6.009 | INTAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.01_INTAUDIT_SECRETARY | 6.01 | INTAUDIT_SECRETARY | #REF!
entity:HQ_6.011_INTAUDIT_SEN_JNTAUD | 6.011 | INTAUDIT_SEN_JNTAUD | #REF!
entity:HQ_6.012_INTAUDIT_SEN_JNTAUD | 6.012 | INTAUDIT_SEN_JNTAUD | #REF!
entity:HQ_6.013_INTAUDIT_SECRETARY | 6.013 | INTAUDIT_SECRETARY | #REF!
entity:HQ_6.014_ACAAUDIT_SUPPAUDIT | 6.014 | ACAAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.015_ACAAUDIT_SUPPAUDIT | 6.015 | ACAAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.016_ACAAUDIT_SUPPAUDIT | 6.016 | ACAAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.017_ACAAUDIT_SUPPAUDIT | 6.017 | ACAAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.018_ACAAUDIT_SUPPAUDIT | 6.018 | ACAAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.019_ACAAUDIT_SUPPAUDIT | 6.019 | ACAAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.02_ACAAUDIT_SUPPAUDIT | 6.02 | ACAAUDIT_SUPPAUDIT | #REF!
entity:HQ_6.021_ACAAUDIT_SECRETARY | 6.021 | ACAAUDIT_SECRETARY | #REF!
entity:HQ_6.022_ACAAUDIT_SECRETARY | 6.022 | ACAAUDIT_SECRETARY | #REF!
entity:HQ_6.023_ACAAUDIT_ACASENAUD | 6.023 | ACAAUDIT_ACASENAUD | #REF!
entity:HQ_6.024_ACAAUDIT_ACASENAUD | 6.024 | ACAAUDIT_ACASENAUD | #REF!
entity:HQ_6.025_FACILITY_MANAGSECRETARY | 6.025 | FACILITY_MANAGSECRETARY | #REF!
entity:HQ_6.026_VACILITY_MANAGDIRENSUIT | 6.026 | VACILITY_MANAGDIRENSUIT | #REF!
entity:HQ_6.027_VP_CAPITAL_CONSULTANT | 6.027 | VP_CAPITAL_CONSULTANT | #REF!
entity:HQ_6.028_VP_CAPITAL_CONSULTANT | 6.028 | VP_CAPITAL_CONSULTANT | #REF!
entity:HQ_6.101_SHELL_SPACE | 6.101 | SHELL_SPACE | #REF!
entity:HQ_6.102_SHELL_SPACE | 6.102 | SHELL_SPACE | #REF!
entity:HQ_6.103_SHELL_SPACE | 6.103 | SHELL_SPACE | #REF!
entity:HQ_6.104_PRINT_COPY | 6.104 | PRINT_COPY | #REF!
entity:HQ_6.105_LOUNGE | 6.105 | LOUNGE | #REF!
entity:HQ_6.106_PANTRY | 6.106 | PANTRY | #REF!
entity:HQ_6.107_JANITORS_CLOSET | 6.107 | JANITORS_CLOSET | #REF!
entity:HQ_6.108_VP_CAPITAL_PROJCOORD | 6.108 | VP_CAPITAL_PROJCOORD | #REF!
entity:HQ_6.109_VP_CAPITAL_WORK_ASSIST | 6.109 | VP_CAPITAL_WORK_ASSIST | #REF!
entity:HQ_6.11_ELECTRICAL_CABINET | 6.11 | ELECTRICAL_CABINET | #REF!
entity:HQ_6.201_VP_CAPITAL_PROJMANAGER | 6.201 | VP_CAPITAL_PROJMANAGER | #REF!
entity:HQ_6.202_VP_CAPITAL_PROJMANAGER | 6.202 | VP_CAPITAL_PROJMANAGER | #REF!
entity:HQ_6.203_PANTRY | 6.203 | PANTRY | #REF!
entity:HQ_6.204_VP_CAPITAL_PROJMANAGER | 6.204 | VP_CAPITAL_PROJMANAGER | #REF!
entity:HQ_6.205_VP_CAPITAL_CONSULTANT | 6.205 | VP_CAPITAL_CONSULTANT | #REF!
entity:HQ_6.206_VP_CAPITAL_STORAGE | 6.206 | VP_CAPITAL_STORAGE | #REF!
entity:HQ_6.207_VP_CAPITAL_SECRETARIES | 6.207 | VP_CAPITAL_SECRETARIES | #REF!
entity:HQ_6.208_PRINT_COPY | 6.208 | PRINT_COPY | #REF!
entity:HQ_6.209_VP_CAPITAL_ENSUIT | 6.209 | VP_CAPITAL_ENSUIT | #REF!
entity:HQ_6.21_VP_CAPITAL_SECRETARIES | 6.21 | VP_CAPITAL_SECRETARIES | #REF!
entity:HQ_6.211_VP_CAPITAL_SECRETARIES | 6.211 | VP_CAPITAL_SECRETARIES | #REF!
entity:HQ_6.212_VP_CAPITAL_DIRECTOR_ENSUIT | 6.212 | VP_CAPITAL_DIRECTOR_ENSUIT | #REF!
entity:HQ_6.301_VP_CAPITAL_MEETING_ROOM | 6.301 | VP_CAPITAL_MEETING_ROOM | #REF!
entity:HQ_6.401_MALE_TOILET | 6.401 | MALE_TOILET | #REF!
entity:HQ_6.402_FEMALE_TOILET | 6.402 | FEMALE_TOILET | #REF!
entity:HQ_6.403_MALE_TOILET | 6.403 | MALE_TOILET | #REF!
entity:HQ_6.404_FEMALE_TOILET | 6.404 | FEMALE_TOILET | #REF!
entity:HQ_6.405_TOILET | 6.405 | TOILET | #REF!
entity:HQ_6.406_TOILET | 6.406 | TOILET | #REF!
entity:HQ_6.407_TOILET | 6.407 | TOILET | #REF!
entity:HQ_6.511_VESTIBULE | 6.511 | VESTIBULE | #REF!
entity:HQ_6.512_IDF_ROOM | 6.512 | IDF_ROOM | #REF!
entity:HQ_6.521_VESTIBULE | 6.521 | VESTIBULE | #REF!
entity:HQ_6.531_IDF_ROOM | 6.531 | IDF_ROOM | #REF!
entity:HQ_6.532_ELECTRICAL_CLOSET | 6.532 | ELECTRICAL_CLOSET | #REF!
entity:HQ_6.533_ELECTRICAL_CLOSET_2 | 6.533 | ELECTRICAL_CLOSET_2 | #REF!
entity:HQ_6.541_VESTIBULE | 6.541 | VESTIBULE | #REF!
entity:HQ_6.601_S-TOWER_CORRIDOR | 6.601 | S-TOWER_CORRIDOR | #REF!
entity:HQ_6.602_BRIDGE_CORRIDOR | 6.602 | BRIDGE_CORRIDOR | #REF!
entity:HQ_6.603_E-TOWER_CORRIDOR | 6.603 | E-TOWER_CORRIDOR | #REF!
entity:HQ_6.604_BRIDGE_CORRIDOR | 6.604 | BRIDGE_CORRIDOR | #REF!
entity:HQ_6.P-1_P-1 | 6.P-1 | P-1 | #REF!
entity:HQ_6.P-2_P-2 | 6.P-2 | P-2 | #REF!
entity:HQ_6.P-3_P-3 | 6.P-3 | P-3 | #REF!
entity:HQ_6.P-4_P-4 | 6.P-4 | P-4 | #REF!
entity:HQ_6.P-5_P-5 | 6.P-5 | P-5 | #REF!
entity:HQ_6.P-6_P-6 | 6.P-6 | P-6 | #REF!
entity:HQ_6.S-1_S-1 | 6.S-1 | S-1 | #REF!
entity:HQ_6.ST-1_ST-1 | 6.ST-1 | ST-1 | #REF!
entity:HQ_6.ST-2_ST-2 | 6.ST-2 | ST-2 | #REF!
entity:HQ_6.ST-3_ST-3 | 6.ST-3 | ST-3 | #REF!
entity:HQ_6.ST-4_ST-4 | 6.ST-4 | ST-4 | #REF!
entity:HQ_7.001_DOCUNIT_EMPLOYEE | 7.001 | DOCUNIT_EMPLOYEE | #REF!
entity:HQ_7.002_DOCUNIT_MULTIMEDIA_STUDIO | 7.002 | DOCUNIT_MULTIMEDIA_STUDIO | #REF!
entity:HQ_7.003_DOCUNIT_EMPLOYEE | 7.003 | DOCUNIT_EMPLOYEE | #REF!
entity:HQ_7.004_DOCUNIT_EMPLOYEE | 7.004 | DOCUNIT_EMPLOYEE | #REF!
entity:HQ_7.005_DOCUNIT_EMPLOYEE | 7.005 | DOCUNIT_EMPLOYEE | #REF!
entity:HQ_7.006_DOCUNIT_EMPLOYEE | 7.006 | DOCUNIT_EMPLOYEE | #REF!
entity:HQ_7.007_CA_COORD | 7.007 | CA_COORD | #REF!
entity:HQ_7.008_CA_COORD | 7.008 | CA_COORD | #REF!
entity:HQ_7.009_CA_COORD | 7.009 | CA_COORD | #REF!
entity:HQ_7.01_CA_COORD | 7.01 | CA_COORD | #REF!
entity:HQ_7.011_CA_COORD | 7.011 | CA_COORD | #REF!
entity:HQ_7.012_CA_COORD | 7.012 | CA_COORD | #REF!
entity:HQ_7.013_CA_COORD | 7.013 | CA_COORD | #REF!
entity:HQ_7.014_CA_COORD | 7.014 | CA_COORD | #REF!
entity:HQ_7.015_CA_COORD | 7.015 | CA_COORD | #REF!
entity:HQ_7.016_CA_COORD | 7.016 | CA_COORD | #REF!
entity:HQ_7.017_CA_ENSUIT | 7.017 | CA_ENSUIT | #REF!
entity:HQ_7.018_CA_SECRETARY | 7.018 | CA_SECRETARY | #REF!
entity:HQ_7.019_BD_UNIT_SECRETARY | 7.019 | BD_UNIT_SECRETARY | #REF!
entity:HQ_7.02_BD_UNIT_EXECUTIVE | 7.02 | BD_UNIT_EXECUTIVE | #REF!
entity:HQ_7.021_BD_UNIT_EXECUTIVE | 7.021 | BD_UNIT_EXECUTIVE | #REF!
entity:HQ_7.022_BD_UNIT_EXECUTIVE | 7.022 | BD_UNIT_EXECUTIVE | #REF!
entity:HQ_7.023_BD_UNIT_EXECUTIVE | 7.023 | BD_UNIT_EXECUTIVE | #REF!
entity:HQ_7.024_BD_UNIT_EXECUTIVE | 7.024 | BD_UNIT_EXECUTIVE | #REF!
entity:HQ_7.025_BD_UNIT_EXECUTIVE | 7.025 | BD_UNIT_EXECUTIVE | #REF!
entity:HQ_7.026_BD_UNIT_EXECUTIVE | 7.026 | BD_UNIT_EXECUTIVE | #REF!
entity:HQ_7.027_BD_UNIT_EXECUTIVE | 7.027 | BD_UNIT_EXECUTIVE | #REF!
entity:HQ_7.028_BD_UNIT_EXECUTIVE | 7.028 | BD_UNIT_EXECUTIVE | #REF!
entity:HQ_7.029_MEETING_ROOM | 7.029 | MEETING_ROOM | #REF!
entity:HQ_7.03_SHELL_SPACE | 7.03 | SHELL_SPACE | #REF!
entity:HQ_7.032_SHELL_SPACE | 7.032 | SHELL_SPACE | #REF!
entity:HQ_7.101_PRINT_COPY | 7.101 | PRINT_COPY | #REF!
entity:HQ_7.102_CA_SECRETARY | 7.102 | CA_SECRETARY | #REF!
entity:HQ_7.103_CA_SECRETARY | 7.103 | CA_SECRETARY | #REF!
entity:HQ_7.104_PRINT_COPY | 7.104 | PRINT_COPY | #REF!
entity:HQ_7.105_CA_SECRETARY | 7.105 | CA_SECRETARY | #REF!
entity:HQ_7.106_LOUNGE | 7.106 | LOUNGE | #REF!
entity:HQ_7.107_PANTRY | 7.107 | PANTRY | #REF!
entity:HQ_7.108_JANITORS_CLOSET | 7.108 | JANITORS_CLOSET | #REF!
entity:HQ_7.109_ELECTRICAL_CABINET | 7.109 | ELECTRICAL_CABINET | #REF!
entity:HQ_7.11_VESTIBULE | 7.11 | VESTIBULE | #REF!
entity:HQ_7.201_CONSULTANTS_SPACE | 7.201 | CONSULTANTS_SPACE | #REF!
entity:HQ_7.202_PRESIDENT_EXECOFFICE | 7.202 | PRESIDENT_EXECOFFICE | #REF!
entity:HQ_7.203_PANTRY | 7.203 | PANTRY | #REF!
entity:HQ_7.204_PRESIDENT_EXECOFFICE | 7.204 | PRESIDENT_EXECOFFICE | #REF!
entity:HQ_7.205_PRESIDENT_EXECOFFICE | 7.205 | PRESIDENT_EXECOFFICE | #REF!
entity:HQ_7.206_PRESIDENT_EXECOFFICE | 7.206 | PRESIDENT_EXECOFFICE | #REF!
entity:HQ_7.207_PRESIDENT_EXECOFFICE | 7.207 | PRESIDENT_EXECOFFICE | #REF!
entity:HQ_7.208_PRESIDENT_SUPPORT_SECRET | 7.208 | PRESIDENT_SUPPORT_SECRET | #REF!
entity:HQ_7.209_PRESIDENT_EXECSECRET | 7.209 | PRESIDENT_EXECSECRET | #REF!
entity:HQ_7.21_PRESIDENT_EXECSECRET | 7.21 | PRESIDENT_EXECSECRET | #REF!
entity:HQ_7.211_PRESIDENT_ENSUIT | 7.211 | PRESIDENT_ENSUIT | #REF!
entity:HQ_7.212_PRESIDENT_MEETING_ROOM | 7.212 | PRESIDENT_MEETING_ROOM | #REF!
entity:HQ_7.213_VICE_CHAIRPERSON_ENSUIT | 7.213 | VICE_CHAIRPERSON_ENSUIT | #REF!
entity:HQ_7.214_VICE_CHAIRSECRETARY | 7.214 | VICE_CHAIRSECRETARY | #REF!
entity:HQ_7.215_VICE_CHAIRPERSON_MEETING_ROOM | 7.215 | VICE_CHAIRPERSON_MEETING_ROOM | #REF!
entity:HQ_7.401_FEMALE_TOILET | 7.401 | FEMALE_TOILET | #REF!
entity:HQ_7.402_MALE_TOILET | 7.402 | MALE_TOILET | #REF!
entity:HQ_7.403_MALE_TOILET | 7.403 | MALE_TOILET | #REF!
entity:HQ_7.404_FEMALE_TOILET | 7.404 | FEMALE_TOILET | #REF!
entity:HQ_7.405_MALE_TOILET | 7.405 | MALE_TOILET | #REF!
entity:HQ_7.406_FEMALE_TOILET | 7.406 | FEMALE_TOILET | #REF!
entity:HQ_7.407_TOILET | 7.407 | TOILET | #REF!
entity:HQ_7.408_TOILET | 7.408 | TOILET | #REF!
entity:HQ_7.409_TOILET | 7.409 | TOILET | #REF!
entity:HQ_7.511_VESTIBULE | 7.511 | VESTIBULE | #REF!
entity:HQ_7.512_IDF_ROOM | 7.512 | IDF_ROOM | #REF!
entity:HQ_7.531_IDF_ROOM | 7.531 | IDF_ROOM | #REF!
entity:HQ_7.532_ELECTRICAL_CLOSET | 7.532 | ELECTRICAL_CLOSET | #REF!
entity:HQ_7.533_ELECTRICAL_CLOSET_2 | 7.533 | ELECTRICAL_CLOSET_2 | #REF!
entity:HQ_7.541_VESTIBULE | 7.541 | VESTIBULE | #REF!
entity:HQ_7.601_S-TOWER_CORRIDOR | 7.601 | S-TOWER_CORRIDOR | #REF!
entity:HQ_7.602_BRIDGE | 7.602 | BRIDGE | #REF!
entity:HQ_7.603_E-TOWER_CORRIDOR | 7.603 | E-TOWER_CORRIDOR | #REF!
entity:HQ_7.P-1_P-1 | 7.P-1 | P-1 | #REF!
entity:HQ_7.P-2_P-2 | 7.P-2 | P-2 | #REF!
entity:HQ_7.P-3_P-3 | 7.P-3 | P-3 | #REF!
entity:HQ_7.P-4_P-4 | 7.P-4 | P-4 | #REF!
entity:HQ_7.P-5_P-5 | 7.P-5 | P-5 | #REF!
entity:HQ_7.P-6_P-6 | 7.P-6 | P-6 | #REF!
entity:HQ_7.S-1_S-1 | 7.S-1 | S-1 | #REF!
entity:HQ_7.ST-1_ST-1 | 7.ST-1 | ST-1 | #REF!
entity:HQ_7.ST-2_ST-2 | 7.ST-2 | ST-2 | #REF!
entity:HQ_7.ST-3_ST-3 | 7.ST-3 | ST-3 | #REF!
entity:HQ_7.ST-4_ST-4 | 7.ST-4 | ST-4 | #REF!
entity:HQ_8.001_OBSERVATION_SPACE | 8.001 | OBSERVATION_SPACE | #REF!
entity:HQ_8.002_VISITORS_CENTER_OFFICE | 8.002 | VISITORS_CENTER_OFFICE | #REF!
entity:HQ_8.101_PANTRY | 8.101 | PANTRY | #REF!
entity:HQ_8.102_MAINTENANCE_STORAGE | 8.102 | MAINTENANCE_STORAGE | #REF!
entity:HQ_8.103_ELECTRICAL_CABINET | 8.103 | ELECTRICAL_CABINET | #REF!
entity:HQ_8.511_VESTIBULE | 8.511 | VESTIBULE | #REF!
entity:HQ_8.512_IDF_ROOM | 8.512 | IDF_ROOM | #REF!
entity:HQ_8.521_VESTIBULE | 8.521 | VESTIBULE | #REF!
entity:HQ_8.531_ELECTRICAL_CLOSET_1 | 8.531 | ELECTRICAL_CLOSET_1 | #REF!
entity:HQ_8.532_ELECTRICAL_CLOSET_2 | 8.532 | ELECTRICAL_CLOSET_2 | #REF!
entity:HQ_8.541_VESTIBULE | 8.541 | VESTIBULE | #REF!
entity:HQ_8.601_BRIDGE | 8.601 | BRIDGE | #REF!
entity:HQ_8.602_VISITORS_CENTER_CORRIDOR | 8.602 | VISITORS_CENTER_CORRIDOR | #REF!
entity:HQ_8.P-1_P-1 | 8.P-1 | P-1 | #REF!
entity:HQ_8.P-2_P-2 | 8.P-2 | P-2 | #REF!
entity:HQ_8.P-3_P-3 | 8.P-3 | P-3 | #REF!
entity:HQ_8.P-4_P-4 | 8.P-4 | P-4 | #REF!
entity:HQ_8.P-5_P-5 | 8.P-5 | P-5 | #REF!
entity:HQ_8.P-6_P-6 | 8.P-6 | P-6 | #REF!
entity:HQ_8.S-1_S-1 | 8.S-1 | S-1 | #REF!
entity:HQ_8.ST-1_ST-1 | 8.ST-1 | ST-1 | #REF!
entity:HQ_8.ST-2_ST-2 | 8.ST-2 | ST-2 | #REF!
entity:HQ_8.ST-3_ST-3 | 8.ST-3 | ST-3 | #REF!
entity:HQ_8.ST-4_ST-4 | 8.ST-4 | ST-4 | #REF!
entity:HQ_9.001_LEGAL_ARCHIVE | 9.001 | LEGAL_ARCHIVE | #REF!
entity:HQ_9.002_LEGAL_CONSULE | 9.002 | LEGAL_CONSULE | #REF!
entity:HQ_9.003_LEGAL_LEGAL_CONSULE | 9.003 | LEGAL_LEGAL_CONSULE | #REF!
entity:HQ_9.004_LEGAL_LEGAL_CONSULE | 9.004 | LEGAL_LEGAL_CONSULE | #REF!
entity:HQ_9.005_LEGAL_LEGAL_CONSULE | 9.005 | LEGAL_LEGAL_CONSULE | #REF!
entity:HQ_9.006_LEGAL_LEGAL_CONSULE | 9.006 | LEGAL_LEGAL_CONSULE | #REF!
entity:HQ_9.007_LEGAL_LEGAL_CONSULE | 9.007 | LEGAL_LEGAL_CONSULE | #REF!
entity:HQ_9.008_LEGAL_LEGSUPSEC | 9.008 | LEGAL_LEGSUPSEC | #REF!
entity:HQ_9.009_LEGAL_LEGSUPSEC | 9.009 | LEGAL_LEGSUPSEC | #REF!
entity:HQ_9.01_LEGAL_LEGADVENSUIT | 9.01 | LEGAL_LEGADVENSUIT | #REF!
entity:HQ_9.011_BMO_EXECASSIST | 9.011 | BMO_EXECASSIST | #REF!
entity:HQ_9.012_BMO_EXECASSIST | 9.012 | BMO_EXECASSIST | #REF!
entity:HQ_9.013_BMO_EXECASSIST | 9.013 | BMO_EXECASSIST | #REF!
entity:HQ_9.014_BMO_EXECASSIST | 9.014 | BMO_EXECASSIST | #REF!
entity:HQ_9.015_BMO_EXECASSIST | 9.015 | BMO_EXECASSIST | #REF!
entity:HQ_9.016_BMO_EXECASSIST | 9.016 | BMO_EXECASSIST | #REF!
entity:HQ_9.017_BMO_EXECASSIST | 9.017 | BMO_EXECASSIST | #REF!
entity:HQ_9.018_BMO_EXECSECRET | 9.018 | BMO_EXECSECRET | #REF!
entity:HQ_9.019_BMO_EXECSECRET | 9.019 | BMO_EXECSECRET | #REF!
entity:HQ_9.02_BMO_EXECSECRET | 9.02 | BMO_EXECSECRET | #REF!
entity:HQ_9.021_BMO_OPERDIRENSUIT | 9.021 | BMO_OPERDIRENSUIT | #REF!
entity:HQ_9.022_BMO_EXECASSIST | 9.022 | BMO_EXECASSIST | #REF!
entity:HQ_9.023_BMO_EXECSECRET | 9.023 | BMO_EXECSECRET | #REF!
entity:HQ_9.024_BMO_EXECSECRET | 9.024 | BMO_EXECSECRET | #REF!
entity:HQ_9.025_BMO_EXECSECRET | 9.025 | BMO_EXECSECRET | #REF!
entity:HQ_9.026_BMO_SUPPSECRET | 9.026 | BMO_SUPPSECRET | #REF!
entity:HQ_9.027_BMO_SUPPSECRET | 9.027 | BMO_SUPPSECRET | #REF!
entity:HQ_9.028_BMO_SUPPSECRET | 9.028 | BMO_SUPPSECRET | #REF!
entity:HQ_9.029_BMO_SUPPSECRET | 9.029 | BMO_SUPPSECRET | #REF!
entity:HQ_9.03_BMO_SUPPSECRET | 9.03 | BMO_SUPPSECRET | #REF!
entity:HQ_9.031_BMO_PRINT_COPY | 9.031 | BMO_PRINT_COPY | #REF!
entity:HQ_9.032_BMO_STORAGE | 9.032 | BMO_STORAGE | #REF!
entity:HQ_9.033_HR_EDUADVADVISOR_ENSUIT | 9.033 | HR_EDUADVADVISOR_ENSUIT | #REF!
entity:HQ_9.034_HR_EDUADVADVISOR_ENSUIT | 9.034 | HR_EDUADVADVISOR_ENSUIT | #REF!
entity:HQ_9.035_HR_EDUADVADVISOR_ENSUIT | 9.035 | HR_EDUADVADVISOR_ENSUIT | #REF!
entity:HQ_9.036_BOD_EXECUTIVE | 9.036 | BOD_EXECUTIVE | #REF!
entity:HQ_9.037_BOD_SECRETARY | 9.037 | BOD_SECRETARY | #REF!
entity:HQ_9.038_BOD_EXECUTIVE | 9.038 | BOD_EXECUTIVE | #REF!
entity:HQ_9.039_MEETING_ROOM | 9.039 | MEETING_ROOM | #REF!
entity:HQ_9.04_BMO_SAFE_ROOM | 9.04 | BMO_SAFE_ROOM | #REF!
entity:HQ_9.041_BMO_ARCHIVE_ROOM | 9.041 | BMO_ARCHIVE_ROOM | #REF!
entity:HQ_9.101_VISITORS_CENTER | 9.101 | VISITORS_CENTER | #REF!
entity:HQ_9.102_BMO_STORAGE_TEA_GIRLS_ROOM | 9.102 | BMO_STORAGE_TEA_GIRLS_ROOM | #REF!
entity:HQ_9.103_BMO_PANTRY | 9.103 | BMO_PANTRY | #REF!
entity:HQ_9.104_BMO_WAITING_AREA | 9.104 | BMO_WAITING_AREA | #REF!
entity:HQ_9.105_LOUNGE | 9.105 | LOUNGE | #REF!
entity:HQ_9.106_STORAGE | 9.106 | STORAGE | #REF!
entity:HQ_9.107_JANITORS_CLOSET | 9.107 | JANITORS_CLOSET | #REF!
entity:HQ_9.108_SUPPORT_SPACE_PREPKITCHEN | 9.108 | SUPPORT_SPACE_PREPKITCHEN | #REF!
entity:HQ_9.109_AHU_ROOM | 9.109 | AHU_ROOM | #REF!
entity:HQ_9.11_SHEIKA_WING_DINING_AREA | 9.11 | SHEIKA_WING_DINING_AREA | #REF!
entity:HQ_9.111_PLANT_ROOM | 9.111 | PLANT_ROOM | #REF!
entity:HQ_9.112_STORAGE | 9.112 | STORAGE | #REF!
entity:HQ_9.114_SUPPORT_SPACE_WASTE_REFUGE | 9.114 | SUPPORT_SPACE_WASTE_REFUGE | #REF!
entity:HQ_9.115_ELECTRICAL_CABINET | 9.115 | ELECTRICAL_CABINET | #REF!
entity:HQ_9.401_MALE_TOILET | 9.401 | MALE_TOILET | #REF!
entity:HQ_9.402_FEMALE_TOILET | 9.402 | FEMALE_TOILET | #REF!
entity:HQ_9.403_MALE_TOILET | 9.403 | MALE_TOILET | #REF!
entity:HQ_9.404_FEMALE_TOILET | 9.404 | FEMALE_TOILET | #REF!
entity:HQ_9.405_TOILET | 9.405 | TOILET | #REF!
entity:HQ_9.406_TOILET | 9.406 | TOILET | #REF!
entity:HQ_9.407_TOILET | 9.407 | TOILET | #REF!
entity:HQ_9.408_TOILET | 9.408 | TOILET | #REF!
entity:HQ_9.409_TOILET | 9.409 | TOILET | #REF!
entity:HQ_9.512_IDF_ROOM | 9.512 | IDF_ROOM | #REF!
entity:HQ_9.521_VESTIBULE | 9.521 | VESTIBULE | #REF!
entity:HQ_9.531_IDF_ROOM | 9.531 | IDF_ROOM | #REF!
entity:HQ_9.532_ELECTRICAL_CLOSET | 9.532 | ELECTRICAL_CLOSET | #REF!
entity:HQ_9.533_ELECTRICAL_CLOSET_2 | 9.533 | ELECTRICAL_CLOSET_2 | #REF!
entity:HQ_9.541_VESTIBULE | 9.541 | VESTIBULE | #REF!
entity:HQ_9.P-1_P-1 | 9.P-1 | P-1 | #REF!
entity:HQ_9.P-2_P-2 | 9.P-2 | P-2 | #REF!
entity:HQ_9.P-3_P-3 | 9.P-3 | P-3 | #REF!
entity:HQ_9.P-4_P-4 | 9.P-4 | P-4 | #REF!
entity:HQ_9.P-5_P-5 | 9.P-5 | P-5 | #REF!
entity:HQ_9.P-6_P-6 | 9.P-6 | P-6 | #REF!
entity:HQ_9.S-1_S-1 | 9.S-1 | S-1 | #REF!
entity:HQ_9.ST-01_ST-01 | 9.ST-01 | ST-01 | #REF!
entity:HQ_9.ST-04_ST-04 | 9.ST-04 | ST-04 | #REF!
entity:HQ_9.ST-2_ST-2 | 9.ST-2 | ST-2 | #REF!
entity:HQ_9.ST-3_ST-3 | 9.ST-3 | ST-3 | #REF!
entity:HQ_9.542_SUPPLY_AND_RETURN_AIR | 9.542 | SUPPLY_AND_RETURN_AIR | #REF!
entity:HQ_9.543_RETURN-AIR | 9.543 | RETURN-AIR | #REF!
entity:HQ_9.544_SUPPLY-AIR | 9.544 | SUPPLY-AIR | #REF!
entity:HQ_10.001_SHEIKHA_WING_STORAGE | 10.001 | SHEIKHA_WING_STORAGE | #REF!
entity:HQ_10.003_BOARD_ROOM_WAITING_AREA | 10.003 | BOARD_ROOM_WAITING_AREA | #REF!
entity:HQ_10.004_EXECDIRARCHCOORD | 10.004 | EXECDIRARCHCOORD | #REF!
entity:HQ_10.005_SHEIKHA_WING_ARCHIVE | 10.005 | SHEIKHA_WING_ARCHIVE | #REF!
entity:HQ_10.006_EXECDIRARCHCOORD | 10.006 | EXECDIRARCHCOORD | #REF!
entity:HQ_10.007_EXECDIR_PROTASSIST | 10.007 | EXECDIR_PROTASSIST | #REF!
entity:HQ_10.008_PROTOCOL_DIR_SCHED_OFFICER | 10.008 | PROTOCOL_DIR_SCHED_OFFICER | #REF!
entity:HQ_10.009_PROTOCOL_DIR_CEREMOFF | 10.009 | PROTOCOL_DIR_CEREMOFF | #REF!
entity:HQ_10.01_PROTOCOL_DIR_CEREMOFF | 10.01 | PROTOCOL_DIR_CEREMOFF | #REF!
entity:HQ_10.011_PROTOCOL_DIR_CEREMOFF | 10.011 | PROTOCOL_DIR_CEREMOFF | #REF!
entity:HQ_10.012_PROTOCOL_DIR_TR_&_VIS_OFF | 10.012 | PROTOCOL_DIR_TR_&_VIS_OFF | #REF!
entity:HQ_10.013_PROTOCOL_DIR_TR_&_VIS_OFF | 10.013 | PROTOCOL_DIR_TR_&_VIS_OFF | #REF!
entity:HQ_10.014_PRINT_COPY | 10.014 | PRINT_COPY | #REF!
entity:HQ_10.015_PROTOCOL_DIRSCHED_OFFICER | 10.015 | PROTOCOL_DIRSCHED_OFFICER | #REF!
entity:HQ_10.016_PLANNING_DIRPLANNING_ANALYST | 10.016 | PLANNING_DIRPLANNING_ANALYST | #REF!
entity:HQ_10.017_PLANNING_DIRSTRATPLANNER | 10.017 | PLANNING_DIRSTRATPLANNER | #REF!
entity:HQ_10.018_PLANNING_DIR_EXTCOORD | 10.018 | PLANNING_DIR_EXTCOORD | #REF!
entity:HQ_10.019_POLICY_DIRSENPOLANALYST | 10.019 | POLICY_DIRSENPOLANALYST | #REF!
entity:HQ_10.02_POLICY_DIR_SENRESEARCH_ANALYST | 10.02 | POLICY_DIR_SENRESEARCH_ANALYST | #REF!
entity:HQ_10.021_POLICY_DIRRESANALYST | 10.021 | POLICY_DIRRESANALYST | #REF!
entity:HQ_10.022_POLICY_DIRRESANALYST | 10.022 | POLICY_DIRRESANALYST | #REF!
entity:HQ_10.023_SHSERVDIR_HR_OFFICER | 10.023 | SHSERVDIR_HR_OFFICER | #REF!
entity:HQ_10.024_SHSERVDIRHR_ASSISTANT | 10.024 | SHSERVDIRHR_ASSISTANT | #REF!
entity:HQ_10.025_SHSERVDIRPROCURREPRESENT | 10.025 | SHSERVDIRPROCURREPRESENT | #REF!
entity:HQ_10.026_SHSERVDIRSERVICE_COORD | 10.026 | SHSERVDIRSERVICE_COORD | #REF!
entity:HQ_10.027_SHSERVDIRGENSERVSUPERV | 10.027 | SHSERVDIRGENSERVSUPERV | #REF!
entity:HQ_10.028_SHSERVDIRFINANCCONTROL | 10.028 | SHSERVDIRFINANCCONTROL | #REF!
entity:HQ_10.029_SHSERVDIRTR&_GUSERV | 10.029 | SHSERVDIRTR&_GUSERV | #REF!
entity:HQ_10.03_PANTRY | 10.03 | PANTRY | #REF!
entity:HQ_10.031_COMMUNICDIRCOMMDESIGNER | 10.031 | COMMUNICDIRCOMMDESIGNER | #REF!
entity:HQ_10.032_COMMUNICDIRSPEECH_EDITOR | 10.032 | COMMUNICDIRSPEECH_EDITOR | #REF!
entity:HQ_10.033_COMMUNICDIR_TRANSLATOR | 10.033 | COMMUNICDIR_TRANSLATOR | #REF!
entity:HQ_10.034_COMMUNICDIRPUBCOMMCOORD | 10.034 | COMMUNICDIRPUBCOMMCOORD | #REF!
entity:HQ_10.035_SHSERVDIR_IT_SUPPORT_OFFICER | 10.035 | SHSERVDIR_IT_SUPPORT_OFFICER | #REF!
entity:HQ_10.036_SHSERVDIR_ACCOUNT | 10.036 | SHSERVDIR_ACCOUNT | #REF!
entity:HQ_10.037_SHSERVDIRSENACCOUNTANT | 10.037 | SHSERVDIRSENACCOUNTANT | #REF!
entity:HQ_10.038_PRINT_COPY | 10.038 | PRINT_COPY | #REF!
entity:HQ_10.101_CONSULTANTS_SPACE | 10.101 | CONSULTANTS_SPACE | #REF!
entity:HQ_10.102_SHEIKHA_WING_MULTIPURPOSE_ROOM | 10.102 | SHEIKHA_WING_MULTIPURPOSE_ROOM | #REF!
entity:HQ_10.103_HH_WING_PANTRY | 10.103 | HH_WING_PANTRY | #REF!
entity:HQ_10.104_HH_WING_STORAGE | 10.104 | HH_WING_STORAGE | #REF!
entity:HQ_10.105_HH_WING_STORAGE | 10.105 | HH_WING_STORAGE | #REF!
entity:HQ_10.106_LOUNGE | 10.106 | LOUNGE | #REF!
entity:HQ_10.107_STORAGE | 10.107 | STORAGE | #REF!
entity:HQ_10.108_JANITORS_CLOSET | 10.108 | JANITORS_CLOSET | #REF!
entity:HQ_10.109_BOARD_PREPROOM | 10.109 | BOARD_PREPROOM | #REF!
entity:HQ_10.11_SHEIKHA_WING_BOARD_ROOM | 10.11 | SHEIKHA_WING_BOARD_ROOM | #REF!
entity:HQ_10.111_AV_ROOM | 10.111 | AV_ROOM | #REF!
entity:HQ_10.112_TRANSLATOR_ROOM | 10.112 | TRANSLATOR_ROOM | #REF!
entity:HQ_10.401_FEMALE_TOILET | 10.401 | FEMALE_TOILET | #REF!
entity:HQ_10.402_MALE_TOILET | 10.402 | MALE_TOILET | #REF!
entity:HQ_10.403_MALE_TOILET | 10.403 | MALE_TOILET | #REF!
entity:HQ_10.404_FEMALE_TOILET | 10.404 | FEMALE_TOILET | #REF!
entity:HQ_10.405_MALE_TOILET | 10.405 | MALE_TOILET | #REF!
entity:HQ_10.406_FEMALE_TOILET | 10.406 | FEMALE_TOILET | #REF!
entity:HQ_10.511_VESTIBULE | 10.511 | VESTIBULE | #REF!
entity:HQ_10.512_IDF_ROOM | 10.512 | IDF_ROOM | #REF!
entity:HQ_10.521_VESTIBULE | 10.521 | VESTIBULE | #REF!
entity:HQ_10.531_IDF_ROOM | 10.531 | IDF_ROOM | #REF!
entity:HQ_10.532_ELECTRICAL_CLOSET_1 | 10.532 | ELECTRICAL_CLOSET_1 | #REF!
entity:HQ_10.533_ELECTRICAL_CLOSET_2 | 10.533 | ELECTRICAL_CLOSET_2 | #REF!
entity:HQ_10.541_VESTIBULE | 10.541 | VESTIBULE | #REF!
entity:HQ_10.601_HH-WING_CORRIDOR | 10.601 | HH-WING_CORRIDOR | #REF!
entity:HQ_10.701_TERRACE | 10.701 | TERRACE | #REF!
entity:HQ_10.P-1_P-1 | 10.P-1 | P-1 | #REF!
entity:HQ_10.P-2_P-2 | 10.P-2 | P-2 | #REF!
entity:HQ_10.P-3_P-3 | 10.P-3 | P-3 | #REF!
entity:HQ_10.P-4_P-4 | 10.P-4 | P-4 | #REF!
entity:HQ_10.P-5_P-5 | 10.P-5 | P-5 | #REF!
entity:HQ_10.P-6_P-6 | 10.P-6 | P-6 | #REF!
entity:HQ_10.S-1_S-1 | 10.S-1 | S-1 | #REF!
entity:HQ_10.ST-1_ST-1 | 10.ST-1 | ST-1 | #REF!
entity:HQ_10.ST-2_ST-2 | 10.ST-2 | ST-2 | #REF!
entity:HQ_10.ST-3_ST-3 | 10.ST-3 | ST-3 | #REF!
entity:HQ_10.ST-4_ST-4 | 10.ST-4 | ST-4 | #REF!
entity:HQ_11.001_COMMUNICDIR_COMMUNICATION_DIRECTOR | 11.001 | COMMUNICDIR_COMMUNICATION_DIRECTOR | #REF!
entity:HQ_11.002_COMMUNICDIRMEDRELOFFICER | 11.002 | COMMUNICDIRMEDRELOFFICER | #REF!
entity:HQ_11.003_SHSERVDIR_DIRSHARED_SERVICES | 11.003 | SHSERVDIR_DIRSHARED_SERVICES | #REF!
entity:HQ_11.004_EXECDIRECTOR_ADMASSIST | 11.004 | EXECDIRECTOR_ADMASSIST | #REF!
entity:HQ_11.005_PROTOCOL_DIRPROTOCOL_DIRECTOR | 11.005 | PROTOCOL_DIRPROTOCOL_DIRECTOR | #REF!
entity:HQ_11.006_PROTOCOL_DIRGIFTS_DIRECTOR | 11.006 | PROTOCOL_DIRGIFTS_DIRECTOR | #REF!
entity:HQ_11.007_EXECDIRCONSULTANT | 11.007 | EXECDIRCONSULTANT | #REF!
entity:HQ_11.008_EXECDIRCONSULTANT | 11.008 | EXECDIRCONSULTANT | #REF!
entity:HQ_11.009_SECRETARY | 11.009 | SECRETARY | #REF!
entity:HQ_11.01_POLICY_DIRDIROF_POL&_RES | 11.01 | POLICY_DIRDIROF_POL&_RES | #REF!
entity:HQ_11.011_SECRETARY | 11.011 | SECRETARY | #REF!
entity:HQ_11.012_PLANNING_DIRDIRPLANNING | 11.012 | PLANNING_DIRDIRPLANNING | #REF!
entity:HQ_11.013_EXECDIRCORRF-UP | 11.013 | EXECDIRCORRF-UP | #REF!
entity:HQ_11.014_EXECDIRCORRMANAGER | 11.014 | EXECDIRCORRMANAGER | #REF!
entity:HQ_11.015_EXECDIRCORRF-UP | 11.015 | EXECDIRCORRF-UP | #REF!
entity:HQ_11.016_EXECDIRLEGAL_ASSIST | 11.016 | EXECDIRLEGAL_ASSIST | #REF!
entity:HQ_11.017_EXECDIRLEGAL_ADVISOR | 11.017 | EXECDIRLEGAL_ADVISOR | #REF!
entity:HQ_11.018_EXECDIREXECASSIST | 11.018 | EXECDIREXECASSIST | #REF!
entity:HQ_11.019_EXECDIR_DEPEXECDIRECTOR | 11.019 | EXECDIR_DEPEXECDIRECTOR | #REF!
entity:HQ_11.02_EXECDIREXECASSIST | 11.02 | EXECDIREXECASSIST | #REF!
entity:HQ_11.021_EXECDIREXECDIRECTOR | 11.021 | EXECDIREXECDIRECTOR | #REF!
entity:HQ_11.022_SHEIKHA_WING_WAITING_ROOM | 11.022 | SHEIKHA_WING_WAITING_ROOM | #REF!
entity:HQ_11.023_SHEIKHA_WING_SECURITY_ROOM | 11.023 | SHEIKHA_WING_SECURITY_ROOM | #REF!
entity:HQ_11.101_AV_ROOM | 11.101 | AV_ROOM | #REF!
entity:HQ_11.102_HH_WING_BUSINESS_LOUNGE | 11.102 | HH_WING_BUSINESS_LOUNGE | #REF!
entity:HQ_11.104_PANTRY | 11.104 | PANTRY | #REF!
entity:HQ_11.105_JANITORS_CLOSET | 11.105 | JANITORS_CLOSET | #REF!
entity:HQ_11.106_ELECTRICAL_ROOM | 11.106 | ELECTRICAL_ROOM | #REF!
entity:HQ_11.107_AV_IT | 11.107 | AV_IT | #REF!
entity:HQ_11.108_PRINT_COPY | 11.108 | PRINT_COPY | #REF!
entity:HQ_11.11_ELECTRICAL_CABINET | 11.11 | ELECTRICAL_CABINET | #REF!
entity:HQ_11.201_SHEIKHA_WING_LOBBY | 11.201 | SHEIKHA_WING_LOBBY | #REF!
entity:HQ_11.202_SHEIKHA_WING_SHEIKHA_ENSUIT | 11.202 | SHEIKHA_WING_SHEIKHA_ENSUIT | #REF!
entity:HQ_11.203_SHEIKHA_WING_RELAX_AREA | 11.203 | SHEIKHA_WING_RELAX_AREA | #REF!
entity:HQ_11.204_SHEIKHA_WING_MEETING_ROOM | 11.204 | SHEIKHA_WING_MEETING_ROOM | #REF!
entity:HQ_11.401_MALE_TOILET | 11.401 | MALE_TOILET | #REF!
entity:HQ_11.402_FEMALE_TOILET | 11.402 | FEMALE_TOILET | #REF!
entity:HQ_11.403_SHEIKHA_WING_BATHROOM | 11.403 | SHEIKHA_WING_BATHROOM | #REF!
entity:HQ_11.404_TOILET | 11.404 | TOILET | #REF!
entity:HQ_11.405_TOILET | 11.405 | TOILET | #REF!
entity:HQ_11.406_TOILET | 11.406 | TOILET | #REF!
entity:HQ_11.407_TOILET | 11.407 | TOILET | #REF!
entity:HQ_11.408_TOILET | 11.408 | TOILET | #REF!
entity:HQ_11.409_TOILET | 11.409 | TOILET | #REF!
entity:HQ_11.41_TOILET | 11.41 | TOILET | #REF!
entity:HQ_11.411_TOILET | 11.411 | TOILET | #REF!
entity:HQ_11.412_TOILET | 11.412 | TOILET | #REF!
entity:HQ_11.511_VESTIBULE | 11.511 | VESTIBULE | #REF!
entity:HQ_11.512_IDF_ROOM | 11.512 | IDF_ROOM | #REF!
entity:HQ_11.521_VESTIBULE | 11.521 | VESTIBULE | #REF!
entity:HQ_11.531_IDF_ROOM | 11.531 | IDF_ROOM | #REF!
entity:HQ_11.532_ELECTRICAL_CLOSET | 11.532 | ELECTRICAL_CLOSET | #REF!
entity:HQ_11.533_ELECTRICAL_CLOSET_2 | 11.533 | ELECTRICAL_CLOSET_2 | #REF!
entity:HQ_11.541_VESTIBULE | 11.541 | VESTIBULE | #REF!
entity:HQ_11.701_SHEIKHA_WING_TERRACE | 11.701 | SHEIKHA_WING_TERRACE | #REF!
entity:HQ_11.702_TERRACE | 11.702 | TERRACE | #REF!
entity:HQ_11.709_SHEIKHA_WING_CONFERENCE_ROOM | 11.709 | SHEIKHA_WING_CONFERENCE_ROOM | #REF!
entity:HQ_11.P-1_P-1 | 11.P-1 | P-1 | #REF!
entity:HQ_11.P-2_P-2 | 11.P-2 | P-2 | #REF!
entity:HQ_11.P-3_P-3 | 11.P-3 | P-3 | #REF!
entity:HQ_11.P-4_P-4 | 11.P-4 | P-4 | #REF!
entity:HQ_11.P-5_P-5 | 11.P-5 | P-5 | #REF!
entity:HQ_11.P-6_P-6 | 11.P-6 | P-6 | #REF!
entity:HQ_11.ST-2_ST-2 | 11.ST-2 | ST-2 | #REF!
entity:HQ_11.ST-3_ST-3 | 11.ST-3 | ST-3 | #REF!
entity:HQ_11.ST-4_ST-4 | 11.ST-4 | ST-4 | #REF!
entity:HQ_RF.001_ROOF | RF.001 | ROOF | #REF!
entity:HQ_2.701_TERRACE | 2.701 | TERRACE | #REF!
entity:HQ_5.214_GSM_ROOM | 5.214 | GSM_ROOM | #REF!
entity:HQ_4.11_PRINT_COPY | 4.11 | PRINT_COPY | #REF!
entity:HQ_12.002_MCC_CLOSET | 12.002 | MCC_CLOSET | #REF!
entity:HQ_12.003_MCC_CLOSET | 12.003 | MCC_CLOSET | #REF!
entity:HQ_12.004_MCC_CLOSET | 12.004 | MCC_CLOSET | #REF!
entity:HQ_B1.004_STAFF_ENTRANCE | B1.004 | STAFF_ENTRANCE | #REF!
entity:HQ_G.400_CORRIDOR | G.400 | CORRIDOR | #REF!
entity:HQ_G.001_PR_&_MARKET_STAFF | G.001 | PR_&_MARKET_STAFF | #REF!
entity:HQ_G.030_STAFF | G.030 | STAFF | #REF!
entity:HQ_G.602_CORRIDOR_(SOUTH_EAST) | G.602 | CORRIDOR_(SOUTH_EAST) | #REF!
entity:HQ_G.603_CORRIDOR_(SOUTH_EAST) | G.603 | CORRIDOR_(SOUTH_EAST) | #REF!
entity:HQ_1.029_FINANCE_MANAGER | 1.029 | FINANCE_MANAGER | #REF!
entity:HQ_1.401_GROUND_FLOOR_VIP_ENTRANCE | 1.401 | GROUND_FLOOR_VIP_ENTRANCE | #REF!
entity:HQ_2.110A_OFFICE_SPACE | 2.110A | OFFICE_SPACE | #REF!
entity:HQ_2.101A_OFFICE_SPACE | 2.101A | OFFICE_SPACE | #REF!
entity:HQ_3.105B_OFFICE_SPACE | 3.105B | OFFICE_SPACE | #REF!
entity:HQ_3.36_ABLUTION_ROOM | 3.36 | ABLUTION_ROOM | #REF!
entity:HQ_3.105A_FEMALE_PRAYER_ROOM | 3.105A | FEMALE_PRAYER_ROOM | #REF!
entity:HQ_3.202A_OFFICE_SPACE | 3.202A | OFFICE_SPACE | #REF!
entity:HQ_3.202B_OFFICE_SPACE | 3.202B | OFFICE_SPACE | #REF!
entity:HQ_4.004_STR_PL_DIR_ENSUIT | 4.004 | STR_PL_DIR_ENSUIT | #REF!
entity:HQ_4.015C_OFFICE_SPACE | 4.015C | OFFICE_SPACE | #REF!
entity:HQ_4.015A_OFFICE_SPACE | 4.015A | OFFICE_SPACE | #REF!
entity:HQ_4.003_STR_PL_DIR_EXEC_SECRE | 4.003 | STR_PL_DIR_EXEC_SECRE | #REF!
entity:HQ_4.001B_OFFICE_SPACE | 4.001B | OFFICE_SPACE | #REF!
entity:HQ_4.001D_OFFICE_SPACE | 4.001D | OFFICE_SPACE | #REF!
entity:HQ_4.001F_OFFICE_SPACE | 4.001F | OFFICE_SPACE | #REF!
entity:HQ_4.001G_OFFICE_SPACE | 4.001G | OFFICE_SPACE | #REF!
entity:HQ_4.103_STORAGE_SPACE | 4.103 | STORAGE_SPACE | #REF!
entity:HQ_5.110_VP_EDU_OFFICERS | 5.110 | VP_EDU_OFFICERS | #REF!
entity:HQ_5.350_CORRIDOR | 5.350 | CORRIDOR | #REF!
entity:HQ_7.031A_OFFICE_SPACE | 7.031A | OFFICE_SPACE | #REF!
entity:HQ_7.301_MEETING_ROOM | 7.301 | MEETING_ROOM | #REF!
entity:HQ_9.601_HH-WING_CORRIDOR | 9.601 | HH-WING_CORRIDOR | #REF!
entity:HQ_10.002E_OFFICE_SPACE | 10.002E | OFFICE_SPACE | #REF!
entity:HQ_10.002D_OFFICE_SPACE | 10.002D | OFFICE_SPACE | #REF!
entity:HQ_10.002C_OFFICE_SPACE | 10.002C | OFFICE_SPACE | #REF!
entity:HQ_10.002A_OFFICE_SPACE | 10.002A | OFFICE_SPACE | #REF!
entity:HQ_11.103_SHEIKHA_WING_BUSINESS_LOUNGE | 11.103 | SHEIKHA_WING_BUSINESS_LOUNGE | #REF!
entity:HQ_8.400_VISITORS_CENTER | 8.400 | VISITORS_CENTER | #REF!
entity:HQ_B1.109_ROOM | B1.109 | ROOM | #REF!
entity:HQ_4.015B_OFFICE_SPACE | 4.015B | OFFICE_SPACE | #REF!
entity:HQ_4.001A_OFFICE_SPACE | 4.001A | OFFICE_SPACE | #REF!
entity:HQ_4.001E_OFFICE_SPACE | 4.001E | OFFICE_SPACE | #REF!
entity:HQ_4.001C_OFFICE_SPACE | 4.001C | OFFICE_SPACE | #REF!
entity:HQ_4.001H_OFFICE_SPACE | 4.001H | OFFICE_SPACE | #REF!
entity:HQ_10.002B_OFFICE_SPACE | 10.002B | OFFICE_SPACE | #REF!
entity:HQ_11.601_SHEIKHA_WING_CORRIDOR | 11.601 | SHEIKHA_WING_CORRIDOR | #REF!
entity:HQ_12.201_SHEIKHA_WING_SHEIKHA_ENSUIT | 12.201 | SHEIKHA_WING_SHEIKHA_ENSUIT | #REF!
entity:HQ_12.202_SHEIKHA_WING_SHEIKHA_ENSUIT | 12.202 | SHEIKHA_WING_SHEIKHA_ENSUIT | #REF!
entity:HQ_12.203_SHEIKHA_WING_RELAX_AREA | 12.203 | SHEIKHA_WING_RELAX_AREA | #REF!
entity:HQ_12.204_SHEIKHA_WING_RELAX_AREA | 12.204 | SHEIKHA_WING_RELAX_AREA | #REF!
entity:HQ_12.001_COMMUNIC_DIR_COMMUNICATION_DIRECTOR | 12.001 | COMMUNIC_DIR_COMMUNICATION_DIRECTOR | #REF!
entity:HQ_12.405_TOILET | 12.405 | TOILET | #REF!
entity:HQ_RF.002_ROOF_PLANT_WALKWAY | RF.002 | ROOF_PLANT_WALKWAY | #REF!

## QNL Room Names with Equip.
Room Entity Name | Room Number | Room Name
entity:QNL_B_228_M1_HVAC_SHAFT | B_228 | M1_HVAC_SHAFT | No Equipment in entity
entity:QNL_B_229_E1_ELEC_SHAFT | B_229 | E1_ELEC_SHAFT | No Equipment in entity
entity:QNL_B_230_REFR_STORE | B_230 | REFR_STORE | No Equipment in entity
entity:QNL_B_231_DISH_WASING | B_231 | DISH_WASING | No Equipment in entity
entity:QNL_B_232_DRY_STORE | B_232 | DRY_STORE | No Equipment in entity
entity:QNL_B_233_WC5_RISER | B_233 | WC5_RISER | No Equipment in entity
entity:QNL_B_234_E3_ELEC_SHAFT | B_234 | E3_ELEC_SHAFT | No Equipment in entity
entity:QNL_B_235_M2_HVAC_SHAFT_ABOVE | B_235 | M2_HVAC_SHAFT_ABOVE | No Equipment in entity
entity:QNL_B_236_WC1_RISER | B_236 | WC1_RISER | No Equipment in entity
entity:QNL_B_237_CORRIDOR | B_237 | CORRIDOR | No Equipment in entity
entity:QNL_B_238_M3_HVAC_SHAFT | B_238 | M3_HVAC_SHAFT | No Equipment in entity
entity:QNL_B_001_TECH_SERVICES_AND_COLLECTIONS_OFFICE | B_001 | TECH_SERVICES_AND_COLLECTIONS_OFFICE | VAV_B_S11_003 | VAV_B_S11_004 | VAV_B_S11_005 | VAV_B_S11_006 | VAV_B_S11_007 | VAV_B_S11_008 | VAV_B_S11_009 | VAV_B_S11_010 | VAV_B_S11_013 | VAV_B_S11_014 | VAV_B_S11_015 | VAV_B_S11_016 | VAV_B_S11_017 | VAV_B_S11_018 | VAV_B_S11_019 | VAV_B_S11_020
entity:QNL_B_002_KITCHEN | B_002 | KITCHEN | VAV_B_S11_024
entity:QNL_B_003_FINANCE_COORDINATOR_&_BUSINESS_SUPPORT_OFCR | B_003 | FINANCE_COORDINATOR_&_BUSINESS_SUPPORT_OFCR | VAV_B_S11_026 | VAV_B_S11_027
entity:QNL_B_004_ANALOG_RESOURCES | B_004 | ANALOG_RESOURCES | VAV_B_S11_028
entity:QNL_B_005_DIGITAL_RESOURCES | B_005 | DIGITAL_RESOURCES | VAV_B_S11_029
entity:QNL_B_006_BUDGET_&_PAYMENT_1 | B_006 | BUDGET_&_PAYMENT_1 | VAV_B_S11_030
entity:QNL_B_007_BUDGET_&_PAYMENT_2 | B_007 | BUDGET_&_PAYMENT_2 | VAV_B_S11_031
entity:QNL_B_008_RECEIVING_AREA | B_008 | RECEIVING_AREA | VAV_B_S11_043 | VAV_B_S11_044 | VAV_B_S11_045 | VAV_B_S11_046
entity:QNL_B_009_RECEPTION_&_LOUNGE | B_009 | RECEPTION_&_LOUNGE | VAV_B_S11_021 | VAV_B_S11_022 | VAV_B_S11_023
entity:QNL_B_010_PATIO_GARDEN | B_010 | PATIO_GARDEN | No Equipment in entity
entity:QNL_B_020_ENGINEERING | B_020 | ENGINEERING | VAV_B_S11_034
entity:QNL_B_021_ARABIC_STUDIES | B_021 | ARABIC_STUDIES | VAV_B_S11_035
entity:QNL_B_022_LICENSING_EXPERT | B_022 | LICENSING_EXPERT | VAV_B_S11_036
entity:QNL_B_023_ARTS_&_HUMANITIES | B_023 | ARTS_&_HUMANITIES | VAV_B_S11_037
entity:QNL_B_024_AD_COLLECTIONS | B_024 | AD_COLLECTIONS | VAV_B_S11_032 | VAV_B_S11_033
entity:QNL_B_025_SOCIAL_SCIENCES | B_025 | SOCIAL_SCIENCES | VAV_B_S11_040
entity:QNL_B_026_BUSINESS_&_COMPUTING | B_026 | BUSINESS_&_COMPUTING | VAV_B_S11_039
entity:QNL_B_027_PROCUREMENT_SPC_PROCUREMENT_OFCR | B_027 | PROCUREMENT_SPC_PROCUREMENT_OFCR | VAV_B_S11_038
entity:QNL_B_028_STORAGE | B_028 | STORAGE | VAV_B_S11_025
entity:QNL_B_029_LITERATURE_&_ANGUAGE | B_029 | LITERATURE_&_ANGUAGE | VAV_B_S11_041
entity:QNL_B_030_SNR_P_COORDINATOR_&_P_COORDINATOR | B_030 | SNR_P_COORDINATOR_&_P_COORDINATOR | VAV_B_S11_042
entity:QNL_B_031_JANITORS_ROOM | B_031 | JANITORS_ROOM | No Equipment in entity
entity:QNL_B_032_REST_ROOM_MEN | B_032 | REST_ROOM_MEN | No Equipment in entity
entity:QNL_B_034_MEETING_ROOM | B_034 | MEETING_ROOM | VAV_B_S13_001 | VAV_B_S13_002
entity:QNL_B036_REST_REST_ROOM_WOMEN | B036_REST | REST_ROOM_WOMEN | No Equipment in entity
entity:QNL_B036_COR_CORRIDOR_4A | B036_COR | CORRIDOR_4A | No Equipment in entity
entity:QNL_B_040_OFFICE | B_040 | OFFICE | VAV_B_S14_001 | CAV_B_S14_001
entity:QNL_B_041_DIGITIZATION_ROOM | B_041 | DIGITIZATION_ROOM | VAV_B_S14_004 | VAV_B_S14_005 | VAV_B_S14_006 | VAV_B_S14_008 | VAV_B_S14_010 | VAV_B_S14_011 | VAV_B_S14_012 | VAV_B_S14_015 | VAV_B_S14_016
entity:QNL_B_042_RECEPTION_&_LOUNGE | B_042 | RECEPTION_&_LOUNGE | No Equipment in entity
entity:QNL_B_043_BINDING_&_PRESERVATION_SPACE | B_043 | BINDING_&_PRESERVATION_SPACE | VAV_B_S14_042 | VAV_B_S14_043 | VAV_B_S14_044 | VAV_B_S14_045 | VAV_B_S14_046 | VAV_B_S14_048 | VAV_B_S14_049 | VAV_B_S14_050 | VAV_B_S14_051
entity:QNL_B044_BOH_B_O_H_KITCHEN | B044_BOH | B_O_H_KITCHEN | No Equipment in entity
entity:QNL_B044_FIN_FINE_BINDING | B044_FIN | FINE_BINDING | No Equipment in entity
entity:QNL_B046_RES_REST_ROOM_MEN | B046_RES | REST_ROOM_MEN | No Equipment in entity
entity:QNL_B046_ITT_ITTIGATION_CONTROL_ROOM | B046_ITT | ITTIGATION_CONTROL_ROOM | DX_B11
entity:QNL_B_047_REST_ROOM_WOMEN | B_047 | REST_ROOM_WOMEN | No Equipment in entity
entity:QNL_B_048_QTEL_ROOM | B_048 | QTEL_ROOM | CCU_B01 | CCU_B02
entity:QNL_B_049_MEP_KITCHEN | B_049 | MEP_KITCHEN | KEF_B019
entity:QNL_B-04B_ST-04B | B-04B | ST-04B | No Equipment in entity
entity:QNL_B_050_TELECOM_ROOM | B_050 | TELECOM_ROOM | CCU_B03 | CCU_B04
entity:QNL_B_051_STORAGE | B_051 | STORAGE | No Equipment in entity
entity:QNL_B_053_CORRIDORS | B_053 | CORRIDORS | No Equipment in entity
entity:QNL_B_054_PATIO_GARDEN | B_054 | PATIO_GARDEN | No Equipment in entity
entity:QNL_B057_DIG_OFFICE_DIG_INIT | B057_DIG | OFFICE_DIG_INIT | No Equipment in entity
entity:QNL_B057_AD_OFFICE_AD_FOR_LIT | B057_AD | OFFICE_AD_FOR_LIT | No Equipment in entity
entity:QNL_B_058_SHELL_SPACE | B_058 | SHELL_SPACE | VAV_B_S14_007 | VAV_B_S14_013
entity:QNL_B_060_MAINTENANCE | B_060 | MAINTENANCE | No Equipment in entity
entity:QNL_B_062_IDF_CORRIDOR | B_062 | IDF_CORRIDOR | FCU_B_003
entity:QNL_B_063_PLANT_ROOM_01 | B_063 | PLANT_ROOM_01 | AHUB002 | AHUB011 | AHUB012 | FCU_B_011 | FCU_B_012 | CAV_B_S12_001 | CAV_B_S12_002 | CAV_B_S12_003 | CAV_B_S15_001 | CAV_B_S15_002 | CAV_B_S15_003
entity:QNL_B_065_VENTLATON | B_065 | VENTLATON | No Equipment in entity
entity:QNL_B_066_CORRIDOR | B_066 | CORRIDOR | No Equipment in entity
entity:QNL_B_067_VENTLATON | B_067 | VENTLATON | No Equipment in entity
entity:QNL_B_068_CORRIDOR | B_068 | CORRIDOR | No Equipment in entity
entity:QNL_B_070_PLANT_ROOM_02 | B_070 | PLANT_ROOM_02 | AHUB003 | AHUB010 | AHUB013 | FCU_B_013 | FCU_B_014 | CAV_B_S13_010 | CAV_B_S13_011 | CAV_B_S13_012 | EF_BBV01 | EF_BBV02 | TEF_B02A | TEF_B02B
entity:QNL_B_071_FIRE_COMMAND_ROOM | B_071 | FIRE_COMMAND_ROOM | FCU_B_006 | EF_B14
entity:QNL_B_072_SPRIMKLERS_PUMPS_&_ZONES_VALVES | B_072 | SPRIMKLERS_PUMPS_&_ZONES_VALVES | FCU_B_007 | CAV_B_S13_021 | EF_B13
entity:QNL_B_080_GENERATOR | B_080 | GENERATOR | EF_B09 | ELEC_Gen
entity:QNL_B_081_MV_ROOM | B_081 | MV_ROOM | DX_B01 | DX_B02
entity:QNL_B_082_TRANSFORMER_ROOM | B_082 | TRANSFORMER_ROOM | DX_B03 | DX_B04 | DX_B14
entity:QNL_B_084_UPS_BATTERY_ROOM | B_084 | UPS_BATTERY_ROOM | CAV_B_S13_020 | DX_B08 | DX_B09
entity:QNL_B_085_FUMIGATION_ROOM | B_085 | FUMIGATION_ROOM | FCU_B_002 | VAV_B_S13_006 | EF_B05
entity:QNL_B_086_FREEZE_AREA | B_086 | FREEZE_AREA | No Equipment in entity
entity:QNL_B_087_GAS_SUPPRESSION_ROOM | B_087 | GAS_SUPPRESSION_ROOM | FCU_B_008 | CAV_B_S13_013
entity:QNL_B_088_PEOPLE_MOVER_PLANT | B_088 | PEOPLE_MOVER_PLANT | FCU_B_009
entity:QNL_B_089_SERVER_ROOM | B_089 | SERVER_ROOM | CAV_B_S13_015 | CCU_B05 | CCU_B06 | CCU_B07
entity:QNL_B_091_FUEL_ROOM | B_091 | FUEL_ROOM | EF_B11
entity:QNL_B_092_STORAGE | B_092 | STORAGE | DX_B20
entity:QNL_B_0924_FUEL_TANK_CHERRY_PICKER_PANKING | B_0924 | FUEL_TANK_CHERRY_PICKER_PANKING | No Equipment in entity
entity:QNL_B_093_TRANSH_CHAMBER | B_093 | TRANSH_CHAMBER | DX_B13 | DX_B15 | EF_B10
entity:QNL_B_095_EMERGENCY_LIGHTING_BATTERY_ROOM | B_095 | EMERGENCY_LIGHTING_BATTERY_ROOM | DX_B07 | DX_B16
entity:QNL_B_100_LOADING_DOCK | B_100 | LOADING_DOCK | No Equipment in entity
entity:QNL_B_101_SHIPPING_CLERK | B_101 | SHIPPING_CLERK | VAV_B_S13_007
entity:QNL_B_102_SECURITY_&_BMS | B_102 | SECURITY_&_BMS | DX_B10
entity:QNL_B_103_PROCESSING_ROOM | B_103 | PROCESSING_ROOM | VAV_B_S13_003 | VAV_B_S13_004
entity:QNL_B_104_STORAGE | B_104 | STORAGE | CAV_B_S13_009
entity:QNL_B106_RES_REST_ROOM_SECURITY | B106_RES | REST_ROOM_SECURITY | DX_B22
entity:QNL_B106_SEC_SECURITY_STORES_SECURITY_UPS | B106_SEC | SECURITY_STORES_SECURITY_UPS | No Equipment in entity
entity:QNL_B_107_SECURITY_EQUIPMENT_ROOM | B_107 | SECURITY_EQUIPMENT_ROOM | DX_B12 | DX_B23
entity:QNL_B_108_TOILET | B_108 | TOILET | No Equipment in entity
entity:QNL_B_109_LOADING_AREA | B_109 | LOADING_AREA | EF_B07 | EF_B08 | EF_B15 | EF_B16
entity:QNL_B_110_PLANT_ROOM_03 | B_110 | PLANT_ROOM_03 | AHUB004 | AHUB009 | AHUB014 | AHUB015 | FCU_B_015 | FCU_B_016 | FCU_B_017 | CAV_B_S14_003 | CAV_B_S14_004 | CAV_B_S14_005 | TEF_B01A | TEF_B01B
entity:QNL_B_111_STORAGE | B_111 | STORAGE | No Equipment in entity
entity:QNL_B_112_CORRIDOR | B_112 | CORRIDOR | No Equipment in entity
entity:QNL_B_113_MAINTENANCE | B_113 | MAINTENANCE | No Equipment in entity
entity:QNL_B_114_VENTLATON | B_114 | VENTLATON | No Equipment in entity
entity:QNL_B_115_CORRIDOR | B_115 | CORRIDOR | No Equipment in entity
entity:QNL_B_116_VENTLATON | B_116 | VENTLATON | No Equipment in entity
entity:QNL_B_120_COMPACT_SHELVING_-MAIN_COLLECTION | B_120 | COMPACT_SHELVING_-MAIN_COLLECTION | TEF_B03A | TEF_B03B
entity:QNL_B_121_SORTING_SHELVING_ROOM | B_121 | SORTING_SHELVING_ROOM | FCU_B_027 | FCU_B_028
entity:QNL_B_122_IT_OFFICE | B_122 | IT_OFFICE | FCU_B_036
entity:QNL_B_132_SHELL_SPACE-SPECIAL_COLLECTION | B_132 | SHELL_SPACE-SPECIAL_COLLECTION | FCU_B_032 | FCU_B_033 | FCU_B_034 | FCU_B_035
entity:QNL_B141_HLP_HL_PLANT_ROOM | B141_HLP | HL_PLANT_ROOM | No Equipment in entity
entity:QNL_B141_VAU_VAULT | B141_VAU | VAULT | CCU_B08 | CCU_B09
entity:QNL_B_142_CORRIDOR | B_142 | CORRIDOR | No Equipment in entity
entity:QNL_B_143_HERITAGE_COLLECTION | B_143 | HERITAGE_COLLECTION | No Equipment in entity
entity:QNL_B_144_PANTRY | B_144 | PANTRY | No Equipment in entity
entity:QNL_B_145_LOBY_&_CSECURITY | B_145 | LOBY_&_CSECURITY | FCU_B_029 | FCU_B_038 | VAV_B_S15_002 | VAV_B_S15_003 | VAV_B_S15_004
entity:QNL_B_146_VIP_REST_ROOM | B_146 | VIP_REST_ROOM | No Equipment in entity
entity:QNL_B_147_VIP_REST_ROOM | B_147 | VIP_REST_ROOM | No Equipment in entity
entity:QNL_B_148_VIP_MAJLIS | B_148 | VIP_MAJLIS | No Equipment in entity
entity:QNL_B_149_DIRECTOR_HEAD | B_149 | DIRECTOR_HEAD | VAV_B_S15_009 | VAV_B_S15_010 | VAV_B_S15_011 | VAV_B_S15_012
entity:QNL_B_150_ASSISTANT_HEAD | B_150 | ASSISTANT_HEAD | No Equipment in entity
entity:QNL_B_151_RESEARCH_&_DOC-RCRDS_MGMT | B_151 | RESEARCH_&_DOC-RCRDS_MGMT | VAV_B_S15_008 | VAV_B_S15_013
entity:QNL_B_152_SECURITY_ROOM | B_152 | SECURITY_ROOM | VAV_B_S15_007
entity:QNL_B_153_PROF_LIBRARIAN | B_153 | PROF_LIBRARIAN | VAV_B_S15_001 | VAV_B_S15_005 | VAV_B_S15_006
entity:QNL_B_155_FACULTY_CARRELS | B_155 | FACULTY_CARRELS | FCU_B_001
entity:QNL_B_156_FACULTY_CARRELS | B_156 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_157_FACULTY_CARRELS | B_157 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_158_FACULTY_CARRELS | B_158 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_159_FACULTY_CARRELS | B_159 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_160_FACULTY_CARRELS | B_160 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_161_FACULTY_CARRELS | B_161 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_162_FACULTY_CARRELS | B_162 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_163_FACULTY_CARRELS | B_163 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_164_FACULTY_CARRELS | B_164 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_165_FACULTY_CARRELS | B_165 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_166_FACULTY_CARRELS | B_166 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_167_FACULTY_CARRELS | B_167 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_168_FACULTY_CARRELS | B_168 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_169_FACULTY_CARRELS | B_169 | FACULTY_CARRELS | No Equipment in entity
entity:QNL_B_200_DIGITIZATION | B_200 | DIGITIZATION | VAV_B_S10_001 | VAV_B_S10_002 | VAV_B_S10_003 | VAV_B_S10_004 | VAV_B_S10_005 | VAV_B_S10_006 | VAV_B_S10_007 | VAV_B_S10_008 | VAV_B_S10_024
entity:QNL_B_201_REST_ROOM_MEN | B_201 | REST_ROOM_MEN | No Equipment in entity
entity:QNL_B_202_REST_ROOM_WOMEN | B_202 | REST_ROOM_WOMEN | No Equipment in entity
entity:QNL_B_203_STORAGE_ROOM | B_203 | STORAGE_ROOM | No Equipment in entity
entity:QNL_B_204_TECHNICAL_SERVICES | B_204 | TECHNICAL_SERVICES | VAV_B_S10_009 | VAV_B_S10_010 | VAV_B_S10_011
entity:QNL_B_205_INSTRUCTION_PRESENTATION | B_205 | INSTRUCTION_PRESENTATION | VAV_B_S10_016 | VAV_B_S10_017 | VAV_B_S10_018
entity:QNL_B_206_INSTRUCTION_OUTREACH | B_206 | INSTRUCTION_OUTREACH | VAV_B_S10_015
entity:QNL_B_207_PRESEARCHERS_READING_AREA | B_207 | PRESEARCHERS_READING_AREA | VAV_B_S10_020 | VAV_B_S10_021 | VAV_B_S10_022 | VAV_B_S10_023
entity:QNL_B_208_PROF_LIBRARIAN | B_208 | PROF_LIBRARIAN | VAV_B_S10_019
entity:QNL_B_209_CONSERVATION_WORK_AREA | B_209 | CONSERVATION_WORK_AREA | VAV_B_S10_012 | VAV_B_S10_013 | VAV_B_S10_014
entity:QNL_B_210_FM_STORAGE | B_210 | FM_STORAGE | FCU_B_022 | FCU_B_023
entity:QNL_B_211_PH_PLANT_ROOM | B_211 | PH_PLANT_ROOM | FCU_B_024 | HEX05
entity:QNL_B_213_MISTING_SYSTEM | B_213 | MISTING_SYSTEM | No Equipment in entity
entity:QNL_B214_COR_CORRIDOR6 | B214_COR | CORRIDOR6 | No Equipment in entity
entity:QNL_B214_IDF_IDF_ROOM | B214_IDF | IDF_ROOM | No Equipment in entity
entity:QNL_B_215_IDF_FM_STORAGE | B_215 | IDF_FM_STORAGE | FCU_B_004
entity:QNL_B_215A_IDF | B_215A | IDF | FCU_B_031 | FCU_B_037
entity:QNL_B_220_PLANT_ROOM_04 | B_220 | PLANT_ROOM_04 | AHUB001 | AHUB005 | AHUB006 | AHUB007 | AHUB008 | FCU_B_018 | FCU_B_019 | FCU_B_020 | FCU_B_021 | HEX01 | HEX02 | HEX03 | HEX04 | CHW_P01 | CHW_P02 | CHW_P03 | CHW_P04 | CHWPU_P01
entity:QNL_B_221_MAINTENANCE | B_221 | MAINTENANCE | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B_222_IDF | B_222 | IDF | FCU_B_031 AHUB001: CCU_B10; FCU_B_037 AHUB005: CCU_B11
entity:QNL_B_223_VENTILATON | B_223 | VENTILATON | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B_224_CORRIDOR | B_224 | CORRIDOR | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B_225_VENTILATON | B_225 | VENTILATON | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B_226_PUMP_ROOM | B_226 | PUMP_ROOM | FCU_B_031 AHUB001: FCU_B_030
entity:QNL_B_227_CORRIDOR | B_227 | CORRIDOR | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-AT-04A_ST-04A | B-AT-04A | ST-04A | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-L-1_L-1 | B-L-1 | L-1 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-L-15_L-15 | B-L-15 | L-15 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-L-2_L-2 | B-L-2 | L-2 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-L-3_L-3 | B-L-3 | L-3 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-L-4_L-4 | B-L-4 | L-4 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-ST-01_ST-01 | B-ST-01 | ST-01 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-ST-02_ST-02 | B-ST-02 | ST-02 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-ST-03_ST-03 | B-ST-03 | ST-03 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-ST-05_ST-05 | B-ST-05 | ST-05 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-ST-11_ST-11 | B-ST-11 | ST-11 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B-ST-12_ST-12 | B-ST-12 | ST-12 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_ST-04_ST-04 | ST-04 | ST-04 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_154_CORRIDOR | L1_154 | CORRIDOR | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_155_SECURITY_ROOM | L1_155 | SECURITY_ROOM | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_156_M2_HVAC_SHAFT | L1_156 | M2_HVAC_SHAFT | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_157_E2_ELEC_SHAFT | L1_157 | E2_ELEC_SHAFT | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_158_M1_HVAC_SHAFT | L1_158 | M1_HVAC_SHAFT | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_159_E1_ELEC_SHAFT | L1_159 | E1_ELEC_SHAFT | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_160_M3_HVAC_SHAFT | L1_160 | M3_HVAC_SHAFT | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_161_N2_PIPE_SHAFT | L1_161 | N2_PIPE_SHAFT | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_162_STORE | L1_162 | STORE | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_001_OPEN_READING_AREA | L1_001 | OPEN_READING_AREA | FCU_B_031 AHUB001: VAV_2F_S12_001; FCU_B_037 AHUB005: VAV_2F_S12_002; FCU_B_037 AHUB006: VAV_2F_S12_003; FCU_B_037 AHUB007: VAV_2F_S12_004; FCU_B_037 AHUB008: VAV_2F_S12_005; FCU_B_037 FCU_B_018: VAV_2F_S12_006; FCU_B_037 FCU_B_019: VAV_2F_S12_007; FCU_B_037 FCU_B_020: VAV_2F_S12_008; FCU_B_037 FCU_B_021: VAV_2F_S12_009
entity:QNL_L1_002_BRAILLE_READER | L1_002 | BRAILLE_READER | FCU_B_031 AHUB001: VAV_2F_S12_010; FCU_B_037 AHUB005: VAV_2F_S12_011
entity:QNL_L1_002A_GREEM_ROOM | L1_002A | GREEM_ROOM | FCU_B_031 AHUB001: VAV_1F_S15_039; FCU_B_037 AHUB005: VAV_1F_S15_040
entity:QNL_L1_003_TUTORING_HEAD | L1_003 | TUTORING_HEAD | FCU_B_031 AHUB001: VAV_2F_S12_012
entity:QNL_L1_004_WRITING_ROOM1 | L1_004 | WRITING_ROOM1 | FCU_B_031 AHUB001: VAV_2F_S12_013
entity:QNL_L1_005_WRITING_ROOM2 | L1_005 | WRITING_ROOM2 | FCU_B_031 AHUB001: VAV_2F_S12_014; FCU_B_037 AHUB005: VAV_2F_S12_015
entity:QNL_L1_006_WRITING_HEAD | L1_006 | WRITING_HEAD | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_007_STUDENT_CARRLES | L1_007 | STUDENT_CARRLES | FCU_B_031 AHUB001: VAV_2F_S12_016; FCU_B_037 AHUB005: VAV_2F_S12_017; FCU_B_037 AHUB006: VAV_2F_S12_018; FCU_B_037 AHUB007: VAV_2F_S12_019; FCU_B_037 AHUB008: VAV_2F_S12_020
entity:QNL_L1_020_INFO_LITERACY_INSTR1 | L1_020 | INFO_LITERACY_INSTR1 | FCU_B_031 AHUB001: VAV_1F_S11_004; FCU_B_037 AHUB005: VAV_1F_S11_005
entity:QNL_L1_021_INFO_LITERACY_INSTR2 | L1_021 | INFO_LITERACY_INSTR2 | FCU_B_031 AHUB001: VAV_1F_S11_006; FCU_B_037 AHUB005: VAV_1F_S11_007; FCU_B_037 AHUB006: VAV_1F_S11_008; FCU_B_037 AHUB007: VAV_1F_S11_009; FCU_B_037 AHUB008: VAV_1F_S11_010; FCU_B_037 FCU_B_018: VAV_1F_S11_011; FCU_B_037 FCU_B_019: VAV_1F_S11_012; FCU_B_037 FCU_B_020: VAV_1F_S11_013
entity:QNL_L1_022_COMPUTER_CLASSROOM | L1_022 | COMPUTER_CLASSROOM | FCU_B_031 AHUB001: VAV_1F_S11_014; FCU_B_037 AHUB005: VAV_1F_S11_015; FCU_B_037 AHUB006: VAV_1F_S11_016; FCU_B_037 AHUB007: VAV_1F_S11_017; FCU_B_037 AHUB008: VAV_1F_S11_018; FCU_B_037 FCU_B_018: VAV_1F_S11_019; FCU_B_037 FCU_B_019: VAV_1F_S11_020; FCU_B_037 FCU_B_020: VAV_1F_S11_021
entity:QNL_L1023_1_CORRIDOR | L1023_1 | CORRIDOR | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1023_2_CORRIDOR | L1023_2 | CORRIDOR | FCU_B_031 AHUB001: VAV_1F_S11_087; FCU_B_037 AHUB005: VAV_1F_S11_088; FCU_B_037 AHUB006: VAV_1F_S11_089; FCU_B_037 AHUB007: VAV_1F_S11_090
entity:QNL_L1023_3_CORRIDOR | L1023_3 | CORRIDOR | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_024_REST_ROOM_MEN | L1_024 | REST_ROOM_MEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_025_REST_ROOM_WOMEN | L1_025 | REST_ROOM_WOMEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_026_GROUP_STUDY_ROOM1 | L1_026 | GROUP_STUDY_ROOM1 | FCU_B_031 AHUB001: VAV_1F_S11_001
entity:QNL_L1_027_GROUP_STUDY_ROOM2 | L1_027 | GROUP_STUDY_ROOM2 | FCU_B_031 AHUB001: VAV_1F_S11_002
entity:QNL_L1_028_GROUP_STUDY_ROOM3 | L1_028 | GROUP_STUDY_ROOM3 | FCU_B_031 AHUB001: VAV_1F_S11_003
entity:QNL_L1_029_GROUP_STUDY_ROOM4 | L1_029 | GROUP_STUDY_ROOM4 | FCU_B_031 AHUB001: VAV_1F_S11_022
entity:QNL_L1_030_ICT_ROOM_02 | L1_030 | ICT_ROOM_02 | FCU_B_031 AHUB001: FCU_1F_002
entity:QNL_L1_040_HEAD_LIBRARIAN_OFFICE | L1_040 | HEAD_LIBRARIAN_OFFICE | FCU_B_031 AHUB001: VAV_1F_S15_005
entity:QNL_L1_041_MULTPURPOSE_ROOM | L1_041 | MULTPURPOSE_ROOM | FCU_B_031 AHUB001: VAV_1F_S15_096; FCU_B_037 AHUB005: VAV_1F_S15_097; FCU_B_037 AHUB006: VAV_1F_S15_098
entity:QNL_L1_042_LOBBY | L1_042 | LOBBY | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_043_BABY_CHAN | L1_043 | BABY_CHAN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_044_BREAST_FEEDING | L1_044 | BREAST_FEEDING | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_045_FEMALE_TOILET | L1_045 | FEMALE_TOILET | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_046_MALE_TOILET | L1_046 | MALE_TOILET | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_047_CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING | L1_047 | CHILDREN_LIBRARY_-_PRE_SCHOOL_READING_&_PLAYING | FCU_B_031 AHUB001: VAV_1F_S15_006; FCU_B_037 AHUB005: VAV_1F_S15_007; FCU_B_037 AHUB006: VAV_1F_S15_008; FCU_B_037 AHUB007: VAV_1F_S15_009; FCU_B_037 AHUB008: VAV_1F_S15_010; FCU_B_037 FCU_B_018: VAV_1F_S15_011; FCU_B_037 FCU_B_019: CAV_1F_S11_006; FCU_B_037 FCU_B_020: CAV_1F_S11_008; FCU_B_037 FCU_B_021: CAV_1F_S11_009
entity:QNL_L1_048_STAFF_OFFICE | L1_048 | STAFF_OFFICE | FCU_B_031 AHUB001: VAV_1F_S15_012; FCU_B_037 AHUB005: VAV_1F_S15_039S
entity:QNL_L1_049_STORAGE | L1_049 | STORAGE | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_050_STROLLER_PARKING | L1_050 | STROLLER_PARKING | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_061_REST_ROOM_MEN | L1_061 | REST_ROOM_MEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_062_REST_ROOM_WOMEN | L1_062 | REST_ROOM_WOMEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_063_MEDIA_STUDIO_1 | L1_063 | MEDIA_STUDIO_1 | FCU_B_031 AHUB001: VAV_1F_S15_001; FCU_B_037 AHUB005: VAV_1F_S15_002
entity:QNL_L1_064_STORAGE | L1_064 | STORAGE | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_065_MEDIA_STUDIO_1 | L1_065 | MEDIA_STUDIO_1 | FCU_B_031 AHUB001: VAV_1F_S15_003; FCU_B_037 AHUB005: VAV_1F_S15_004
entity:QNL_L1067_FRO_FRONT_KITCHEN | L1067_FRO | FRONT_KITCHEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1067_RES_RESTAURANT | L1067_RES | RESTAURANT | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_080_PUBLIC_SERVICE | L1_080 | PUBLIC_SERVICE | FCU_B_031 AHUB001: VAV_2F_S14_001; FCU_B_037 AHUB005: VAV_2F_S14_002; FCU_B_037 AHUB006: VAV_2F_S14_003; FCU_B_037 AHUB007: VAV_2F_S14_004
entity:QNL_L1_081_BIBLIOGRANHER1 | L1_081 | BIBLIOGRANHER1 | FCU_B_031 AHUB001: VAV_2F_S14_005
entity:QNL_L1_082_BIBLIOGRAPHER2 | L1_082 | BIBLIOGRAPHER2 | FCU_B_031 AHUB001: VAV_2F_S14_006
entity:QNL_L1_083_SPEC_COLL&ARCH | L1_083 | SPEC_COLL&ARCH | FCU_B_031 AHUB001: VAV_2F_S14_007
entity:QNL_L1_084_R&L_SERVICES | L1_084 | R&L_SERVICES | FCU_B_031 AHUB001: VAV_2F_S14_008
entity:QNL_L1_085_ADPUBLIC_SERVICE | L1_085 | ADPUBLIC_SERVICE | FCU_B_031 AHUB001: VAV_2F_S14_009
entity:QNL_L1_086_REF_LIBRARIAN_1 | L1_086 | REF_LIBRARIAN_1 | FCU_B_031 AHUB001: VAV_2F_S14_010
entity:QNL_L1_087_REF_LIBRARIAN_2 | L1_087 | REF_LIBRARIAN_2 | FCU_B_031 AHUB001: VAV_2F_S14_011
entity:QNL_L1_088_REF_LIBRARIAN_3 | L1_088 | REF_LIBRARIAN_3 | FCU_B_031 AHUB001: VAV_2F_S14_012
entity:QNL_L1_089_REF_LIBRARIAN_4 | L1_089 | REF_LIBRARIAN_4 | FCU_B_031 AHUB001: VAV_2F_S14_013
entity:QNL_L1_090_REF_LIBRARIAN_5 | L1_090 | REF_LIBRARIAN_5 | FCU_B_031 AHUB001: VAV_2F_S14_014
entity:QNL_L1_091_REF_LIBRARIAN_6 | L1_091 | REF_LIBRARIAN_6 | FCU_B_031 AHUB001: VAV_2F_S14_015
entity:QNL_L1_092_REF_LIBRARIAN_7 | L1_092 | REF_LIBRARIAN_7 | FCU_B_031 AHUB001: VAV_2F_S14_016
entity:QNL_L1_093_REF_LIBRARIAN_8 | L1_093 | REF_LIBRARIAN_8 | FCU_B_031 AHUB001: VAV_2F_S14_017
entity:QNL_L1_094_REF_LIBRARIAN_9 | L1_094 | REF_LIBRARIAN_9 | FCU_B_031 AHUB001: VAV_2F_S14_018
entity:QNL_L1_095_REF_LIBRARIAN_10 | L1_095 | REF_LIBRARIAN_10 | FCU_B_031 AHUB001: VAV_2F_S14_019
entity:QNL_L1_096_REF_LIBRARIAN_11 | L1_096 | REF_LIBRARIAN_11 | FCU_B_031 AHUB001: VAV_2F_S14_020
entity:QNL_L1_097_REF_LIBRARIAN_12 | L1_097 | REF_LIBRARIAN_12 | FCU_B_031 AHUB001: VAV_2F_S14_021
entity:QNL_L1_098_STORAGE | L1_098 | STORAGE | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_099_IDF_ROOM_02 | L1_099 | IDF_ROOM_02 | FCU_B_031 AHUB001: FCU_1F_003
entity:QNL_L1_100_AERIAL_PLATFORM_PARKING | L1_100 | AERIAL_PLATFORM_PARKING | FCU_B_031 AHUB001: CAV_1F_S15_004; FCU_B_037 AHUB005: CAV_1F_S15_018
entity:QNL_L1_101_REST_ROOMMEN | L1_101 | REST_ROOMMEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_102_REST_ROOM_WOMEN | L1_102 | REST_ROOM_WOMEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1104_FEM_PRAYER_ROOM_FEMALE | L1104_FEM | PRAYER_ROOM_FEMALE | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1104_MEL_PRAYER_ROOM_MALE | L1104_MEL | PRAYER_ROOM_MALE | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_105_ABLUTIONMEN | L1_105 | ABLUTIONMEN | FCU_B_031 AHUB001: VAV_1F_S15_038
entity:QNL_L1_106_ABLUTIONWOMEN | L1_106 | ABLUTIONWOMEN | FCU_B_031 AHUB001: VAV_1F_S15_025
entity:QNL_L1_130_PUBLIS_SPACE | L1_130 | PUBLIS_SPACE | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_142_LEARNING_COMMONS | L1_142 | LEARNING_COMMONS | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_153_FURNITURE_STORAGE | L1_153 | FURNITURE_STORAGE | FCU_B_031 AHUB001: CAV_1F_S15_019
entity:QNL_L1-L-1_L-1 | L1-L-1 | L-1 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1-L-2_L-2 | L1-L-2 | L-2 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1-L-3_L-3 | L1-L-3 | L-3 | FCU_B_031 AHUB001: EF_201
entity:QNL_L1-L-4_L-4 | L1-L-4 | L-4 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1-L-5_L-5 | L1-L-5 | L-5 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1-RP-10_RP-10 | L1-RP-10 | RP-10 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1-ST-01_ST-01 | L1-ST-01 | ST-01 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1-ST-02_ST-02 | L1-ST-02 | ST-02 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1-ST-03_ST-03 | L1-ST-03 | ST-03 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1-ST-10_ST-10 | L1-ST-10 | ST-10 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L1_140_SPECIAL_EVENTS | L1_140 | SPECIAL_EVENTS | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_006_STORAGE | L2_006 | STORAGE | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_007_REST_ROOM_MEN | L2_007 | REST_ROOM_MEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_008_REST_ROOM_WOMEN | L2_008 | REST_ROOM_WOMEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_009_KDF_ROOM | L2_009 | KDF_ROOM | FCU_B_031 AHUB001: FCU_2F_005
entity:QNL_L2_010_BREAKOUT_SPACE | L2_010 | BREAKOUT_SPACE | FCU_B_031 AHUB001: VAV_2F_S12_021
entity:QNL_L2_011_CTRCULATION_OFFICE | L2_011 | CTRCULATION_OFFICE | FCU_B_031 AHUB001: VAV_2F_S12_022; FCU_B_037 AHUB005: VAV_2F_S12_026
entity:QNL_L2_012_OFFICE_SPEC_COL | L2_012 | OFFICE_SPEC_COL | FCU_B_031 AHUB001: VAV_2F_S12_023
entity:QNL_L2_013_OFFICE_SPEC_COL | L2_013 | OFFICE_SPEC_COL | FCU_B_031 AHUB001: VAV_2F_S12_024
entity:QNL_L2_014_TRANSL_SPC_&_EDI_PUBLICATIONS_SPC | L2_014 | TRANSL_SPC_&_EDI_PUBLICATIONS_SPC | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_015_40_GROUP_STUDY_ROOM_5 | L2_015 | 40_GROUP_STUDY_ROOM_5 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_016_40_GROUP_STUDY_ROOM_6 | L2_016 | 40_GROUP_STUDY_ROOM_6 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_017_40_GROUP_STUDY_ROOM_7 | L2_017 | 40_GROUP_STUDY_ROOM_7 | FCU_B_031 AHUB001: VAV_2F_S12_027; FCU_B_037 AHUB005: VAV_2F_S12_029
entity:QNL_L2_018_GROUP_STUDY_ROOM_8 | L2_018 | GROUP_STUDY_ROOM_8 | FCU_B_031 AHUB001: VAV_2F_S12_028; FCU_B_037 AHUB005: VAV_2F_S12_097
entity:QNL_L2_021_LIBR_COM_REO_&_EVENTS_SPC | L2_021 | LIBR_COM_REO_&_EVENTS_SPC | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_022_ACADEMIC_PERS_LIBRARIA | L2_022 | ACADEMIC_PERS_LIBRARIA | FCU_B_031 AHUB001: VAV_2F_S13_006
entity:QNL_L2_023_AD_ADMIN_&_PLANNING | L2_023 | AD_ADMIN_&_PLANNING | FCU_B_031 AHUB001: VAV_2F_S13_007
entity:QNL_L2_024_OFFICE_COORD | L2_024 | OFFICE_COORD | FCU_B_031 AHUB001: VAV_2F_S13_008
entity:QNL_L2_025_OPEN_OFFICE | L2_025 | OPEN_OFFICE | FCU_B_031 AHUB001: VAV_2F_S13_009
entity:QNL_L2_041_PANTRY | L2_041 | PANTRY | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_042_REST_ROOM | L2_042 | REST_ROOM | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_043_SERVICE_&_LOUNGE | L2_043 | SERVICE_&_LOUNGE | FCU_B_031 AHUB001: VAV_2F_S13_003
entity:QNL_L2_044_LIBDIRECTORS_ROOM | L2_044 | LIBDIRECTORS_ROOM | FCU_B_031 AHUB001: VAV_2F_S13_001; FCU_B_037 AHUB005: VAV_2F_S13_002
entity:QNL_L2_046_VIP_MEETING | L2_046 | VIP_MEETING | FCU_B_031 AHUB001: VAV_2F_S15_005
entity:QNL_L2_047_REST_ROOM | L2_047 | REST_ROOM | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_048_VIP_WATING | L2_048 | VIP_WATING | FCU_B_031 AHUB001: VAV_2F_S13_016
entity:QNL_L2_049_REST_ROOM_MEN | L2_049 | REST_ROOM_MEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_050_REST_ROOM_WOMEN | L2_050 | REST_ROOM_WOMEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_051_VIP_ROOM | L2_051 | VIP_ROOM | FCU_B_031 AHUB001: VAV_2F_S15_001; FCU_B_037 AHUB005: VAV_2F_S15_002; FCU_B_037 AHUB006: VAV_2F_S15_003; FCU_B_037 AHUB007: VAV_2F_S15_004
entity:QNL_L2_070_INDIVISTUDY_ROOM | L2_070 | INDIVISTUDY_ROOM | FCU_B_031 AHUB001: FCU_2F_048; FCU_B_037 AHUB005: FCU_2F_049; FCU_B_037 AHUB006: FCU_2F_050
entity:QNL_L2_071_INDIVISTUDY_ROOM | L2_071 | INDIVISTUDY_ROOM | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_072_INDIVISTUDY_ROOM | L2_072 | INDIVISTUDY_ROOM | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_073_INDIVISTUDY_ROOM | L2_073 | INDIVISTUDY_ROOM | FCU_B_031 AHUB001: FCU_2F_051; FCU_B_037 AHUB005: FCU_2F_052; FCU_B_037 AHUB006: FCU_2F_053
entity:QNL_L2_074_INDIVISTUDY_ROOM | L2_074 | INDIVISTUDY_ROOM | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_075_INDIVISTUDY_ROOM | L2_075 | INDIVISTUDY_ROOM | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_076_GROUP_STUDY_ROOM | L2_076 | GROUP_STUDY_ROOM | FCU_B_031 AHUB001: FCU_2F_046; FCU_B_037 AHUB005: FCU_2F_047
entity:QNL_L2_077_GROUP_STUDY_ROOM | L2_077 | GROUP_STUDY_ROOM | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_079_REST_ROOM_MEN | L2_079 | REST_ROOM_MEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_081_GROUP_STUDY_ROOM | L2_081 | GROUP_STUDY_ROOM | FCU_B_031 AHUB001: FCU_2F_045
entity:QNL_L2_085_REST_ROOM_WOMEN | L2_085 | REST_ROOM_WOMEN | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2_087_AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID | L2_087 | AUDITORIUM_HIGH_LEVLEL_IN_CEILING_VOID | FCU_B_031 AHUB001: FCU_2F_034; FCU_B_037 AHUB005: FCU_2F_035; FCU_B_037 AHUB006: FCU_2F_036; FCU_B_037 AHUB007: FCU_2F_037; FCU_B_037 AHUB008: FCU_2F_038; FCU_B_037 FCU_B_018: FCU_2F_039; FCU_B_037 FCU_B_019: FCU_2F_040
entity:QNL_L2-L-1_1_L-1 | L2-L-1_1 | L-1 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2-L-1_2_L-2 | L2-L-1_2 | L-2 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2-L-3_L-3 | L2-L-3 | L-3 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2-L-4_L-4 | L2-L-4 | L-4 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2-ST-01_ST-01 | L2-ST-01 | ST-01 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_L2-ST-02_ST-02 | L2-ST-02 | ST-02 | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_T1_020_OPEN_LOUNGE_TERRACE | T1_020 | OPEN_LOUNGE_TERRACE | FCU_B_031 AHUB001: FCU_2F_060; FCU_B_037 AHUB005: FCU_2F_061; FCU_B_037 AHUB006: FCU_2F_062
entity:QNL_T1_021_OPEN_STUDY_TERRACE | T1_021 | OPEN_STUDY_TERRACE | FCU_B_031 AHUB001: FCU_2F_056; FCU_B_037 AHUB005: FCU_2F_057; FCU_B_037 AHUB006: FCU_2F_058; FCU_B_037 AHUB007: FCU_2F_059
entity:QNL_T1_323_IDF_ROOM | T1_323 | IDF_ROOM | FCU_B_031 AHUB001: FCU_1F_001
entity:QNL_L1_BR6_BRIDGE_CEILING_VOID | L1_BR6 | BRIDGE_CEILING_VOID | FCU_1F_004 | FCU_1F_005 | FCU_1F_006 | FCU_1F_007 | FCU_1F_008 | FCU_1F_013 | FCU_1F_015 | FCU_1F_043 | FCU_1F_044 | FCU_1F_045 | FCU_1F_046
entity:QNL_L1_BR5_BRIDGE_CEILING_VOID | L1_BR5 | BRIDGE_CEILING_VOID | FCU_B_031 AHUB001: FCU_1F_009; FCU_B_037 AHUB005: FCU_1F_010; FCU_B_037 AHUB006: FCU_1F_011; FCU_B_037 AHUB007: FCU_1F_012; FCU_B_037 AHUB008: FCU_1F_019; FCU_B_037 FCU_B_018: FCU_1F_021; FCU_B_037 FCU_B_019: FCU_1F_042; FCU_B_037 FCU_B_020: FCU_1F_053; FCU_B_037 FCU_B_021: FCU_1F_054
entity:QNL_L1_BR4_BRIDGE_CEILING_VOID | L1_BR4 | BRIDGE_CEILING_VOID | FCU_B_031 AHUB001: FCU_1F_014; FCU_B_037 AHUB005: FCU_1F_017; FCU_B_037 AHUB006: FCU_1F_018; FCU_B_037 AHUB007: FCU_1F_026; FCU_B_037 AHUB008: FCU_1F_028; FCU_B_037 FCU_B_018: FCU_1F_039; FCU_B_037 FCU_B_019: FCU_1F_040; FCU_B_037 FCU_B_020: FCU_1F_051; FCU_B_037 FCU_B_021: FCU_1F_052
entity:QNL_L1_BR3_BRIDGE_CEILING_VOID | L1_BR3 | BRIDGE_CEILING_VOID | FCU_B_031 AHUB001: FCU_1F_020; FCU_B_037 AHUB005: FCU_1F_022; FCU_B_037 AHUB006: FCU_1F_023; FCU_B_037 AHUB007: FCU_1F_024; FCU_B_037 AHUB008: FCU_1F_037; FCU_B_037 FCU_B_018: FCU_1F_038
entity:QNL_L1_BR2_BRIDGE_CEILING_VOID | L1_BR2 | BRIDGE_CEILING_VOID | FCU_B_031 AHUB001: FCU_1F_025; FCU_B_037 AHUB005: FCU_1F_027; FCU_B_037 AHUB006: FCU_1F_029; FCU_B_037 AHUB007: FCU_1F_030; FCU_B_037 AHUB008: FCU_1F_035; FCU_B_037 FCU_B_018: FCU_1F_036; FCU_B_037 FCU_B_019: FCU_1F_049; FCU_B_037 FCU_B_020: FCU_1F_050
entity:QNL_L1_BR1_BRIDGE_CEILING_VOID | L1_BR1 | BRIDGE_CEILING_VOID | FCU_B_031 AHUB001: FCU_1F_031; FCU_B_037 AHUB005: FCU_1F_032; FCU_B_037 AHUB006: FCU_1F_033; FCU_B_037 AHUB007: FCU_1F_034; FCU_B_037 AHUB008: FCU_1F_047; FCU_B_037 FCU_B_018: FCU_1F_048
entity:QNL_L1_144_ILL_DIRECTOR | L1_144 | ILL_DIRECTOR | FCU_B_031 AHUB001: FCU_1F_057; FCU_B_037 AHUB005: FCU_1F_058
entity:QNL_L1_150_RESTAURANT | L1_150 | RESTAURANT | FCU_1F_059 | FCU_1F_060 | FCU_1F_061 | FCU_1F_062 | FCU_1F_063 | FCU_1F_064 | CAV_1F_S15_002 | CAV_1F_S15_005 | CAV_1F_S15_006 | CAV_1F_S15_010 | CAV_1F_S15_011 | CAV_1F_S15_012 | CAV_1F_S15_013 | CAV_1F_S15_014 | CAV_1F_S15_015 | CAV_1F_S15_016 | CAV_1F_S15_017
entity:QNL_T1_275_IDF_ROOM | T1_275 | IDF_ROOM | FCU_B_031 AHUB001: FCU_2F_001
entity:QNL_T1_276_IDF_ROOM | T1_276 | IDF_ROOM | FCU_B_031 AHUB001: FCU_2F_002
entity:QNL_T1_171_IDF_ROOM | T1_171 | IDF_ROOM | FCU_B_031 AHUB001: FCU_2F_003
entity:QNL_T1_1714_IDF_ROOM | T1_1714 | IDF_ROOM | FCU_B_031 AHUB001: FCU_2F_004
entity:QNL_L2_088_BRIDGE_RAISED_FLOOR | L2_088 | BRIDGE_RAISED_FLOOR | FCU_B_031 AHUB001: FCU_2F_041; FCU_B_037 AHUB005: FCU_2F_042; FCU_B_037 AHUB006: FCU_2F_043; FCU_B_037 AHUB007: FCU_2F_044
entity:QNL_B_140_HL_PLANT_ROOM | B_140 | HL_PLANT_ROOM | FCU_B_031 AHUB001: FCU_B_005
entity:QNL_B_105_SECURITY_CONTOL_ROOM | B_105 | SECURITY_CONTOL_ROOM | FCU_B_031 AHUB001: FCU_B_010; FCU_B_037 AHUB005: VAV_B_S13_008
entity:QNL_B_212_MISTING_PUMP_ROOM | B_212 | MISTING_PUMP_ROOM | FCU_B_031 AHUB001: FCU_B_025; FCU_B_037 AHUB005: FCU_B_026
entity:QNL_L1_104_PRAYER_ROOM_FEMALE | L1_104 | PRAYER_ROOM_FEMALE | FCU_B_031 AHUB001: VAV_1F_S15_021; FCU_B_037 AHUB005: VAV_1F_S15_022; FCU_B_037 AHUB006: VAV_1F_S15_023; FCU_B_037 AHUB007: VAV_1F_S15_024
entity:QNL_B_001A_BREAK_OUT_AREA | B_001A | BREAK_OUT_AREA | FCU_B_031 AHUB001: VAV_B_S11_001; FCU_B_037 AHUB005: VAV_B_S11_002; FCU_B_037 AHUB006: VAV_B_S11_011; FCU_B_037 AHUB007: VAV_B_S11_012; FCU_B_037 AHUB008: KEF_B04
entity:QNL_B_056_OFFICE_DIG_INIT | B_056 | OFFICE_DIG_INIT | FCU_B_031 AHUB001: VAV_B_S14_002
entity:QNL_B_057_OFFICE_AD_FOR_LIT | B_057 | OFFICE_AD_FOR_LIT | FCU_B_031 AHUB001: VAV_B_S14_003; FCU_B_037 AHUB005: VAV_B_S14_009
entity:QNL_B_59_SHELL_SPACE | B_59 | SHELL_SPACE | FCU_B_031 AHUB001: VAV_B_S14_014
entity:QNL_B_044_BOH_KITCHEN | B_044 | BOH_KITCHEN | FCU_B_031 AHUB001: VAV_B_S14_040; FCU_B_037 AHUB005: VAV_B_S14_041; FCU_B_037 AHUB006: VAV_B_S14_047; FCU_B_037 AHUB007: CAV_B_S14_006; FCU_B_037 AHUB008: CAV_B_S14_007
entity:QNL_L1_023_CORRIDOR | L1_023 | CORRIDOR | FCU_B_031 AHUB001: CAV_1F_S11_001; FCU_B_037 AHUB005: CAV_1F_S11_002; FCU_B_037 AHUB006: CAV_1F_S11_007
entity:QNL_B_061_CORRIDOR | B_061 | CORRIDOR | FCU_B_031 AHUB001: No Equipment in entity
entity:QNL_B_064_CORRIDOR_2 | B_064 | CORRIDOR_2 | FCU_B_031 AHUB001: CAV_B_S13_001; FCU_B_037 AHUB005: CAV_B_S13_002; FCU_B_037 AHUB006: CAV_B_S13_003; FCU_B_037 AHUB007: CAV_B_S13_004; FCU_B_037 AHUB008: CAV_B_S13_005; FCU_B_037 FCU_B_018: CAV_B_S13_014
entity:QNL_B_035_CORRIDOR_4 | B_035 | CORRIDOR_4 | FCU_B_031 AHUB001: CAV_B_S13_006; FCU_B_037 AHUB005: CAV_B_S13_007; FCU_B_037 AHUB006: CAV_B_S13_008
entity:QNL_B_104A_PLANT_ROOM | B_104A | PLANT_ROOM | FCU_B_031 AHUB001: CAV_B_S13_050
entity:QNL_B_052_CORRIDOR_3 | B_052 | CORRIDOR_3 | FCU_B_031 AHUB001: CAV_B_S14_002; FCU_B_037 AHUB005: KEF_B020
entity:QNL_L1_990_VESTIBULE | L1_990 | VESTIBULE | FCU_B_031 AHUB001: FCU_1F_055
entity:QNL_L1_991_EXTERNAL_BOOK_DROP | L1_991 | EXTERNAL_BOOK_DROP | FCU_B_031 AHUB001: FCU_1F_056
entity:QNL_L2_992_GULF_MATERIAL | L2_992 | GULF_MATERIAL | FCU_B_031 AHUB001: VAV_2F_S10_001; FCU_B_037 AHUB005: VAV_2F_S10_002; FCU_B_037 AHUB006: VAV_2F_S10_003; FCU_B_037 AHUB007: VAV_2F_S10_004; FCU_B_037 AHUB008: VAV_2F_S10_005; FCU_B_037 FCU_B_018: VAV_2F_S10_006
entity:QNL_L2_993_CORRIDOR | L2_993 | CORRIDOR | FCU_B_031 AHUB001: VAV_2F_S12_025; FCU_B_037 AHUB005: VAV_2F_S13_010; FCU_B_037 AHUB006: VAV_2F_S13_011; FCU_B_037 AHUB007: VAV_2F_S13_012; FCU_B_037 AHUB008: VAV_2F_S13_013; FCU_B_037 FCU_B_018: VAV_2F_S13_014; FCU_B_037 FCU_B_019: VAV_2F_S13_015
entity:QNL_L1_BC1_BRIDGE_CEILING | L1_BC1 | BRIDGE_CEILING | FCU_B_031 AHUB001: FCU_1F_016
entity:QNL_L1_BC2_BRIDGE_CEILING | L1_BC2 | BRIDGE_CEILING | FCU_B_031 AHUB001: FCU_1F_041
entity:QNL_L1_BI_BRIDGE_IDF | L1_BI | BRIDGE_IDF | FCU_B_031 AHUB001: FCU_1F_065
entity:QNL_B_083_HV_ROOM | B_083 | HV_ROOM | FCU_B_031 AHUB001: DX_B05; FCU_B_037 AHUB005: DX_B06
entity:QNL_B_045A_REFRIGERATE_STORE | B_045A | REFRIGERATE_STORE | FCU_B_031 AHUB001: DX_B17; FCU_B_037 AHUB005: DX_B18; FCU_B_037 AHUB006: DX_B19
entity:QNL_P_004_PLANT_ZONE | P_004 | PLANT_ZONE | FCU_B_031 AHUB001: DX_B21; FCU_B_037 AHUB005: DX_B24; FCU_B_037 AHUB006: EF_RP02; FCU_B_037 AHUB007: SEF_RP07; FCU_B_037 AHUB008: SEF_RP08; FCU_B_037 FCU_B_018: SEF_RP09; FCU_B_037 FCU_B_019: SEF_ZoneB
entity:QNL_B_055_DIGITIZATION_CENTER | B_055 | DIGITIZATION_CENTER | FCU_B_031 AHUB001: EF_B06
entity:QNL_B_214_IDF_ROOM | B_214 | IDF_ROOM | FCU_B_031 AHUB001: EF_B12
entity:QNL_P_002_PLANT_ZONE | P_002 | PLANT_ZONE | FCU_B_031 AHUB001: EF_RP01; FCU_B_037 AHUB005: SEF_RP04; FCU_B_037 AHUB006: SEF_RP05; FCU_B_037 AHUB007: SEF_RP06; FCU_B_037 AHUB008: SEF_ZoneA
entity:QNL_P_007_PLANT_ZONE | P_007 | PLANT_ZONE | FCU_B_031 AHUB001: EF_RP03; FCU_B_037 AHUB005: SEF_RP10; FCU_B_037 AHUB006: SEF_ZoneC
entity:QNL_L1_067_RESTAURANT | L1_067 | RESTAURANT | FCU_B_031 AHUB001: KEF_101
entity:QNL_P_006_PLANT_ZONE | P_006 | PLANT_ZONE | FCU_B_031 AHUB001: SEF_RP11; FCU_B_037 AHUB005: SEF_RP12
entity:QNL_L1-E2_ELEC_SHAFT | L1-E2 | ELEC_SHAFT | FCU_B_031 AHUB001: TEF_101C
entity:QNL_L1-E1_ELEC_SHAFT | L1-E1 | ELEC_SHAFT | FCU_B_031 AHUB001: TEF_102C