## Dar Cairo candidates
Verdict | Family / feature | Dar Cairo rows | What it needs | QNL evidence | Tiers to build | New meters
BUILD | para:Generator_Meter | 2 meters | Generation and energy-generation sensors, run time, status | entity:QNL_ELEC-Gen exists as para:Generator with L1/L2/L3 current and voltage, frequency, on/off status, and an Electrical-Energy-Usage-Sensor via ACB14. Every input is there. | Building | 1
BUILD | brick:isSubMeterOf chain | 12 rows | Nothing - pure structure | Chains each floor and room meter up to the building meter of the same class, so the front end can walk the metering tree instead of showing 1,459 flat meters. No telemetry at all. | all tiers | 0 (1,453 rows)
BUILD | para:Electric_Power_Target / para:Thermal_Power_Target | 288 + 181 points | A target value per meter - a setpoint, not a measurement | Turns every consumption tile into over/under target. Dar Cairo attaches one to 34 meters per electrical class. Needs the targets from the client, not from the BMS. | same as the meter | 0 (1,459 points)
CONDITIONAL | para:General_Util_Meter | 68 meters | Same electrical points as HVAC / LTG / SPWR | Dar Cairo splits general utilities out as its own class at building, floor and zone. Buildable from the same basis as the four QNL already has - but only if QNL's electrical distribution actually separates a "general" category. Electrical question, not a data one. | B, F (+R?) | 6 or 360
CONDITIONAL | Forecast points (Day/Week/Month/Year) | 75 x 4 classes | The calculation engine to publish forecast series | Derived from the Consumption and Demand series the layer already declares. Dar Cairo carries 5 intervals x 2 kinds on its building meter, each with brick:aggregate + aggregationInterval. Backend capability question. | Building first | 0 (10-40 points)
CONDITIONAL | para:Energy_KPI | 42 points | A KPI formula per utility | Dar Cairo has ELEC_KPI_CALC, CW_KPI_CALC and COMBINED_KPI_CALC on its building meter. Same dependency as forecasts. | Building | 0 (2-3 points)
CONDITIONAL | EUI - brick:Energy_Sensor, unit:KiloW-HR-PER-M2 | 1 point | Gross floor area per building and level | QNL carries no area property at all - zero unit:M2. Intake asks for gross area per building and level; supply it and this is one point. | Building, Floor | 0 (1-6 points)
SKIP | para:Data-Center_Meter | 2 meters | Electrical points for the data-centre load | QNL has B-089_Server-Room and 6 IDF rooms, but the room-tier brick:Electrical_Meter already covers B-089_Server-Room. A Data-Center_Meter beside it is the Utility_Meter mistake again - a second answer to the same question. | - | 0
SKIP | para:Solar_Meter | 2 meters | Generation sensors on a PV array | No solar or PV anywhere in QNL - no array, no inverter, no generation point. | - | 0
SKIP | brick:Water_Meter | 68 meters | Potable-water flow or volume points | Zero potable-water points. Every "water" match in the sheet is a chilled-water temperature or an air flow. Nothing to sum. | - | 0
SKIP | para:Occupant-Wellbeing_Meter | 50 meters | CO2, TVOC, PM2.5, PM10, illuminance, noise, occupancy, temperature, RH | Temperature (310 points) and RH (115) available; CO2, TVOC, PM, lux, noise and occupancy all absent. Six of eight inputs missing - the KPI it exists to compute cannot be formed. | - | 0
SKIP | brick:Thermal_Power_Meter | 11 meters | - | Not needed separately: it is the parent class of para:CHW_Meter and para:HW_Meter, both of which QNL already builds. | - | 0