## START HERE
RDC - one unit, several register rows
The RDC register lists one air-terminal assembly across several rows. A VAV box is `VAV4110_EV4111` - the box and its valve - and the air terminal it feeds is a row of its own, `AT-4110`. The BMS screens draw the whole assembly as one widget, labelled the way the register writes the box: `NB-VAV4110-EV4111`. No widget is ever labelled AT; there is nothing on the screen to click for a terminal.
That is why 644 AT rows came back with no reading: they have no widget of their own, not because nothing serves them.
How the rows are grouped
By the unit number, within one building, one level and one zone, and only across the air-terminal families (AT, EV, VEV, CEV, FEV, VAV, CAV, EAV). Three things that grouping has to get right:
FCU and AHU are left out. FCU1004 and VAV1004 share a number and are different units - both are drawn as separate widgets on South GF-6.
The south building registers terminals on L0 and boxes on GF. Those are one floor under two names, so they are treated as one; every other level is kept apart, or NB_1F_AT-5930 merges with NB_2F_AT-5930.
VEV-5192a and VEV-5192b are two units. The letter is part of the number, not decoration.
What the sheets say
Assemblies every register row, grouped. `rows in assembly` is how many rows the unit is split across.
Conflicts the assemblies whose rows do not agree about the room.
Fills on the Assemblies sheet:
red the assembly names more than one room, and the room numbers differ - the register contradicts itself
amber same room, different wording (Conf against Conference, or a typo such as Director Ofice)
green a BMS screen reading applies to this row, either its own or its assembly's
A box feeding several terminals is not a conflict. AT-7120 runs to nine of them, numbered -N1 to -N9, in nine different rooms, and those rows keep their own room rather than taking the box's.

## Assemblies
Assembly | Rows in assembly | Register tag | Type | Room in column D | Assembly agrees? | Room per BMS screen | Read from
NB_AHU8511 | 1 | RDC_NB_AHU8511 | AHU | NORTH BUILDING PENT HOUSE N-2101 | yes
NB_AHU8512 | 1 | RDC_NB_AHU8512 | AHU | NORTH BUILDING PENT HOUSE N-2101 | yes
NB_2F_2F_AHU8513 | 1 | RDC_NB_2F_2F_AHU8513 | AHU | NORTH BUILDING PENT HOUSE N-2101 | yes
NB_2F_AHU8514 | 1 | RDC_NB_2F_AHU8514 | AHU | NORTH BUILDING PENT HOUSE N-2101 | yes
NB_2F_AHU8515 | 1 | RDC_NB_2F_AHU8515 | AHU | NORTH BUILDING PENT HOUSE N-2101 | yes
NB_2F_AHU8516 | 1 | RDC_NB_2F_AHU8516 | AHU | NORTH BUILDING PENT HOUSE N-2101 | yes
NB_2F_AHU8517 | 1 | RDC_NB_2F_AHU8517 | AHU | NORTH BUILDING PENT HOUSE N-2101 | yes
NB_2F_AHU8518 | 1 | RDC_NB_2F_AHU8518 | AHU | NORTH BUILDING PENT HOUSE N-2101 | yes
NB_2F_AHU8519 | 1 | RDC_NB_2F_AHU8519 | AHU | NORTH BUILDING PENT HOUSE N-2101 | yes
NB_2F_AHU8520 | 1 | RDC_NB_2F_AHU8520 | AHU | NORTH BUILDING PENT HOUSE N-2101 | yes
NB_2F_AHU8521 | 1 | RDC_NB_2F_AHU8521 | AHU | NORTH BUILDING PENT HOUSE N-2101 | yes
SB_2F_AHU8011 | 1 | RDC_SB_2F_AHU8011 | AHU | SOUTH BUILDING PENTHOUSE S-2101 | yes
SB_2F_AHU8012 | 1 | RDC_SB_2F_AHU8012 | AHU | SOUTH BUILDING PENTHOUSE S-2101 | yes
SB_2F_AHU8021 | 1 | RDC_SB_2F_AHU8021 | AHU | SOUTH BUILDING PENTHOUSE S-2101 | yes
SB_2F_AHU8022 | 1 | RDC_SB_2F_AHU8022 | AHU | SOUTH BUILDING PENTHOUSE S-2101 | yes | South Penthouse S-2101 | this row
SB_2F_AHU8023 | 1 | RDC_SB_2F_AHU8023 | AHU | SOUTH BUILDING PENTHOUSE S-2101 | yes
SB_2F_AHU8024 | 1 | RDC_SB_2F_AHU8024 | AHU | SOUTH BUILDING PENTHOUSE S-2101 | yes | South Penthouse S-2101 | this row
SB_2F_AHU8025 | 1 | RDC_SB_2F_AHU8025 | AHU | SOUTH BUILDING PENTHOUSE S-2101 | yes | South Penthouse S-2101 | this row
SB_2F_AHU8026 | 1 | RDC_SB_2F_AHU8026 | AHU | SOUTH BUILDING PENTHOUSE S-2101 | yes
SB_GF_AHU8031 | 1 | RDC_SB_GF_AHU8031 | AHU | COMPUTER RESEARCH LAB S-1112 | yes | Mech S-0136 | this row
SB_GF_AHU8032 | 1 | RDC_SB_GF_AHU8032 | AHU | COMPUTER RESEARCH LAB S-1112 | yes | Mech S-0136 | this row
SB_GF_AHU8033 | 1 | RDC_SB_GF_AHU8033 | AHU | COMPUTER RESEARCH LAB S-1112 | yes | Mech S-0136 | this row
SB_GF_AHU8034 | 1 | RDC_SB_GF_AHU8034 | AHU | COMPUTER RESEARCH LAB S-1112 | yes | Mech S-0136 | this row
SB_GF_AHU8035 | 1 | RDC_SB_GF_AHU8035 | AHU | COMPUTER RESEARCH LAB S-1112 | yes | MECH S-0136 | this row
SB_GF_AHU8036 | 1 | RDC_SB_GF_AHU8036 | AHU | COMPUTER RESEARCH LAB S-1112 | yes
SB_GF_AHU8037 | 1 | RDC_SB_GF_AHU8037 | AHU | COMPUTER RESEARCH LAB S-1112 | yes | Cyber Server S-0138 | this row
SB_GF_AHU8041 | 1 | RDC_SB_GF_AHU8041 | AHU | UPS ROOM S-0145 | yes
SB_GF_AHU8042 | 1 | RDC_SB_GF_AHU8042 | AHU | UPS ROOM S-0145 | yes | Corridor S-0143 | this row
UB_AHU8601 | 1 | RDC_UB_AHU8601 | AHU | UTILITY BUILDING MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
UB_AHU8602 | 1 | RDC_UB_AHU8602 | AHU | UTILITY BUILDING MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
UB_AHU8603 | 1 | RDC_UB_AHU8603 | AHU | UTILITY BUILDING MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
UB_AHU8604 | 1 | RDC_UB_AHU8604 | AHU | UTILITY BUILDING MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
UB_AHU8605 | 1 | RDC_UB_AHU8605 | AHU | UTILITY BUILDING MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
UB_AHU8606 | 1 | RDC_UB_AHU8606 | AHU | UTILITY BUILDING MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
UB_AHU8607 | 1 | RDC_UB_AHU8607 | AHU | UTILITY BUILDING MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
UB_AHU8608 | 1 | RDC_UB_AHU8608 | AHU | UTILITY BUILDING MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
UB_AHU8609 | 1 | RDC_UB_AHU8609 | AHU | UTILITY BUILDING MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
NB_GF_VAV4001 | 2 | RDC_NB_GF_VAV4001 | VAV | Store N-0201 | yes
|  | RDC_NB_GF_AT-4001 | AT | Store N-0201
NB_GF_VAV4005_EV4006 | 2 | RDC_NB_GF_VAV4005_EV4006 | EV | Electrical N-0202 | yes
|  | RDC_NB_GF_AT-4005 | AT | Electrical N-0202
NB_GF_VAV4040 | 1 | RDC_NB_GF_VAV4040 | VAV | Air Quality High Bay N-0215A | yes
NB_GF_VAV4050_VEV4051 | 1 | RDC_NB_GF_VAV4050_VEV4051 | VEV | CSP High Bay N-0215B | yes | CSP High Bay N-0215B | this row
NB_GF_VAV4060_VEV4061 | 1 | RDC_NB_GF_VAV4060_VEV4061 | VEV | Machine Shop N-0215C | yes | Machine Shop N-0215C | this row
NB_GF_VAV4070A_VEV4073A | 1 | RDC_NB_GF_VAV4070A_VEV4073A | VAV | Open High Bay Lab N-0215D | yes | Open High Bay Lab N-0215D | this row
NB_GF_VAV4070B_VEV4073B | 1 | RDC_NB_GF_VAV4070B_VEV4073B | VAV | Open High Bay Lab N-0215D | yes
NB_GF_VAV4071A_VEV4074A | 1 | RDC_NB_GF_VAV4071A_VEV4074A | VAV | Open High Bay Lab N-0215D | yes
NB_GF_VAV4071B_VEV4074B | 1 | RDC_NB_GF_VAV4071B_VEV4074B | VAV | Open High Bay Lab N-0215D | yes
NB_GF_VAV4072A_VEV4075A | 1 | RDC_NB_GF_VAV4072A_VEV4075A | VAV | Open High Bay Lab N-0215D | yes
NB_GF_VAV4072B_VEV4075B | 1 | RDC_NB_GF_VAV4072B_VEV4075B | VAV | Open High Bay Lab N-0215D | yes
NB_GF_VAV4080A_VEV4082A | 1 | RDC_NB_GF_VAV4080A_VEV4082A | VAV | Desal High Bay Lab N-0215E | yes | Desal High Bay Lab N-0215E | this row
NB_GF_VAV4080B_VEV4082B | 1 | RDC_NB_GF_VAV4080B_VEV4082B | VAV | Desal High Bay Lab N-0215E | yes
NB_GF_VAV4081A_VEV4083A | 1 | RDC_NB_GF_VAV4081A_VEV4083A | VAV | Desal High Bay Lab N-0215E | yes
NB_GF_VAV4081B_VEV4083B | 1 | RDC_NB_GF_VAV4081B_VEV4083B | VAV | Desal High Bay Lab N-0215E | yes | Desal High Bay Lab N-0215E | this row
NB_GF_VAV4090_VEV4091 | 1 | RDC_NB_GF_VAV4090_VEV4091 | VEV | Support Lab N-0215F | yes
NB_GF_VAV4100_EV4101 | 2 | RDC_NB_GF_VAV4100_EV4101 | EV | Emergency Elec. Room N-0225 | yes | Emergency Elec. Room N-0225 | this row
|  | RDC_NB_GF_AT-4100 | AT | Emergency Elec. Room N-0225 |  | Emergency Elec. Room N-0225 | NB_GF_VAV4100_EV4101
NB_GF_VAV4105_EV4106 | 2 | RDC_NB_GF_VAV4105_EV4106 | EV | Normal Electrical Room N-0225 | yes | Normal Elec. Room N-0226 | this row
|  | RDC_NB_GF_AT-4105 | AT | Normal Electrical Room N-0225 |  | Normal Elec. Room N-0226 | NB_GF_VAV4105_EV4106
NB_GF_VAV4110_EV4111 | 2 | RDC_NB_GF_VAV4110_EV4111 | EV | Conference Room N-0227 | yes | Conference Room N-0227 | this row
|  | RDC_NB_GF_AT-4110 | AT | Conference Room N-0227 |  | Conference Room N-0227 | NB_GF_VAV4110_EV4111
NB_GF_VAV4115_EV4116 | 2 | RDC_NB_GF_VAV4115_EV4116 | EV | Office N-0228 | yes | Office N-0228 | this row
|  | RDC_NB_GF_AT-4115 | AT | Office N-0228 |  | Office N-0228 | NB_GF_VAV4115_EV4116
NB_GF_VAV4120_EV4121 | 2 | RDC_NB_GF_VAV4120_EV4121 | EV | Office N-0229 | yes | Office N-0229 | this row
|  | RDC_NB_GF_AT-4120 | AT | Office N-0229 |  | Office N-0229 | NB_GF_VAV4120_EV4121
NB_GF_VAV4125_EV4126 | 2 | RDC_NB_GF_VAV4125_EV4126 | EV | Office N-0230 | yes | Office N-0230 | this row
|  | RDC_NB_GF_AT-4125 | AT | Office N-0230 |  | Office N-0230 | NB_GF_VAV4125_EV4126
NB_GF_VAV4130_EV4131 | 2 | RDC_NB_GF_VAV4130_EV4131 | EV | Office N-0231 | yes | Office N-0231 | this row
|  | RDC_NB_GF_AT-4130 | AT | Office N-0231 |  | Office N-0231 | NB_GF_VAV4130_EV4131
NB_GF_VAV4135_EV4136 | 2 | RDC_NB_GF_VAV4135_EV4136 | EV | Office N-0232 | yes | Office N-0232 | this row
|  | RDC_NB_GF_AT-4135 | AT | Office N-0232 |  | Office N-0232 | NB_GF_VAV4135_EV4136
NB_GF_VAV4140_EV4141 | 2 | RDC_NB_GF_VAV4140_EV4141 | EV | Conference Room N-0233 | yes
|  | RDC_NB_GF_AT-4140 | AT | Conference Room N-0233
NB_GF_VAV4145_EV4146 | 2 | RDC_NB_GF_VAV4145_EV4146 | EV | Office N-0234 | yes | Office N-0234 | this row
|  | RDC_NB_GF_AT-4145 | AT | Office N-0234 |  | Office N-0234 | NB_GF_VAV4145_EV4146
NB_GF_VAV4165_EV4166 | 2 | RDC_NB_GF_VAV4165_EV4166 | EV | Office N-0236 | yes | Office N-0236 | this row
|  | RDC_NB_GF_AT-4165 | AT | Office N-0236 |  | Office N-0236 | NB_GF_VAV4165_EV4166
NB_GF_VAV4180_VEV4181 | 1 | RDC_NB_GF_VAV4180_VEV4181 | VEV | Test Room N-0240A | yes
NB_GF_VAV4190_VEV4192 | 1 | RDC_NB_GF_VAV4190_VEV4192 | VEV | CSP Lab N-0240B | yes
NB_GF_VAV4191 | 1 | RDC_NB_GF_VAV4191 | VAV | CSP Lab N-0240B | yes
NB_GF_VAV4200_VEV4201 | 1 | RDC_NB_GF_VAV4200_VEV4201 | VEV | Test Room 1 N-0240C | yes
NB_GF_VAV4210 | 1 | RDC_NB_GF_VAV4210 | VAV | Desalination Lab N-0240D | yes
NB_GF_VAV4211 | 1 | RDC_NB_GF_VAV4211 | VAV | Desalination Lab N-0240D | yes
NB_GF_VAV4212 | 1 | RDC_NB_GF_VAV4212 | VAV | Desalination Lab N-0240D | yes
NB_GF_VAV4225 | 2 | RDC_NB_GF_VAV4225 | VAV | Office N-0247 | yes | Office N-0247 | this row
|  | RDC_NB_GF_AT-4225 | AT | Office N-0247 |  | Office N-0247 | NB_GF_VAV4225
NB_GF_VAV4230 | 2 | RDC_NB_GF_VAV4230 | VAV | Office N-0248 | yes
|  | RDC_NB_GF_AT-4230 | AT | Office N-0248
NB_GF_VAV4235 | 2 | RDC_NB_GF_VAV4235 | VAV | Office 05 -8WS- N-0250 | wording only
|  | RDC_NB_GF_AT-4235 | AT | Workstation N-0250
NB_GF_VAV4240 | 2 | RDC_NB_GF_VAV4240 | VAV | Office 04 N-0251 | yes
|  | RDC_NB_GF_AT-4240 | AT | Office N-0251
NB_GF_VAV4245 | 2 | RDC_NB_GF_VAV4245 | VAV | Office N-0252 | yes | Office N-0252 | this row
|  | RDC_NB_GF_AT-4245 | AT | Office N-0252 |  | Office N-0252 | NB_GF_VAV4245
NB_GF_VAV4250 | 2 | RDC_NB_GF_VAV4250 | VAV | Office N-0253 | yes | Office N-0253 | this row
|  | RDC_NB_GF_AT-4250 | AT | Office N-0253 |  | Office N-0253 | NB_GF_VAV4250
NB_GF_VAV4255 | 2 | RDC_NB_GF_VAV4255 | VAV | Office N-0254 | yes
|  | RDC_NB_GF_AT-4255 | AT | Office N-0254
NB_GF_VAV4260 | 2 | RDC_NB_GF_VAV4260 | VAV | Office 05 -8WS- N-0255 | wording only
|  | RDC_NB_GF_AT-4260 | AT | Workstation N-0255
NB_GF_VAV4265 | 2 | RDC_NB_GF_VAV4265 | VAV | Office N-0256 | yes
|  | RDC_NB_GF_AT-4265 | AT | Office N-0256
NB_GF_VAV4270 | 2 | RDC_NB_GF_VAV4270 | VAV | Office N-0257 | yes
|  | RDC_NB_GF_AT-4270 | AT | Office N-0257
NB_GF_VAV4275 | 2 | RDC_NB_GF_VAV4275 | VAV | Office N-0258 | yes
|  | RDC_NB_GF_AT-4275 | AT | Office N-0258
NB_GF_VAV4280 | 2 | RDC_NB_GF_VAV4280 | VAV | Office N-0259 | yes
|  | RDC_NB_GF_AT-4280 | AT | Office N-0259
NB_GF_VAV4285 | 2 | RDC_NB_GF_VAV4285 | VAV | Workstation N-0260 | yes
|  | RDC_NB_GF_AT-4285 | AT | Workstation N-0260
NB_GF_VAV4290 | 2 | RDC_NB_GF_VAV4290 | VAV | Office 04 N-0261 | yes
|  | RDC_NB_GF_AT-4290 | AT | Office N-0261
NB_GF_VAV4295 | 2 | RDC_NB_GF_VAV4295 | VAV | Office N-0262 | yes
|  | RDC_NB_GF_AT-4295 | AT | Office N-0262
NB_GF_VAV4300 | 2 | RDC_NB_GF_VAV4300 | VAV | Office N-0263 | yes
|  | RDC_NB_GF_AT-4300 | AT | Office N-0263
NB_GF_VAV4305 | 2 | RDC_NB_GF_VAV4305 | VAV | Office N-0264 | yes
|  | RDC_NB_GF_AT-4305 | AT | Office N-0264
NB_GF_VAV4310 | 2 | RDC_NB_GF_VAV4310 | VAV | Workstation N-0265 | yes
|  | RDC_NB_GF_AT-4310 | AT | Workstation N-0265
NB_GF_VAV4312 | 2 | RDC_NB_GF_VAV4312 | VAV | Breakout N-0265B | yes
|  | RDC_NB_GF_AT-4312 | AT | Breakout N-0265B
NB_GF_VAV5000_EV5002 | 2 | RDC_NB_GF_VAV5000_EV5002 | EV | Lobby North N-0101 | yes
|  | RDC_NB_GF_AT-5000 | AT | Lobby North N-0101
NB_GF_VAV5001_EV5003 | 2 | RDC_NB_GF_VAV5001_EV5003 | EV | Lobby North N-0101 | yes
|  | RDC_NB_GF_AT-5001 | AT | Lobby North N-0101
NB_GF_VAV5010_EV5011 | 2 | RDC_NB_GF_VAV5010_EV5011 | EV | Conf N-0106 | yes
|  | RDC_NB_GF_AT-5010 | AT | Conf N-0106
NB_GF_VAV5015_EV5016 | 2 | RDC_NB_GF_VAV5015_EV5016 | EV | Conference N-0107 | yes
|  | RDC_NB_GF_AT-5015 | AT | Conference N-0107
NB_GF_VAV5025 | 2 | RDC_NB_GF_VAV5025 | VAV | Corridor N-0110 | yes
|  | RDC_NB_GF_AT-5025 | AT | Corridor N-0110
NB_GF_VAV5030_EV5031 | 2 | RDC_NB_GF_VAV5030_EV5031 | EV | Confr Room N-0112 | yes
|  | RDC_NB_GF_AT-5030 | AT | Confr Room N-0112
NB_GF_VAV5040_EV5041 | 2 | RDC_NB_GF_VAV5040_EV5041 | EV | Normal Elec. N-0113 | yes
|  | RDC_NB_GF_AT-5040 | AT | Normal Elec. N-0113
NB_GF_VAV5045_EV5046 | 2 | RDC_NB_GF_VAV5045_EV5046 | EV | Emergency Elec. N-0114 | yes
|  | RDC_NB_GF_AT-5045 | AT | Emergency Elec. N-0114
NB_GF_VAV5050 | 1 | RDC_NB_GF_VAV5050 | VAV | Analytical Core Lab 1 N-0114A | yes
NB_GF_VAV5051 | 1 | RDC_NB_GF_VAV5051 | VAV | Analytical Core Lab 1 N-0114A | yes
NB_GF_VAV5054 | 1 | RDC_NB_GF_VAV5054 | VAV | Clean Lab N-0114B | yes
NB_GF_VAV5060_CEV5061 | 1 | RDC_NB_GF_VAV5060_CEV5061 | CEV | Clean Lab N-0114B | yes
NB_GF_VAV5070 | 1 | RDC_NB_GF_VAV5070 | VAV | Dirty Lab N-0114C | yes
NB_GF_VAV5080_VEV5081 | 1 | RDC_NB_GF_VAV5080_VEV5081 | VEV | Bio Analyt N-0114D | yes
NB_GF_VAV5090 | 1 | RDC_NB_GF_VAV5090 | VAV | Air Quality N-0114F | yes
NB_GF_VAV5091 | 1 | RDC_NB_GF_VAV5091 | VAV | Air Quality N-0114F | yes
NB_GF_VAV5100_EV5101 | 2 | RDC_NB_GF_VAV5100_EV5101 | EV | Office N-0115 | yes | Office N-0115 | this row
|  | RDC_NB_GF_AT-5100 | AT | Office N-0115 |  | Office N-0115 | NB_GF_VAV5100_EV5101
NB_GF_VAV5105 | 2 | RDC_NB_GF_VAV5105 | VAV | Office N-0116 | yes
|  | RDC_NB_GF_AT-5105 | AT | Office N-0116
NB_GF_VAV5110 | 2 | RDC_NB_GF_VAV5110 | VAV | Office N-0117 | yes
|  | RDC_NB_GF_AT-5110 | AT | Office N-0117
NB_GF_VAV5115 | 2 | RDC_NB_GF_VAV5115 | VAV | Office N-0118 | yes
|  | RDC_NB_GF_AT-5115 | AT | Office N-0118
NB_GF_VAV5120 | 2 | RDC_NB_GF_VAV5120 | VAV | Office N-0119 | yes | Office N-0119 | this row
|  | RDC_NB_GF_AT-5120 | AT | Office N-0119 |  | Office N-0119 | NB_GF_VAV5120
NB_GF_VAV5125 | 2 | RDC_NB_GF_VAV5125 | VAV | Office N-0120 | yes
|  | RDC_NB_GF_AT-5125 | AT | Office N-0120
NB_GF_VAV5130 | 2 | RDC_NB_GF_VAV5130 | VAV | Office N-0121 | yes
|  | RDC_NB_GF_AT-5130 | AT | Office N-0121
NB_GF_VAV5135 | 2 | RDC_NB_GF_VAV5135 | VAV | Office N-0122 | yes
|  | RDC_NB_GF_AT-5135 | AT | Office N-0122
NB_GF_VAV5140 | 2 | RDC_NB_GF_VAV5140 | VAV | Office N-0123 | yes | Office N-0123 | this row
|  | RDC_NB_GF_AT-5140 | AT | Office N-0123 |  | Office N-0123 | NB_GF_VAV5140
NB_GF_VAV5145 | 2 | RDC_NB_GF_VAV5145 | VAV | Office N-0124 | yes
|  | RDC_NB_GF_AT-5145 | AT | Office N-0124
NB_GF_VAV5150 | 2 | RDC_NB_GF_VAV5150 | VAV | Office N-0125 | yes | Office N-0125 | this row
|  | RDC_NB_GF_AT-5150 | AT | Office N-0125 |  | Office N-0125 | NB_GF_VAV5150
NB_GF_VAV5152 | 2 | RDC_NB_GF_VAV5152 | VAV | Office N-0126 | yes
|  | RDC_NB_GF_AT-5152 | AT | Office N-0126
NB_GF_VAV5155 | 2 | RDC_NB_GF_VAV5155 | VAV | Office N-0127 | yes
|  | RDC_NB_GF_AT-5155 | AT | Office N-0127
NB_GF_VAV5156 | 2 | RDC_NB_GF_VAV5156 | VAV | Office 04 N-0129 | yes
|  | RDC_NB_GF_AT-5156 | AT | Office 04 N-0129
NB_GF_VAV5165_EV5166 | 2 | RDC_NB_GF_VAV5165_EV5166 | EV | Corridor N-0134 | yes | Serv Core N-0136 | this row
|  | RDC_NB_GF_AT-5165 | AT | Corridor N-0134 |  | Serv Core N-0136 | NB_GF_VAV5165_EV5166
NB_GF_VAV5180 | 1 | RDC_NB_GF_VAV5180 | VAV | Analytical Core Lab 2 N-0140A | yes
NB_GF_VAV5181 | 1 | RDC_NB_GF_VAV5181 | VAV | Analytical Core Lab 2 N-0140A | yes
NB_GF_VAV5190 | 1 | RDC_NB_GF_VAV5190 | VAV | Furnace Room N-0140B | yes
NB_GF_VAV5200 | 1 | RDC_NB_GF_VAV5200 | VAV | Prep Lab N-0140C | yes
NB_GF_VAV5210 | 1 | RDC_NB_GF_VAV5210 | VAV | Sputter Room N-0140D | yes
NB_GF_VAV5220 | 1 | RDC_NB_GF_VAV5220 | VAV | MBE/Evap Room N-0140E | yes
NB_GF_VAV5230 | 1 | RDC_NB_GF_VAV5230 | VAV | ALD Room N-0140F | yes
NB_GF_VAV5250_VEV5251 | 1 | RDC_NB_GF_VAV5250_VEV5251 | VEV | Support Room N-0140H | yes
NB_GF_VAV5260_VEV5261 | 1 | RDC_NB_GF_VAV5260_VEV5261 | VEV | PLD Room N-0140J | yes
NB_GF_VAV5270A | 1 | RDC_NB_GF_VAV5270A | VAV | Organic Chemistry Lab N-0140K | yes
NB_GF_VAV5270B | 1 | RDC_NB_GF_VAV5270B | VAV | Org Chem N-0140K | yes
NB_GF_VAV5295_EV5296 | 2 | RDC_NB_GF_VAV5295_EV5296 | EV | Conference Room N-0149 | yes
|  | RDC_NB_GF_AT-5295 | AT | Conference Room N-0149
NB_GF_VAV5300 | 2 | RDC_NB_GF_VAV5300 | VAV | Corridor N-0150 | yes
|  | RDC_NB_GF_AT-5300 | AT | Corridor N-0150
NB_GF_VAV5305 | 2 | RDC_NB_GF_VAV5305 | VAV | Office N-0151 | yes
|  | RDC_NB_GF_AT-5305 | AT | Office N-0151
NB_GF_VAV5310 | 2 | RDC_NB_GF_VAV5310 | VAV | Office N-0152 | yes | Office N-0152 | this row
|  | RDC_NB_GF_AT-5310 | AT | Office N-0152 |  | Office N-0152 | NB_GF_VAV5310
NB_GF_VAV5315 | 2 | RDC_NB_GF_VAV5315 | VAV | Open Office N-0153 | yes
|  | RDC_NB_GF_AT-5315 | AT | Open Office N-0153
NB_GF_VAV5325 | 2 | RDC_NB_GF_VAV5325 | VAV | Office N-0155 | yes
|  | RDC_NB_GF_AT-5325 | AT | Office N-0155
NB_GF_VAV5330 | 2 | RDC_NB_GF_VAV5330 | VAV | Office N-0156 | yes
|  | RDC_NB_GF_AT-5330 | AT | Office N-0156
NB_GF_VAV5335 | 2 | RDC_NB_GF_VAV5335 | VAV | Office N-0157 | yes
|  | RDC_NB_GF_AT-5335 | AT | Office N-0157
NB_GF_VAV5340 | 2 | RDC_NB_GF_VAV5340 | VAV | Office N-0158 | yes
|  | RDC_NB_GF_AT-5340 | AT | Office N-0158
NB_GF_VAV5345 | 2 | RDC_NB_GF_VAV5345 | VAV | Office N-0159 | yes
|  | RDC_NB_GF_AT-5345 | AT | Office N-0159
NB_GF_VAV5355 | 2 | RDC_NB_GF_VAV5355 | VAV | Office N-0161 | yes
|  | RDC_NB_GF_AT-5355 | AT | Office N-0161
NB_GF_VAV5360 | 2 | RDC_NB_GF_VAV5360 | VAV | Office N-0162 | yes
|  | RDC_NB_GF_AT-5360 | AT | Office N-0162
NB_GF_VAV5365 | 2 | RDC_NB_GF_VAV5365 | VAV | Office N-0163 | yes
|  | RDC_NB_GF_AT-5365 | AT | Office N-0163
NB_GF_VAV5370 | 2 | RDC_NB_GF_VAV5370 | VAV | Office N-0164 | yes
|  | RDC_NB_GF_AT-5370 | AT | Office N-0164
NB_GF_VAV5380 | 2 | RDC_NB_GF_VAV5380 | VAV | Office N-0166 | yes
|  | RDC_NB_GF_AT-5380 | AT | Office N-0166
NB_GF_VAV5385 | 2 | RDC_NB_GF_VAV5385 | VAV | Office N-0167A | yes
|  | RDC_NB_GF_AT-5385 | AT | Office N-0167A
NB_GF_VAV5390 | 2 | RDC_NB_GF_VAV5390 | VAV | Office 04 N-0168 | yes
|  | RDC_NB_GF_AT-5390 | AT | Office 04 N-0168
NB_GF_VAV5395 | 2 | RDC_NB_GF_VAV5395 | VAV | Exp. Office N-0169 | yes
|  | RDC_NB_GF_AT-5395 | AT | Exp. Office N-0169
NB_GF_VAV5400 | 2 | RDC_NB_GF_VAV5400 | VAV | Reception Area N-0170 | yes
|  | RDC_NB_GF_AT-5400 | AT | Reception Area N-0170
NB_GF_VAV5405 | 2 | RDC_NB_GF_VAV5405 | VAV | Exp. Office N-0172 | yes
|  | RDC_NB_GF_AT-5405 | AT | Exp. Office N-0172
NB_GF_VAV5410_EV5411 | 2 | RDC_NB_GF_VAV5410_EV5411 | EV | Conf Room N-0173 | yes
|  | RDC_NB_GF_AT-5410 | AT | Conf Room N-0173
NB_GF_VAV5415 | 2 | RDC_NB_GF_VAV5415 | VAV | Office 04 N-0174 | yes
|  | RDC_NB_GF_AT-5415 | AT | Office 04 N-0174
NB_GF_VAV6000_EV6001 | 2 | RDC_NB_GF_VAV6000_EV6001 | EV | Conf Room N-0301 | yes
|  | RDC_NB_GF_AT-6000 | AT | Conf Room N-0301
NB_GF_VAV6010_EV6011 | 2 | RDC_NB_GF_VAV6010_EV6011 | EV | Conf N-0304 | yes
|  | RDC_NB_GF_AT-6010 | AT | Conf N-0304
NB_GF_VAV6025_EV6026 | 2 | RDC_NB_GF_VAV6025_EV6026 | EV | Normal Elec. N-0310 | yes
|  | RDC_NB_GF_AT-6025 | AT | Normal Elec. N-0310
NB_GF_VAV6130_EV6131 | 2 | RDC_NB_GF_VAV6130_EV6131 | EV | Store N-0315 | yes
|  | RDC_NB_GF_AT-6130 | AT | Store N-0315
NB_GF_VAV6135 | 2 | RDC_NB_GF_VAV6135 | VAV | Store N-0316 | yes | Store N-0316 | this row
|  | RDC_NB_GF_AT-6135 | AT | Store N-0316 |  | Store N-0316 | NB_GF_VAV6135
NB_GF_VAV6140 | 2 | RDC_NB_GF_VAV6140 | VAV | Workstation N-0317 | yes
|  | RDC_NB_GF_AT-6140 | AT | Workstation N-0317
NB_GF_VAV6145 | 2 | RDC_NB_GF_VAV6145 | VAV | Office N-0318 | yes
|  | RDC_NB_GF_AT-6145 | AT | Office N-0318
NB_GF_VAV6150 | 2 | RDC_NB_GF_VAV6150 | VAV | Office N-0319 | yes
|  | RDC_NB_GF_AT-6150 | AT | Office N-0319
NB_GF_VAV6155 | 2 | RDC_NB_GF_VAV6155 | VAV | Workstation N-0320 | yes
|  | RDC_NB_GF_AT-6155 | AT | Workstation N-0320
NB_GF_VAV6160 | 2 | RDC_NB_GF_VAV6160 | VAV | Office N-0321 | yes
|  | RDC_NB_GF_AT-6160 | AT | Office N-0321
NB_GF_VAV6170 | 2 | RDC_NB_GF_VAV6170 | VAV | Office N-0323 | yes
|  | RDC_NB_GF_AT-6170 | AT | Office N-0323
NB_GF_VAV6175 | 2 | RDC_NB_GF_VAV6175 | VAV | Workstation N-0324 | yes
|  | RDC_NB_GF_AT-6175 | AT | Workstation N-0324
NB_GF_VAV6180 | 2 | RDC_NB_GF_VAV6180 | VAV | Office N-0325 | yes
|  | RDC_NB_GF_AT-6180 | AT | Office N-0325
NB_GF_VAV6185_EV6186 | 2 | RDC_NB_GF_VAV6185_EV6186 | EV | Office N-0326 | yes
|  | RDC_NB_GF_AT-6185 | AT | Office N-0326
NB_GF_VAV6190_EV6191 | 2 | RDC_NB_GF_VAV6190_EV6191 | EV | Normal Elec. N-0328 | yes
|  | RDC_NB_GF_AT-6190 | AT | Normal Elec. N-0328
NB_GF_VAV6195 | 2 | RDC_NB_GF_VAV6195 | VAV | Store N-0329 | yes
|  | RDC_NB_GF_AT-6195 | AT | Store N-0329
NB_GF_VAV6200_EV6201 | 2 | RDC_NB_GF_VAV6200_EV6201 | EV | Conf N-0330 | yes
|  | RDC_NB_GF_AT-6200 | AT | Conf N-0330
NB_GF_VAV6205_EV6206 | 2 | RDC_NB_GF_VAV6205_EV6206 | EV | Conf N-0331 | wording only
|  | RDC_NB_GF_AT-6205 | AT | Conference N-0331
NB_GF_VAV6210 | 2 | RDC_NB_GF_VAV6210 | VAV | Corr. +N-033B N-0332C | different room
|  | RDC_NB_GF_AT-6210 | AT | Corridor N-0332C
NB_GF_VAV6220_EV6221 | 2 | RDC_NB_GF_VAV6220_EV6221 | EV | Emergency Elec. N-0333 | yes
|  | RDC_NB_GF_AT-6220 | AT | Emergency Elec. N-0333
NB_GF_VAV6240_EV6241 | 2 | RDC_NB_GF_VAV6240_EV6241 | EV | Emergency Electrical N-0350A | yes
|  | RDC_NB_GF_AT-6240 | AT | Emergency Electrical N-0350A
NB_GF_VAV6285_EV6286 | 2 | RDC_NB_GF_VAV6285_EV6286 | EV | Conf N-0358 | wording only
|  | RDC_NB_GF_AT-6285 | AT | Conference N-0358
NB_GF_VAV6295_EV6296 | 2 | RDC_NB_GF_VAV6295_EV6296 | EV | Conference N-0360 | yes
|  | RDC_NB_GF_AT-6295 | AT | Conference N-0360
NB_GF_VAV6300 | 2 | RDC_NB_GF_VAV6300 | VAV | Store N-0362B | yes
|  | RDC_NB_GF_AT-6300 | AT | Store N-0362B
NB_GF_VAV6305 | 2 | RDC_NB_GF_VAV6305 | VAV | Office N-0363 | yes
|  | RDC_NB_GF_AT-6305 | AT | Office N-0363
NB_GF_VAV6310 | 2 | RDC_NB_GF_VAV6310 | VAV | Office N-0364 | yes
|  | RDC_NB_GF_AT-6310 | AT | Office N-0364
NB_GF_VAV6315_EV6316 | 3 | RDC_NB_GF_VAV6315_EV6316 | EV | Conf Room N-0364A | yes
|  | RDC_NB_GF_AT-6315 | AT | Conf Room N-0364A
|  | RDC_NB_GF_EV-6316 | EV | Conf Room N-0364A
NB_GF_VAV6320 | 2 | RDC_NB_GF_VAV6320 | VAV | Corridor N-0365 | yes
|  | RDC_NB_GF_AT-6320 | AT | Corridor N-0365
NB_GF_VAV6325 | 2 | RDC_NB_GF_VAV6325 | VAV | Office N-0366 | yes
|  | RDC_NB_GF_AT-6325 | AT | Office N-0366
NB_GF_VAV6330 | 2 | RDC_NB_GF_VAV6330 | VAV | Office 04 N-0367 | yes
|  | RDC_NB_GF_AT-6330 | AT | Office 04 N-0367
NB_GF_VAV6335 | 2 | RDC_NB_GF_VAV6335 | VAV | Office N-0368 | yes
|  | RDC_NB_GF_AT-6335 | AT | Office N-0368
NB_GF_VAV6340 | 2 | RDC_NB_GF_VAV6340 | VAV | Office N-0369 | yes
|  | RDC_NB_GF_AT-6340 | AT | Office N-0369
NB_GF_VAV6345 | 2 | RDC_NB_GF_VAV6345 | VAV | Office N-0370 | yes
|  | RDC_NB_GF_AT-6345 | AT | Office N-0370
NB_GF_VAV6350 | 2 | RDC_NB_GF_VAV6350 | VAV | Office N-0371 | yes
|  | RDC_NB_GF_AT-6350 | AT | Office N-0371
NB_GF_VAV6355 | 2 | RDC_NB_GF_VAV6355 | VAV | Workstation N-0372 | yes
|  | RDC_NB_GF_AT-6355 | AT | Workstation N-0372
NB_GF_VAV6360 | 2 | RDC_NB_GF_VAV6360 | VAV | Office N-0374 | yes
|  | RDC_NB_GF_AT-6360 | AT | Office N-0374
NB_GF_VAV6365 | 2 | RDC_NB_GF_VAV6365 | VAV | Office N-0375 | yes
|  | RDC_NB_GF_AT-6365 | AT | Office N-0375
NB_GF_VAV6370 | 2 | RDC_NB_GF_VAV6370 | VAV | Office N-0376 | yes
|  | RDC_NB_GF_AT-6370 | AT | Office N-0376
NB_GF_VAV6375 | 2 | RDC_NB_GF_VAV6375 | VAV | Office N-0377 | yes
|  | RDC_NB_GF_AT-6375 | AT | Office N-0377
NB_GF_VAV6380 | 2 | RDC_NB_GF_VAV6380 | VAV | Workstation N-0378 | yes
|  | RDC_NB_GF_AT-6380 | AT | Workstation N-0378
NB_GF_VAV6390 | 2 | RDC_NB_GF_VAV6390 | VAV | Office N-0379 | yes
|  | RDC_NB_GF_AT-6390 | AT | Office N-0379
NB_GF_VAV6395 | 2 | RDC_NB_GF_VAV6395 | VAV | Office N-0380 | yes
|  | RDC_NB_GF_AT-6395 | AT | Office N-0380
NB_GF_VAV6400 | 2 | RDC_NB_GF_VAV6400 | VAV | Workstation N-0381 | yes
|  | RDC_NB_GF_AT-6400 | AT | Workstation N-0381
NB_GF_VAV6405 | 2 | RDC_NB_GF_VAV6405 | VAV | Office N-0382 | yes
|  | RDC_NB_GF_AT-6405 | AT | Office N-0382
NB_GF_VAV6410 | 2 | RDC_NB_GF_VAV6410 | VAV | Office N-0383 | yes
|  | RDC_NB_GF_AT-6410 | AT | Office N-0383
NB_GF_VAV7000 | 2 | RDC_NB_GF_VAV7000 | VAV | Vestibule Staging N-0401 | yes
|  | RDC_NB_GF_AT-7000 | AT | Vestibule / Staging N-0401
NB_GF_VAV7020A | 1 | RDC_NB_GF_VAV7020A | VAV | NMR Lab N-0404A | yes
NB_GF_VAV7020B | 1 | RDC_NB_GF_VAV7020B | VAV | NMR Lab N-0404A | yes
NB_GF_VAV7021A | 1 | RDC_NB_GF_VAV7021A | VAV | NMR Lab N-0404A | yes
NB_GF_VAV7021B | 1 | RDC_NB_GF_VAV7021B | VAV | NMR Lab N-0404A | yes
NB_GF_VAV7030_VEV7031 | 1 | RDC_NB_GF_VAV7030_VEV7031 | VEV | CONTROL ROOM N-0404B | yes
NB_GF_VAV7040 | 1 | RDC_NB_GF_VAV7040 | VAV | Service Equipm. Room N-0404C | yes
NB_GF_VAV7050_VEV7051 | 1 | RDC_NB_GF_VAV7050_VEV7051 | VEV | EM Prep 1 - MAT N-0404D | yes
NB_GF_VAV7060_VEV7061 | 1 | RDC_NB_GF_VAV7060_VEV7061 | VEV | EM Prep 2 - BIO N-0404E | yes
NB_GF_VAV7070A | 1 | RDC_NB_GF_VAV7070A | VAV | Surf Analysis Lab N-0404F | yes
NB_GF_VAV7070B | 1 | RDC_NB_GF_VAV7070B | VAV | Surf Analysis Lab N-0404F | yes
NB_GF_VAV7071A | 1 | RDC_NB_GF_VAV7071A | VAV | Surf Analysis Lab N-0404F | yes
NB_GF_VAV7071B | 1 | RDC_NB_GF_VAV7071B | VAV | Surf Analysis Lab N-0404F | yes
NB_GF_VAV7080 | 2 | RDC_NB_GF_VAV7080 | VAV | Exp. Office N-0410 | yes
|  | RDC_NB_GF_AT-7080 | AT | Exp. Office N-0410
NB_GF_VAV7085 | 2 | RDC_NB_GF_VAV7085 | VAV | Office N-0411 | yes
|  | RDC_NB_GF_AT-7085 | AT | Office N-0411
NB_GF_VAV7090 | 3 | RDC_NB_GF_VAV7090 | VAV | Office N-0412 | yes
|  | RDC_NB_GF_AT-7090-N1 | AT | Office N-0412
|  | RDC_NB_GF_AT-7090-N2 | AT | Office N-0412A
NB_GF_VAV7095 | 2 | RDC_NB_GF_VAV7095 | VAV | Office N-0413 | yes
|  | RDC_NB_GF_AT-7095 | AT | Office N-0413
NB_GF_VAV7100 | 2 | RDC_NB_GF_VAV7100 | VAV | Office N-0414 | yes
|  | RDC_NB_GF_AT-7100 | AT | Office N-0414
NB_GF_VAV7105 | 3 | RDC_NB_GF_VAV7105 | VAV | Office N-0415 | yes
|  | RDC_NB_GF_AT-7105-N1 | AT | Office N-0415
|  | RDC_NB_GF_AT-7105-N2 | AT | Office N-0415A
NB_GF_VAV7110 | 2 | RDC_NB_GF_VAV7110 | VAV | Office N-0416 | yes
|  | RDC_NB_GF_AT-7110 | AT | Office N-0416
NB_GF_VAV7115 | 2 | RDC_NB_GF_VAV7115 | VAV | Office N-0417 | yes
|  | RDC_NB_GF_AT-7115 | AT | Office N-0417
NB_GF_VAV7120 | 10 | RDC_NB_GF_VAV7120 | VAV | Office N-0418 | yes
|  | RDC_NB_GF_AT-7120-N1 | AT | Office N-0418
|  | RDC_NB_GF_AT-7120-N2 | AT | Office N-0418A
|  | RDC_NB_GF_AT-7120-N3 | AT | Office N-0430A
|  | RDC_NB_GF_AT-7120-N4 | AT | Office N-0430B
|  | RDC_NB_GF_AT-7120-N5 | AT | Office N-0430C
|  | RDC_NB_GF_AT-7120-N6 | AT | Office N-0430D
|  | RDC_NB_GF_AT-7120-N7 | AT | Office N-0430E
|  | RDC_NB_GF_AT-7120-N8 | AT | Office N-0430F
|  | RDC_NB_GF_AT-7120-N9 | AT | Corridor N-0418A
NB_GF_VAV7125_EV7126 | 2 | RDC_NB_GF_VAV7125_EV7126 | EV | Normal Elec. Room N-0420 | yes
|  | RDC_NB_GF_AT-7125 | AT | NORMAL ELEC. ROOM N-0420
NB_GF_VAV7130 | 2 | RDC_NB_GF_VAV7130 | VAV | Office N-0421 | yes
|  | RDC_NB_GF_AT-7130 | AT | Office N-0421
NB_GF_VAV7135 | 2 | RDC_NB_GF_VAV7135 | VAV | Office N-0422 | yes
|  | RDC_NB_GF_AT-7135 | AT | Office N-0422
NB_GF_VAV7140_EV7141 | 2 | RDC_NB_GF_VAV7140_EV7141 | EV | Conference N-0423 | yes
|  | RDC_NB_GF_AT-7140 | AT | Conference N-0423
NB_GF_VAV7145 | 2 | RDC_NB_GF_VAV7145 | VAV | Office N-0425 | yes
|  | RDC_NB_GF_AT-7145 | AT | Office N-0425
NB_GF_VAV7155 | 2 | RDC_NB_GF_VAV7155 | VAV | Office N-0427 | yes
|  | RDC_NB_GF_AT-7155 | AT | Office N-0427
NB_GF_VAV7165 | 2 | RDC_NB_GF_VAV7165 | VAV | Office N-0429 | yes
|  | RDC_NB_GF_AT-7165 | AT | Office N-0429
NB_GF_VAV7175 | 1 | RDC_NB_GF_VAV7175 | VAV | Office 05-15-WS N-0431 | yes | Corridor N-0432 | this row
NB_GF_VAV7176 | 1 | RDC_NB_GF_VAV7176 | VAV | Office 05-15-WS N-0431 | yes
NB_GF_VAV7180 | 2 | RDC_NB_GF_VAV7180 | VAV | Corridor N-0432 | yes
|  | RDC_NB_GF_AT-7180 | AT | Corridor N-0432
NB_GF_VAV7185_EV7186 | 2 | RDC_NB_GF_VAV7185_EV7186 | EV | Emer. Elec. Room N-0433 | yes
|  | RDC_NB_GF_AT-7185 | AT | Emer. Elec. Room N-0433
NB_GF_VAV7195 | 2 | RDC_NB_GF_VAV7195 | VAV | Office 04 N-0436 | yes
|  | RDC_NB_GF_AT-7195 | AT | OFFICE N-0436
NB_GF_VAV7205 | 2 | RDC_NB_GF_VAV7205 | VAV | Office 04 N-0438 | yes
|  | RDC_NB_GF_AT-7205 | AT | Office 04 N-0438
NB_GF_VAV7215_EV7216 | 2 | RDC_NB_GF_VAV7215_EV7216 | EV | Conference Room N-0440 | yes
|  | RDC_NB_GF_AT-7215 | AT | CONFERENCE ROOM N-0440
NB_GF_VAV7220_CEV7221 | 1 | RDC_NB_GF_VAV7220_CEV7221 | CEV | Service Corridor N-0441 | yes
NB_GF_VAV7230_VEV7231 | 1 | RDC_NB_GF_VAV7230_VEV7231 | VEV | Inter Lab N-0442A | yes
NB_GF_VAV7240_VEV7241A | 1 | RDC_NB_GF_VAV7240_VEV7241A | VAV | Optical Lab N-0442B | yes
NB_GF_VAV7250_VEV7251 | 1 | RDC_NB_GF_VAV7250_VEV7251 | VEV | CONF N-0442C | yes
NB_GF_VAV7260_VEV7261 | 1 | RDC_NB_GF_VAV7260_VEV7261 | VEV | SEM 1 Room N-0442D | yes
NB_GF_VAV7270_VEV7271 | 1 | RDC_NB_GF_VAV7270_VEV7271 | VEV | SERV 1 N-0442E | yes
NB_GF_VAV7280_VEV7281 | 1 | RDC_NB_GF_VAV7280_VEV7281 | VEV | Confocal 2 Room N-0442F | yes
NB_GF_VAV7290_VEV7291 | 1 | RDC_NB_GF_VAV7290_VEV7291 | VEV | SEM 2 N-0442G | yes
NB_GF_VAV7300 | 1 | RDC_NB_GF_VAV7300 | VAV | Air Lock 1 N-0442H | yes
NB_GF_VAV7310_VEV7311 | 1 | RDC_NB_GF_VAV7310_VEV7311 | VEV | SEM 3 N-0442J | yes
NB_GF_VAV7320_VEV7321 | 1 | RDC_NB_GF_VAV7320_VEV7321 | VEV | SEM 4 N-0442K | yes
NB_GF_VAV7330_VEV7331 | 1 | RDC_NB_GF_VAV7330_VEV7331 | VEV | SEM 5 N-0442L | yes
NB_GF_VAV7340_VEV7341 | 1 | RDC_NB_GF_VAV7340_VEV7341 | VEV | SERV 2 N-0442M | yes
NB_GF_VAV7350_VEV7351 | 1 | RDC_NB_GF_VAV7350_VEV7351 | VEV | SEM Lab N-0442N | yes
NB_GF_VAV7360_VEV7361 | 1 | RDC_NB_GF_VAV7360_VEV7361 | VEV | SEM Lab N-0442p | yes
NB_GF_VAV7370_VEV7371 | 1 | RDC_NB_GF_VAV7370_VEV7371 | VEV | A/L 2 N-0442R | yes
NB_GF_VAV7385 | 2 | RDC_NB_GF_VAV7385 | VAV | Office N-0444 | yes
|  | RDC_NB_GF_AT-7385 | AT | Office N-0444
NB_GF_VAV7390 | 2 | RDC_NB_GF_VAV7390 | VAV | Office 04 N-0445 | yes
|  | RDC_NB_GF_AT-7390 | AT | Office 04 N-0445
NB_GF_VAV7395 | 2 | RDC_NB_GF_VAV7395 | VAV | Workstation N-0446 | yes
|  | RDC_NB_GF_AT-7395 | AT | Workstation N-0446
NB_GF_VAV7400 | 2 | RDC_NB_GF_VAV7400 | VAV | Office N-0447 | yes
|  | RDC_NB_GF_AT-7400 | AT | Office N-0447
NB_GF_VAV7405 | 2 | RDC_NB_GF_VAV7405 | VAV | Office N-0448 | yes
|  | RDC_NB_GF_AT-7405 | AT | Office N-0448
NB_GF_VAV7410 | 2 | RDC_NB_GF_VAV7410 | VAV | Office N-0449 | yes
|  | RDC_NB_GF_AT-7410 | AT | Office N-0449
NB_GF_VAV7415 | 2 | RDC_NB_GF_VAV7415 | VAV | Office N-0450 | yes
|  | RDC_NB_GF_AT-7415 | AT | Office N-0450
NB_GF_VAV7425 | 2 | RDC_NB_GF_VAV7425 | VAV | Office 05-8-WKS N-0452 | wording only
|  | RDC_NB_GF_AT-7425 | AT | Workstation N-0452
NB_GF_VAV7430 | 2 | RDC_NB_GF_VAV7430 | VAV | Office N-0453 | yes
|  | RDC_NB_GF_AT-7430 | AT | Office N-0453
NB_GF_VAV7435 | 2 | RDC_NB_GF_VAV7435 | VAV | Office N-0454 | yes
|  | RDC_NB_GF_AT-7435 | AT | Office N-0454
NB_GF_VAV7440 | 2 | RDC_NB_GF_VAV7440 | VAV | Office N-0455 | yes
|  | RDC_NB_GF_AT-7440 | AT | Office N-0455
NB_GF_VAV7445 | 2 | RDC_NB_GF_VAV7445 | VAV | Office 04 N-0456 | yes
|  | RDC_NB_GF_AT-7445 | AT | Office N-0456
NB_GF_VAV7460 | 2 | RDC_NB_GF_VAV7460 | VAV | Office 05-8-WKS N-0457 | wording only | Workstation N-0457 | this row
|  | RDC_NB_GF_AT-7460 | AT | Workstation N-0457 |  | Workstation N-0457 | NB_GF_VAV7460
NB_GF_VAV7465 | 2 | RDC_NB_GF_VAV7465 | VAV | Office N-0458 | yes
|  | RDC_NB_GF_AT-7465 | AT | Office N-0458
NB_GF_VAV7470 | 2 | RDC_NB_GF_VAV7470 | VAV | Office N-0459 | yes
|  | RDC_NB_GF_AT-7470 | AT | Office N-0459
NB_GF_VAV7475 | 2 | RDC_NB_GF_VAV7475 | VAV | Office N-0460 | yes
|  | RDC_NB_GF_AT-7475 | AT | Office N-0460
NB_GF_VAV7480 | 2 | RDC_NB_GF_VAV7480 | VAV | Office N-0461 | yes
|  | RDC_NB_GF_AT-7480 | AT | Office N-0461
NB_GF_VAV7485 | 2 | RDC_NB_GF_VAV7485 | VAV | Office 05-8-WKS N-0462 | wording only
|  | RDC_NB_GF_AT-7485 | AT | WORKSTATION N-0462
NB_GF_VAV7490_EV7495 | 2 | RDC_NB_GF_VAV7490_EV7495 | EV | Confer N-0463 | yes
|  | RDC_NB_GF_AT-7490 | AT | Confer N-0463
NB_GF_VAV7496 | 2 | RDC_NB_GF_VAV7496 | VAV | Office 04 N-0464 | yes
|  | RDC_NB_GF_AT-7496 | AT | Office N-0464
NB_GF_VAV7498 | 2 | RDC_NB_GF_VAV7498 | VAV | Office N-0465 | yes
|  | RDC_NB_GF_AT-7498 | AT | Office N-0465
NB_GF_VAV7499 | 2 | RDC_NB_GF_VAV7499 | VAV | Office 04 N-0466 | yes
|  | RDC_NB_GF_AT-7499 | AT | Office N-0466
SB_1F_VAV0506 | 2 | RDC_SB_1F_VAV0506 | VAV | Conf. S-1110 | yes
|  | RDC_SB_1F_AT-0506 | AT | Conf. S-1110
SB_1F_VAV0507 | 2 | RDC_SB_1F_VAV0507 | VAV | Computer Research Lab-4 S-1112 | yes
|  | RDC_SB_1F_AT-0507 | AT | Computer Research Lab-4 S-1112
SB_1F_VAV0508 | 2 | RDC_SB_1F_VAV0508 | VAV | Conf S-1113 | yes
|  | RDC_SB_1F_AT-0508 | AT | Conf S-1113
SB_1F_VAV0509 | 2 | RDC_SB_1F_VAV0509 | VAV | NCIR Office S-1115 | yes
|  | RDC_SB_1F_AT-0509 | AT | NCIR OFFICE S-1115
SB_1F_VAV0510 | 2 | RDC_SB_1F_VAV0510 | VAV | Workstation S-1115A | yes
|  | RDC_SB_1F_AT-0510 | AT | Workstation S-1115A
SB_1F_VAV0511 | 2 | RDC_SB_1F_VAV0511 | VAV | NCIR Office S-1116 | yes
|  | RDC_SB_1F_AT-0511 | AT | NCIR Office S-1116
SB_1F_VAV0512 | 2 | RDC_SB_1F_VAV0512 | VAV | NCIR Office S-1117 | yes
|  | RDC_SB_1F_AT-0512 | AT | NCIR Office S-1117
SB_1F_VAV0513 | 2 | RDC_SB_1F_VAV0513 | VAV | NCIR Office S-1118 | yes
|  | RDC_SB_1F_AT-0513 | AT | NCIR Office S-1118
SB_1F_VAV0514 | 2 | RDC_SB_1F_VAV0514 | VAV | NCIR Office S-1119 | yes | Sc.Comp.Office3 S-1119 | this row
|  | RDC_SB_1F_AT-0514 | AT | NCIR Office S-1119 |  | Sc.Comp.Office3 S-1119 | SB_1F_VAV0514
SB_1F_VAV0518 | 2 | RDC_SB_1F_VAV0518 | VAV | Office S-1161 | yes
|  | RDC_SB_1F_AT-0518 | AT | Office S-1161
SB_1F_VAV0519 | 2 | RDC_SB_1F_VAV0519 | VAV | Office S-1162 | yes
|  | RDC_SB_1F_AT-0519 | AT | Office S-1162
SB_1F_VAV0520 | 2 | RDC_SB_1F_VAV0520 | VAV | Office S-1163 | yes
|  | RDC_SB_1F_AT-0520 | AT | Office S-1163
SB_1F_VAV0521 | 2 | RDC_SB_1F_VAV0521 | VAV | Office S-1164 | yes
|  | RDC_SB_1F_AT-0521 | AT | Office S-1164
SB_1F_VAV0522 | 2 | RDC_SB_1F_VAV0522 | VAV | Office S-1165 | yes
|  | RDC_SB_1F_AT-0522 | AT | Office S-1165
SB_1F_VAV0523 | 2 | RDC_SB_1F_VAV0523 | VAV | Office S-1166 | yes
|  | RDC_SB_1F_AT-0523 | AT | Office S-1166
SB_1F_VAV0526 | 2 | RDC_SB_1F_VAV0526 | VAV | Office S-1171 | yes
|  | RDC_SB_1F_AT-0526 | AT | Office S-1171
SB_1F_VAV0527 | 2 | RDC_SB_1F_VAV0527 | VAV | Office S-1172 | yes
|  | RDC_SB_1F_AT-0527 | AT | Office S-1172
SB_1F_VAV0528 | 2 | RDC_SB_1F_VAV0528 | VAV | Office S-1173 | yes
|  | RDC_SB_1F_AT-0528 | AT | Office S-1173
SB_1F_VAV0529 | 2 | RDC_SB_1F_VAV0529 | VAV | Corridor S-1174 | yes
|  | RDC_SB_1F_AT-0529 | AT | Corridor S-1174
SB_1F_VAV0530 | 2 | RDC_SB_1F_VAV0530 | VAV | Situation Room S-1175 | yes
|  | RDC_SB_1F_AT-0530 | AT | Situation Room S-1175
SB_1F_VAV0531 | 2 | RDC_SB_1F_VAV0531 | VAV | Immersive Viz Lab S-1176 | yes
|  | RDC_SB_1F_AT-0531 | AT | Immersive Viz Lab S-1176
SB_1F_VAV0532 | 2 | RDC_SB_1F_VAV0532 | VAV | Conference Room S-1177 | yes
|  | RDC_SB_1F_AT-0532 | AT | Conference Room S-1177
SB_1F_VAV0533 | 2 | RDC_SB_1F_VAV0533 | VAV | Telepresence S-1179 | yes
|  | RDC_SB_1F_AT-0533 | AT | Telepresence S-1179
SB_1F_VAV0538 | 2 | RDC_SB_1F_VAV0538 | VAV | Workstation S-1151A | yes
|  | RDC_SB_1F_AT-0538 | AT | Workstation S-1151A
SB_1F_VAV1501 | 2 | RDC_SB_1F_VAV1501 | VAV | Workstation S-1119A | yes
|  | RDC_SB_1F_AT-1501 | AT | Workstation S-1119A
SB_1F_VAV1502 | 2 | RDC_SB_1F_VAV1502 | VAV | NCIR Office S-1120 | yes
|  | RDC_SB_1F_AT-1502 | AT | NCIR Office S-1120
SB_1F_VAV1503 | 2 | RDC_SB_1F_VAV1503 | VAV | NCIR Office S-1121 | yes
|  | RDC_SB_1F_AT-1503 | AT | NCIR Office S-1121
SB_1F_VAV1505 | 2 | RDC_SB_1F_VAV1505 | VAV | SC. Comp Office 2 S-1123 | yes
|  | RDC_SB_1F_AT-1505 | AT | SC. Comp Office 2 S-1123
SB_1F_VAV1506 | 2 | RDC_SB_1F_VAV1506 | VAV | SC. Comp Office 3 S-1124 | yes
|  | RDC_SB_1F_AT-1506 | AT | SC. Comp Office 3 S-1124
SB_1F_VAV1507 | 2 | RDC_SB_1F_VAV1507 | VAV | Workstation S-1124A | yes
|  | RDC_SB_1F_AT-1507 | AT | Workstation S-1124A
SB_1F_VAV1508 | 2 | RDC_SB_1F_VAV1508 | VAV | Scientific Comp. Office 1 S-1125 | yes
|  | RDC_SB_1F_AT-1508 | AT | Scientific Comp. Office 1 S-1125
SB_1F_VAV1509 | 2 | RDC_SB_1F_VAV1509 | VAV | Scientific Comp. Office S-1126 | yes
|  | RDC_SB_1F_AT-1509 | AT | Scientific Comp. Office S-1126
SB_1F_VAV1510 | 2 | RDC_SB_1F_VAV1510 | VAV | ALT Office 2 S-1127 | yes
|  | RDC_SB_1F_AT-1510 | AT | ALT Office 2 S-1127
SB_1F_VAV1511 | 2 | RDC_SB_1F_VAV1511 | VAV | ALT Office 3 S-1128 | yes
|  | RDC_SB_1F_AT-1511 | AT | ALT Office 3 S-1128
SB_1F_VAV1512 | 2 | RDC_SB_1F_VAV1512 | VAV | Workstation S-1128A | yes
|  | RDC_SB_1F_AT-1512 | AT | Workstation S-1128A
SB_1F_VAV1513 | 2 | RDC_SB_1F_VAV1513 | VAV | ALT Office 1 S-1129 | yes
|  | RDC_SB_1F_AT-1513 | AT | ALT Office 1 S-1129
SB_1F_VAV1514 | 2 | RDC_SB_1F_VAV1514 | VAV | ALT Office S-1130 | yes
|  | RDC_SB_1F_AT-1514 | AT | ALT Office S-1130
SB_1F_VAV1515 | 2 | RDC_SB_1F_VAV1515 | VAV | Distub. Syst Office 1 S-1131 | yes
|  | RDC_SB_1F_AT-1515 | AT | Distub. Syst Office 1 S-1131
SB_1F_VAV1516 | 2 | RDC_SB_1F_VAV1516 | VAV | Distub. Syst Office S-1132 | yes
|  | RDC_SB_1F_AT-1516 | AT | Distub. Syst Office S-1132
SB_1F_VAV1517 | 2 | RDC_SB_1F_VAV1517 | VAV | Workstation S-1132A | yes
|  | RDC_SB_1F_AT-1517 | AT | Workstation S-1132A
SB_1F_VAV1518 | 2 | RDC_SB_1F_VAV1518 | VAV | Distub. Syst Office S-1133 | yes
|  | RDC_SB_1F_AT-1518 | AT | Distub. Syst Office S-1133
SB_1F_VAV1519 | 2 | RDC_SB_1F_VAV1519 | VAV | Distub. Syst Office S-1134 | yes
|  | RDC_SB_1F_AT-1519 | AT | Distub. Syst Office S-1134
SB_1F_VAV1520 | 2 | RDC_SB_1F_VAV1520 | VAV | Data Analytic Office S-1135 | yes
|  | RDC_SB_1F_AT-1520 | AT | Data Analytic Office S-1135
SB_1F_VAV1521 | 2 | RDC_SB_1F_VAV1521 | VAV | Data Analytic Office S-1136 | yes
|  | RDC_SB_1F_AT-1521 | AT | Data Analytic Office S-1136
SB_1F_VAV1522 | 2 | RDC_SB_1F_VAV1522 | VAV | Workstation S-1136A | yes
|  | RDC_SB_1F_AT-1522 | AT | Workstation S-1136A
SB_1F_VAV1523 | 2 | RDC_SB_1F_VAV1523 | VAV | Data Analytic Office S-1137 | yes
|  | RDC_SB_1F_AT-1523 | AT | Data Analytic Office S-1137
SB_1F_VAV1524 | 2 | RDC_SB_1F_VAV1524 | VAV | Data Analytic Office S-1138 | yes
|  | RDC_SB_1F_AT-1524 | AT | Data Analytic Office S-1138
SB_1F_VAV1525 | 2 | RDC_SB_1F_VAV1525 | VAV | Office S-1139 | yes
|  | RDC_SB_1F_AT-1525 | AT | Office S-1139
SB_1F_VAV1526 | 2 | RDC_SB_1F_VAV1526 | VAV | Office S-1140 | yes
|  | RDC_SB_1F_AT-1526 | AT | Office S-1140
SB_1F_VAV1527 | 2 | RDC_SB_1F_VAV1527 | VAV | Conference Room S-1141 | yes
|  | RDC_SB_1F_AT-1527 | AT | Conference Room S-1141
SB_1F_VAV1528 | 2 | RDC_SB_1F_VAV1528 | VAV | Office S-1142 | yes
|  | RDC_SB_1F_AT-1528 | AT | Office S-1142
SB_1F_VAV1529 | 2 | RDC_SB_1F_VAV1529 | VAV | Office S-1144 | yes
|  | RDC_SB_1F_AT-1529 | AT | Office S-1144
SB_1F_VAV1530 | 2 | RDC_SB_1F_VAV1530 | VAV | Office S-1145 | yes
|  | RDC_SB_1F_AT-1530 | AT | Office S-1145
SB_1F_VAV1531 | 2 | RDC_SB_1F_VAV1531 | VAV | Office S-1146 | yes
|  | RDC_SB_1F_AT-1531 | AT | Office S-1146
SB_1F_VAV1532 | 2 | RDC_SB_1F_VAV1532 | VAV | Workstation S-1146A | yes
|  | RDC_SB_1F_AT-1532 | AT | Workstation S-1146A
SB_1F_VAV1533 | 2 | RDC_SB_1F_VAV1533 | VAV | Office S-1148 | yes
|  | RDC_SB_1F_AT-1533 | AT | Office S-1148
SB_1F_VAV1534 | 2 | RDC_SB_1F_VAV1534 | VAV | Office S-1149 | yes
|  | RDC_SB_1F_AT-1534 | AT | Office S-1149
SB_1F_VAV1536 | 2 | RDC_SB_1F_VAV1536 | VAV | Office S-1150 | yes
|  | RDC_SB_1F_AT-1536 | AT | Office S-1150
SB_1F_VAV1539 | 2 | RDC_SB_1F_VAV1539 | VAV | Video Conf. Room S-1154 | yes
|  | RDC_SB_1F_AT-1539 | AT | Video Conf. Room S-1154
SB_1F_VAV1540 | 2 | RDC_SB_1F_VAV1540 | VAV | Conf S-1159 | yes
|  | RDC_SB_1F_AT-1540 | AT | Conf S-1159
SB_1F_VAV1542 | 2 | RDC_SB_1F_VAV1542 | VAV | Office S-1182 | yes
|  | RDC_SB_1F_AT-1542 | AT | Office S-1182
SB_1F_VAV1543 | 2 | RDC_SB_1F_VAV1543 | VAV | Workstation S-1182A | yes
|  | RDC_SB_1F_AT-1543 | AT | Workstation S-1182A
SB_1F_VAV1544 | 2 | RDC_SB_1F_VAV1544 | VAV | Office S-1182C | yes
|  | RDC_SB_1F_AT-1544 | AT | Office S-1182C
SB_1F_VAV1545 | 2 | RDC_SB_1F_VAV1545 | VAV | Office S-1182D | yes
|  | RDC_SB_1F_AT-1545 | AT | Office S-1182D
SB_1F_VAV1546 | 2 | RDC_SB_1F_VAV1546 | VAV | Office S-1182E | yes
|  | RDC_SB_1F_AT-1546 | AT | Office S-1182E
SB_1F_VAV1547 | 2 | RDC_SB_1F_VAV1547 | VAV | Office S-1182F | yes
|  | RDC_SB_1F_AT-1547 | AT | Office S-1182F
SB_1F_VAV1548 | 2 | RDC_SB_1F_VAV1548 | VAV | Office S-1183 | yes
|  | RDC_SB_1F_AT-1548 | AT | Office S-1183
SB_1F_VAV1549 | 2 | RDC_SB_1F_VAV1549 | VAV | Workstation S-1183A | yes
|  | RDC_SB_1F_AT-1549 | AT | Workstation S-1183A
SB_1F_VAV1550 | 2 | RDC_SB_1F_VAV1550 | VAV | Office S-1184 | yes
|  | RDC_SB_1F_AT-1550 | AT | Office S-1184
SB_1F_VAV1551 | 2 | RDC_SB_1F_VAV1551 | VAV | Social Comp Office S-1185 | yes
|  | RDC_SB_1F_AT-1551 | AT | Social Comp Office S-1185
SB_1F_VAV1552 | 2 | RDC_SB_1F_VAV1552 | VAV | Social Comp Office S-1186 | yes
|  | RDC_SB_1F_AT-1552 | AT | Social Comp Office S-1186
SB_1F_VAV1553 | 2 | RDC_SB_1F_VAV1553 | VAV | Workstation S-1186A | yes
|  | RDC_SB_1F_AT-1553 | AT | Workstation S-1186A
SB_1F_VAV1554 | 2 | RDC_SB_1F_VAV1554 | VAV | Social Comp Office S-1187 | yes
|  | RDC_SB_1F_AT-1554 | AT | Social Comp Office S-1187
SB_1F_VAV1555 | 2 | RDC_SB_1F_VAV1555 | VAV | Social Comp Office S-1188 | yes
|  | RDC_SB_1F_AT-1555 | AT | Social Comp Office S-1188
SB_1F_VAV1556 | 2 | RDC_SB_1F_VAV1556 | VAV | Cyber Sec Office S-1189 | yes
|  | RDC_SB_1F_AT-1556 | AT | Cyber Sec Office S-1189
SB_1F_VAV1557 | 2 | RDC_SB_1F_VAV1557 | VAV | Cyber Sec Office S-1190 | yes
|  | RDC_SB_1F_AT-1557 | AT | Cyber Sec Office S-1190
SB_1F_VAV1558 | 2 | RDC_SB_1F_VAV1558 | VAV | Workstation S-1190A | yes
|  | RDC_SB_1F_AT-1558 | AT | Workstation S-1190A
SB_1F_VAV1559 | 2 | RDC_SB_1F_VAV1559 | VAV | Office S-1191 | yes
|  | RDC_SB_1F_AT-1559 | AT | Office S-1191
SB_1F_VAV1560 | 2 | RDC_SB_1F_VAV1560 | VAV | Cyber Sec Office S-1192 | yes
|  | RDC_SB_1F_AT-1560 | AT | Cyber Sec Office S-1192
SB_1F_VAV1561 | 2 | RDC_SB_1F_VAV1561 | VAV | Cyber Sec Office S-1193 | yes
|  | RDC_SB_1F_AT-1561 | AT | Cyber Sec Office S-1193
SB_1F_VAV2501 | 2 | RDC_SB_1F_VAV2501 | VAV | Lobby S-1201 | yes
|  | RDC_SB_1F_AT-2501 | AT | Lobby S-1201
SB_1F_VAV2502 | 2 | RDC_SB_1F_VAV2502 | VAV | Lobby S-1202 | yes
|  | RDC_SB_1F_AT-2502 | AT | Lobby S-1202
SB_1F_VAV2503 | 2 | RDC_SB_1F_VAV2503 | VAV | Lobby S-1202 | yes
|  | RDC_SB_1F_AT-2503 | AT | Lobby S-1202
SB_1F_VAV2504 | 2 | RDC_SB_1F_VAV2504 | VAV | Lobby S-1202 | yes
|  | RDC_SB_1F_AT-2504 | AT | Lobby S-1202
SB_1F_VAV2505 | 2 | RDC_SB_1F_VAV2505 | VAV | Lobby S-1202 | yes
|  | RDC_SB_1F_AT-2505 | AT | Lobby S-1202
SB_1F_VAV2506 | 2 | RDC_SB_1F_VAV2506 | VAV | Lobby S-1202 | yes
|  | RDC_SB_1F_AT-2506 | AT | Lobby S-1202
SB_1F_VAV2508 | 2 | RDC_SB_1F_VAV2508 | VAV | Female Prayer S-1207 | yes
|  | RDC_SB_1F_AT-2508 | AT | Female Prayer S-1207
SB_1F_VAV2509 | 2 | RDC_SB_1F_VAV2509 | VAV | Open Plan S-1210 | yes
|  | RDC_SB_1F_AT-2509 | AT | Open Plan S-1210
SB_1F_VAV2510 | 2 | RDC_SB_1F_VAV2510 | VAV | Exc. Dir. Office S-1211 | yes
|  | RDC_SB_1F_AT-2510 | AT | Exc. Dir. Office S-1211
SB_1F_VAV2511 | 2 | RDC_SB_1F_VAV2511 | VAV | Office S-1212 | yes
|  | RDC_SB_1F_AT-2511 | AT | Office S-1212
SB_1F_VAV2512 | 2 | RDC_SB_1F_VAV2512 | VAV | Office S-1213 | yes
|  | RDC_SB_1F_AT-2512 | AT | Office S-1213
SB_1F_VAV2513 | 2 | RDC_SB_1F_VAV2513 | VAV | Office S-1214 | yes
|  | RDC_SB_1F_AT-2513 | AT | Office S-1214
SB_1F_VAV2514 | 2 | RDC_SB_1F_VAV2514 | VAV | Office S-1215 | yes
|  | RDC_SB_1F_AT-2514 | AT | Office S-1215
SB_1F_VAV2515 | 2 | RDC_SB_1F_VAV2515 | VAV | Office S-1216 | yes
|  | RDC_SB_1F_AT-2515 | AT | Office S-1216
SB_1F_VAV2516 | 2 | RDC_SB_1F_VAV2516 | VAV | Executive Director Office S-1217 | yes
|  | RDC_SB_1F_AT-2516 | AT | Executive Director Office S-1217
SB_1F_VAV2517 | 2 | RDC_SB_1F_VAV2517 | VAV | Executive Director Office S-1218 | yes
|  | RDC_SB_1F_AT-2517 | AT | Executive Director Office S-1218
SB_1F_VAV2518 | 2 | RDC_SB_1F_VAV2518 | VAV | Office S-1219 | yes
|  | RDC_SB_1F_AT-2518 | AT | Office S-1219
SB_1F_VAV2519 | 2 | RDC_SB_1F_VAV2519 | VAV | Office S-1220 | yes
|  | RDC_SB_1F_AT-2519 | AT | Office S-1220
SB_1F_VAV2520 | 2 | RDC_SB_1F_VAV2520 | VAV | Office S-1221 | yes
|  | RDC_SB_1F_AT-2520 | AT | Office S-1221
SB_1F_VAV2521 | 2 | RDC_SB_1F_VAV2521 | VAV | Office S-1222 | yes
|  | RDC_SB_1F_AT-2521 | AT | Office S-1222
SB_1F_VAV2522 | 2 | RDC_SB_1F_VAV2522 | VAV | Office S-1223 | yes
|  | RDC_SB_1F_AT-2522 | AT | Office S-1223
SB_1F_VAV2523 | 2 | RDC_SB_1F_VAV2523 | VAV | Office S-1224 | yes
|  | RDC_SB_1F_AT-2523 | AT | Office S-1224
SB_1F_VAV2524 | 2 | RDC_SB_1F_VAV2524 | VAV | Office S-1225 | yes
|  | RDC_SB_1F_AT-2524 | AT | Office S-1225
SB_1F_VAV2525 | 2 | RDC_SB_1F_VAV2525 | VAV | Office S-1226 | yes
|  | RDC_SB_1F_AT-2525 | AT | Office S-1226
SB_1F_VAV2526 | 2 | RDC_SB_1F_VAV2526 | VAV | Open Plan S-1227 | yes
|  | RDC_SB_1F_AT-2526 | AT | Open Plan S-1227
SB_1F_VAV2527 | 2 | RDC_SB_1F_VAV2527 | VAV | Director Office S-1228 | yes
|  | RDC_SB_1F_AT-2527 | AT | Director Office S-1228
SB_1F_VAV2528 | 2 | RDC_SB_1F_VAV2528 | VAV | Director Office S-1230 | yes
|  | RDC_SB_1F_AT-2528 | AT | Director Office S-1230
SB_1F_VAV2529 | 2 | RDC_SB_1F_VAV2529 | VAV | Office S-1231 | yes
|  | RDC_SB_1F_AT-2529 | AT | Office S-1231
SB_1F_VAV2530 | 2 | RDC_SB_1F_VAV2530 | VAV | Office S-1232 | yes
|  | RDC_SB_1F_AT-2530 | AT | Office S-1232
SB_1F_VAV2531 | 2 | RDC_SB_1F_VAV2531 | VAV | Director Office S-1241 | wording only
|  | RDC_SB_1F_AT-2531 | AT | Director Ofice S-1241
SB_1F_VAV2532 | 2 | RDC_SB_1F_VAV2532 | VAV | Office S-1242 | yes
|  | RDC_SB_1F_AT-2532 | AT | Office S-1242
SB_1F_VAV2533 | 2 | RDC_SB_1F_VAV2533 | VAV | Cooridor S-1246 | yes
|  | RDC_SB_1F_AT-2533 | AT | Cooridor S-1246
SB_1F_VAV2534 | 2 | RDC_SB_1F_VAV2534 | VAV | Meeting Room S-1247 | yes
|  | RDC_SB_1F_AT-2534 | AT | Meeting Room S-1247
SB_1F_VAV2535 | 2 | RDC_SB_1F_VAV2535 | VAV | Store S-1248 | yes
|  | RDC_SB_1F_AT-2535 | AT | Store S-1248
SB_1F_VAV2536 | 2 | RDC_SB_1F_VAV2536 | VAV | Normal Elec. S-1251 | yes | Mech. Chasing S-1249 | this row
|  | RDC_SB_1F_AT-2536 | AT | Normal Elec. S-1251 |  | Mech. Chasing S-1249 | SB_1F_VAV2536
SB_1F_VAV2538 | 2 | RDC_SB_1F_VAV2538 | VAV | Office S-1257 | yes
|  | RDC_SB_1F_AT-2538 | AT | Office S-1257
SB_1F_VAV2539 | 2 | RDC_SB_1F_VAV2539 | VAV | Office S-1257B | yes
|  | RDC_SB_1F_AT-2539 | AT | Office S-1257B
SB_1F_VAV2540 | 2 | RDC_SB_1F_VAV2540 | VAV | Executive Director S-1260 | yes
|  | RDC_SB_1F_AT-2540 | AT | Executive Director S-1260
SB_1F_VAV2541 | 2 | RDC_SB_1F_VAV2541 | VAV | Assistant S-1261 | yes
|  | RDC_SB_1F_AT-2541 | AT | Assistant S-1261
SB_1F_VAV2542 | 2 | RDC_SB_1F_VAV2542 | VAV | Open Plan S-1263 | yes
|  | RDC_SB_1F_AT-2542 | AT | Open Plan S-1263
SB_1F_VAV2543 | 2 | RDC_SB_1F_VAV2543 | VAV | Office S-1264 | yes
|  | RDC_SB_1F_AT-2543 | AT | Office S-1264
SB_1F_VAV2544 | 2 | RDC_SB_1F_VAV2544 | VAV | Office S-1265 | yes
|  | RDC_SB_1F_AT-2544 | AT | Office S-1265
SB_1F_VAV2545 | 2 | RDC_SB_1F_VAV2545 | VAV | Office S-1266 | yes
|  | RDC_SB_1F_AT-2545 | AT | Office S-1266
SB_1F_VAV2546 | 2 | RDC_SB_1F_VAV2546 | VAV | Office S-1267 | yes
|  | RDC_SB_1F_AT-2546 | AT | Office S-1267
SB_1F_VAV2547 | 2 | RDC_SB_1F_VAV2547 | VAV | Office S-1268 | yes
|  | RDC_SB_1F_AT-2547 | AT | Office S-1268
SB_1F_VAV2548 | 2 | RDC_SB_1F_VAV2548 | VAV | Office S-1269 | yes
|  | RDC_SB_1F_AT-2548 | AT | Office S-1269
SB_1F_VAV2549 | 2 | RDC_SB_1F_VAV2549 | VAV | Office S-1270 | yes
|  | RDC_SB_1F_AT-2549 | AT | Office S-1270
SB_1F_VAV2550 | 2 | RDC_SB_1F_VAV2550 | VAV | Office S-1271 | yes
|  | RDC_SB_1F_AT-2550 | AT | Office S-1271
SB_1F_VAV2551 | 2 | RDC_SB_1F_VAV2551 | VAV | Meeting Room S-1272 | yes
|  | RDC_SB_1F_AT-2551 | AT | Meeting Room S-1272
SB_1F_VAV2552 | 2 | RDC_SB_1F_VAV2552 | VAV | Vestibule S-1273 | yes | FPC S-1277 | this row
|  | RDC_SB_1F_AT-2552 | AT | Vestibule S-1273 |  | FPC S-1277 | SB_1F_VAV2552
SB_1F_VAV2553 | 2 | RDC_SB_1F_VAV2553 | VAV | Male Prayer S-1278 | yes
|  | RDC_SB_1F_AT-2553 | AT | Male Prayer S-1278
SB_1F_VAV3504 | 2 | RDC_SB_1F_VAV3504 | VAV | Open Plan S-1229 | yes
|  | RDC_SB_1F_AT-3504 | AT | Open Plan S-1229
SB_1F_VAV3505 | 2 | RDC_SB_1F_VAV3505 | VAV | Open Plan S-1229 | yes
|  | RDC_SB_1F_AT-3505 | AT | Open Plan S-1229
SB_1F_VAV3506 | 2 | RDC_SB_1F_VAV3506 | VAV | Office S-1233 | yes
|  | RDC_SB_1F_AT-3506 | AT | Office S-1233
SB_1F_VAV3507 | 2 | RDC_SB_1F_VAV3507 | VAV | Office S-1234 | yes
|  | RDC_SB_1F_AT-3507 | AT | Office S-1234
SB_1F_VAV3508 | 2 | RDC_SB_1F_VAV3508 | VAV | Office S-1235 | yes
|  | RDC_SB_1F_AT-3508 | AT | Office S-1235
SB_1F_VAV3509 | 2 | RDC_SB_1F_VAV3509 | VAV | Policy Director Office S-1237 | yes
|  | RDC_SB_1F_AT-3509 | AT | Policy Director Office S-1237
SB_1F_VAV3510 | 2 | RDC_SB_1F_VAV3510 | VAV | Policy Executive Director Office S-1240 | yes
|  | RDC_SB_1F_AT-3510 | AT | Policy Executive Director Office S-1240
SB_1F_VAV3511 | 2 | RDC_SB_1F_VAV3511 | VAV | Corridor S-1280 | yes
|  | RDC_SB_1F_AT-3511 | AT | CORRIDOR S-1280
SB_1F_VAV3512 | 2 | RDC_SB_1F_VAV3512 | VAV | Pantry S-1282 | yes
|  | RDC_SB_1F_AT-3512 | AT | Pantry S-1282
SB_1F_VAV3513 | 2 | RDC_SB_1F_VAV3513 | VAV | Office S-1283 | yes
|  | RDC_SB_1F_AT-3513 | AT | Office S-1283
SB_1F_VAV3514 | 2 | RDC_SB_1F_VAV3514 | VAV | Office S-1284 | yes
|  | RDC_SB_1F_AT-3514 | AT | Office S-1284
SB_1F_VAV3515 | 2 | RDC_SB_1F_VAV3515 | VAV | S-1285 VP R&D | yes
|  | RDC_SB_1F_AT-3515 | AT | S-1285 VP R&D
SB_1F_VAV3516 | 2 | RDC_SB_1F_VAV3516 | VAV | Meeting Room S-1288 | yes
|  | RDC_SB_1F_AT-3516 | AT | Meeting Room S-1288
SB_1F_VAV3517 | 2 | RDC_SB_1F_VAV3517 | VAV | Dressing Room S-1290 | yes
|  | RDC_SB_1F_AT-3517 | AT | Dressing Room S-1290
SB_1F_VAV3518 | 2 | RDC_SB_1F_VAV3518 | VAV | Waiting Area S-1292 | yes
|  | RDC_SB_1F_AT-3518 | AT | Waiting Area S-1292
SB_1F_VAV3519 | 1 | RDC_SB_1F_VAV3519 | VAV | Open Plan S-1293 | yes
SB_1F_VAV3520 | 2 | RDC_SB_1F_VAV3520 | VAV | Office S-1294 | yes
|  | RDC_SB_1F_AT-3520 | AT | Office S-1294
SB_1F_VAV3521 | 2 | RDC_SB_1F_VAV3521 | VAV | Office S-1295 | yes
|  | RDC_SB_1F_AT-3521 | AT | Office S-1295
SB_1F_VAV3522 | 2 | RDC_SB_1F_VAV3522 | VAV | Conference Room S-1296 | yes
|  | RDC_SB_1F_AT-3522 | AT | Conference Room S-1296
SB_1F_VAV3523 | 2 | RDC_SB_1F_VAV3523 | VAV | Office S-1299 | yes
|  | RDC_SB_1F_AT-3523 | AT | Office S-1299
SB_1F_VAV3524 | 2 | RDC_SB_1F_VAV3524 | VAV | Normal Elec. S-1238 | yes
|  | RDC_SB_1F_AT-3524 | AT | Normal Elec. S-1238
SB_GF_VAV0001 | 2 | RDC_SB_GF_VAV0001 | VAV | Vestibule S-0101 | yes | Vestbule S-0101 | this row
|  | RDC_SB_L0_AT-0001 | AT | Vestibule S-0101 |  | Vestbule S-0101 | SB_GF_VAV0001
SB_GF_VAV0002 | 2 | RDC_SB_GF_VAV0002 | VAV | Main Lobby S-0102 | wording only
|  | RDC_SB_L0_AT-0002 | AT | Employee Entry Lobby S-0102
SB_GF_VAV0003 | 2 | RDC_SB_GF_VAV0003 | VAV | Entrance Lobby S-0102 | yes
|  | RDC_SB_L0_AT-0003 | AT | Entrance Lobby S-0102
SB_GF_VAV0007 | 2 | RDC_SB_GF_VAV0007 | VAV | Conference S-0109 | wording only
|  | RDC_SB_L0_AT-0007 | AT | Conf S-0109
SB_GF_VAV0008 | 2 | RDC_SB_GF_VAV0008 | VAV | Computer Research Lab 3 S-0110 | yes
|  | RDC_SB_L0_AT-0008 | AT | Computer Research Lab 3 S-0110
SB_GF_VAV0009 | 2 | RDC_SB_GF_VAV0009 | VAV | Phone Booth S-0111 | yes
|  | RDC_SB_L0_AT-0009 | AT | Phone Booth S-0111
SB_GF_VAV0010 | 2 | RDC_SB_GF_VAV0010 | VAV | Phone Booth S-0112 | yes
|  | RDC_SB_L0_AT-0010 | AT | Phone Booth S-0112
SB_GF_VAV0011 | 2 | RDC_SB_GF_VAV0011 | VAV | Conference S-0113 | yes
|  | RDC_SB_L0_AT-0011 | AT | Conference Room S-0113
SB_GF_VAV0012 | 2 | RDC_SB_GF_VAV0012 | VAV | Computer Research Lab 2 S-0114 | yes
|  | RDC_SB_L0_AT-0012 | AT | Computer Research Lab 2 S-0114
SB_GF_VAV0013 | 2 | RDC_SB_GF_VAV0013 | VAV | Phone Booth S-0115 | yes
|  | RDC_SB_L0_AT-0013 | AT | Phone Booth S-0115
SB_GF_VAV0014 | 2 | RDC_SB_GF_VAV0014 | VAV | Phone Booth S-0116 | yes
|  | RDC_SB_L0_AT-0014 | AT | Phone Booth S-0116
SB_GF_VAV0016 | 2 | RDC_SB_GF_VAV0016 | VAV | Conference S-0118 | wording only
|  | RDC_SB_L0_AT-0016 | AT | Conf S-0118
SB_GF_VAV0017 | 2 | RDC_SB_GF_VAV0017 | VAV | Computer Research Lab 1 S-0119 | yes
|  | RDC_SB_L0_AT-0017 | AT | Computer Research Lab 1 S-0119
SB_GF_VAV0018 | 2 | RDC_SB_GF_VAV0018 | VAV | Restaurant S-0123 | yes
|  | RDC_SB_L0_AT-0018 | AT | Restaurant S-0123
SB_GF_VAV0019 | 2 | RDC_SB_GF_VAV0019 | VAV | Restaurant S-0123 | yes
|  | RDC_SB_L0_AT-0019 | AT | Restaurant S-0123
SB_GF_VAV0025 | 2 | RDC_SB_GF_VAV0025 | VAV | Alt Recording Sound S-0135 | yes
|  | RDC_SB_L0_AT-0025 | AT | Alt Recording/Sound S-0135
SB_GF_VAV1003_VEV1002 | 5 | RDC_SB_GF_VAV1003_VEV1002 | VEV | NOC Lab S-0140A | different room
|  | RDC_SB_L0_AT-1002 | AT | Computer Lab S-0139
|  | RDC_SB_L0_AT-1003 | AT | NOC S-0140A
|  | RDC_SB_L0_EV-1002 | EV | NOC S-0140A
|  | RDC_SB_L0_EV-1003 | EV | UPS S-0145
SB_GF_VAV1004 | 2 | RDC_SB_GF_VAV1004 | VAV | Corridor S-0137 / S-0143 | different room | Dedicated Cyber SOC/NOC Lab S-0141 | this row
|  | RDC_SB_L0_AT-1004 | AT | Dedicated Cyber SOC/NOC Lab S-0141 |  | Dedicated Cyber SOC/NOC Lab S-0141 | SB_GF_VAV1004
SB_GF_VAV1008 | 2 | RDC_SB_GF_VAV1008 | VAV | Cyber Embedded Sys. S-0146 | wording only
|  | RDC_SB_L0_AT-1008 | AT | Cyber/Embedded/Dist System Electrical Lab S-0146
SB_GF_VAV2002 | 2 | RDC_SB_GF_VAV2002 | VAV | Conference Room S-0207 | yes
|  | RDC_SB_L0_AT-2002 | AT | Conference Room S-0207
SB_GF_VAV2003 | 2 | RDC_SB_GF_VAV2003 | VAV | Multi Purpose Hall S-0208 | yes
|  | RDC_SB_L0_AT-2003 | AT | Multi Purpose Hall S-0208
SB_GF_VAV2004 | 2 | RDC_SB_GF_VAV2004 | VAV | Multi Purpose Hall S-0208 | yes
|  | RDC_SB_L0_AT-2004 | AT | Multi Purpose Hall S-0208
SB_GF_VAV2005 | 1 | RDC_SB_GF_VAV2005 | VAV | Technical Open Plan S-0211 | yes
SB_GF_VAV2006 | 2 | RDC_SB_GF_VAV2006 | VAV | Meeting Room S-0212 | yes
|  | RDC_SB_L0_AT-2006 | AT | Meeting Room S-0212
SB_GF_VAV2007 | 2 | RDC_SB_GF_VAV2007 | VAV | Office S-0213 | yes | Office S-0213 | this row
|  | RDC_SB_L0_AT-2007 | AT | Office S-0213 |  | Office S-0213 | SB_GF_VAV2007
SB_GF_VAV2008 | 2 | RDC_SB_GF_VAV2008 | VAV | Office S-0214 | yes | Office S-0214 | this row
|  | RDC_SB_L0_AT-2008 | AT | Office S-0214 |  | Office S-0214 | SB_GF_VAV2008
SB_GF_VAV2009 | 2 | RDC_SB_GF_VAV2009 | VAV | Office S-0215 | yes | Office S-0215 | this row
|  | RDC_SB_L0_AT-2009 | AT | Office S-0215 |  | Office S-0215 | SB_GF_VAV2009
SB_GF_VAV2010 | 2 | RDC_SB_GF_VAV2010 | VAV | Office S-0216 | yes | Office S-0216 | this row
|  | RDC_SB_L0_AT-2010 | AT | Office S-0216 |  | Office S-0216 | SB_GF_VAV2010
SB_GF_VAV2011 | 2 | RDC_SB_GF_VAV2011 | VAV | Office S-0217 | yes | Office S-0217 | this row
|  | RDC_SB_L0_AT-2011 | AT | Office S-0217 |  | Office S-0217 | SB_GF_VAV2011
SB_GF_VAV2012 | 2 | RDC_SB_GF_VAV2012 | VAV | Director Office S-0218 | yes | Director Office S-0218 | this row
|  | RDC_SB_L0_AT-2012 | AT | Director Office S-0218 |  | Director Office S-0218 | SB_GF_VAV2012
SB_GF_VAV2013 | 2 | RDC_SB_GF_VAV2013 | VAV | Office S-0219 | yes | Office S-0219 | this row
|  | RDC_SB_L0_AT-2013 | AT | Office S-0219 |  | Office S-0219 | SB_GF_VAV2013
SB_GF_VAV2014 | 2 | RDC_SB_GF_VAV2014 | VAV | Office S-0220 | yes | Office S-0220 | this row
|  | RDC_SB_L0_AT-2014 | AT | Office S-0220 |  | Office S-0220 | SB_GF_VAV2014
SB_GF_VAV2015 | 2 | RDC_SB_GF_VAV2015 | VAV | Director Office S-0221 | yes | Director Office S-0221 | this row
|  | RDC_SB_L0_AT-2015 | AT | Director Office S-0221 |  | Director Office S-0221 | SB_GF_VAV2015
SB_GF_VAV2016 | 2 | RDC_SB_GF_VAV2016 | VAV | Director Office S-0222 | yes | Director Office S-0222 | this row
|  | RDC_SB_L0_AT-2016 | AT | Director Office S-0222 |  | Director Office S-0222 | SB_GF_VAV2016
SB_GF_VAV2017 | 2 | RDC_SB_GF_VAV2017 | VAV | Meeting Room S-0223 | yes
|  | RDC_SB_L0_AT-2017 | AT | Meeting Room S-0223
SB_GF_VAV2018 | 2 | RDC_SB_GF_VAV2018 | VAV | Print Hub S-0225 | different room
|  | RDC_SB_L0_AT-2018 | AT | PANTRY S-0226
SB_GF_VAV2019 | 2 | RDC_SB_GF_VAV2019 | VAV | Office S-0227 | yes
|  | RDC_SB_L0_AT-2019 | AT | Office S-0227
SB_GF_VAV2020 | 2 | RDC_SB_GF_VAV2020 | VAV | Informal Meeting S-0231 | yes
|  | RDC_SB_L0_AT-2020 | AT | Informal Meeting S-0231
SB_GF_VAV2021 | 2 | RDC_SB_GF_VAV2021 | VAV | Open Plan S-0228 | yes
|  | RDC_SB_L0_AT-2021 | AT | Open Plan S-0228
SB_GF_VAV2022 | 2 | RDC_SB_GF_VAV2022 | VAV | Director Office S-0229 | yes
|  | RDC_SB_L0_AT-2022 | AT | Director Office S-0229
SB_GF_VAV2023 | 2 | RDC_SB_GF_VAV2023 | VAV | Office S-0230 | yes
|  | RDC_SB_L0_AT-2023 | AT | Office S-0230
SB_GF_VAV2024 | 2 | RDC_SB_GF_VAV2024 | VAV | Executive Director Office S-0232 | yes
|  | RDC_SB_L0_AT-2024 | AT | Executive Director Office S-0232
SB_GF_VAV2025 | 2 | RDC_SB_GF_VAV2025 | VAV | Executive Director Office S-0233 | yes
|  | RDC_SB_L0_AT-2025 | AT | Executive Director Office S-0233
SB_GF_VAV2026 | 2 | RDC_SB_GF_VAV2026 | VAV | Office S-0234 | yes
|  | RDC_SB_L0_AT-2026 | AT | Office S-0234
SB_GF_VAV2027 | 2 | RDC_SB_GF_VAV2027 | VAV | Office S-0235 | yes
|  | RDC_SB_L0_AT-2027 | AT | Office S-0235
SB_GF_VAV2028 | 2 | RDC_SB_GF_VAV2028 | VAV | Office S-0236 | yes
|  | RDC_SB_L0_AT-2028 | AT | Office S-0236
SB_GF_VAV2029 | 2 | RDC_SB_GF_VAV2029 | VAV | Waiting Area S-0251 | yes
|  | RDC_SB_L0_AT-2029 | AT | Waiting Area S-0251
SB_GF_VAV2030 | 2 | RDC_SB_GF_VAV2030 | VAV | Office S-0259 | yes
|  | RDC_SB_L0_AT-2030 | AT | Office S-0259
SB_GF_VAV2031 | 2 | RDC_SB_GF_VAV2031 | VAV | Office S-0260 | yes
|  | RDC_SB_L0_AT-2031 | AT | Office S-0260
SB_GF_VAV2032 | 2 | RDC_SB_GF_VAV2032 | VAV | Open Plan S-0269 | yes
|  | RDC_SB_L0_AT-2032 | AT | Open Plan S-0269
SB_GF_VAV2033 | 2 | RDC_SB_GF_VAV2033 | VAV | Store S-0275 | different room
|  | RDC_SB_L0_AT-2033 | AT | CORRIDOR S-0273
SB_GF_VAV2034 | 2 | RDC_SB_GF_VAV2034 | VAV | Meeting Room S-0274 | yes
|  | RDC_SB_L0_AT-2034 | AT | Meeting Room S-0274
SB_GF_VAV2035 | 2 | RDC_SB_GF_VAV2035 | VAV | Pantry S-0270 | different room
|  | RDC_SB_L0_AT-2035 | AT | MECH S-0272
SB_GF_VAV2036 | 2 | RDC_SB_GF_VAV2036 | VAV | Emergency Elec. Room S-0278 | yes
|  | RDC_SB_L0_AT-2036 | AT | Emergency Elec. Room S-0278
SB_GF_VAV2037 | 2 | RDC_SB_GF_VAV2037 | VAV | Men S-0284 | yes
|  | RDC_SB_L0_AT-2037 | AT | Men S-0284
SB_GF_VAV2038 | 2 | RDC_SB_GF_VAV2038 | VAV | Informal Meeting S-0285 | yes
|  | RDC_SB_L0_AT-2038 | AT | Informal Meeting S-0285
SB_GF_VAV2039 | 2 | RDC_SB_GF_VAV2039 | VAV | Meeting Room S-0286 | yes
|  | RDC_SB_L0_AT-2039 | AT | Meeting Room S-0286
SB_GF_VAV2040 | 2 | RDC_SB_GF_VAV2040 | VAV | Open Plan S-0289 | yes
|  | RDC_SB_L0_AT-2040 | AT | Open Plan S-0289
SB_GF_VAV2041 | 2 | RDC_SB_GF_VAV2041 | VAV | Open Plan S-0289 | yes
|  | RDC_SB_L0_AT-2041 | AT | Open Plan S-0289
SB_GF_VAV2042 | 2 | RDC_SB_GF_VAV2042 | VAV | Corridor S-0273 | different room
|  | RDC_SB_L0_AT-2042 | AT | Lobby S-0294
SB_GF_VAV2043 | 2 | RDC_SB_GF_VAV2043 | VAV | Women S-0281 | different room
|  | RDC_SB_L0_AT-2043 | AT | Lobby S-0294
SB_GF_VAV2044 | 2 | RDC_SB_GF_VAV2044 | VAV | Lobby S-0294 | yes
|  | RDC_SB_L0_AT-2044 | AT | Lobby S-0294
SB_GF_VAV2045 | 2 | RDC_SB_GF_VAV2045 | VAV | Lobby S-0294 | yes
|  | RDC_SB_L0_AT-2045 | AT | Lobby S-0294
SB_GF_VAV2046 | 2 | RDC_SB_GF_VAV2046 | VAV | Lobby S-0294 | yes
|  | RDC_SB_L0_AT-2046 | AT | Lobby S-0294
SB_GF_VAV2047 | 2 | RDC_SB_GF_VAV2047 | VAV | Lobby S-0294 | yes
|  | RDC_SB_L0_AT-2047 | AT | Lobby S-0294
SB_GF_VAV3001 | 2 | RDC_SB_GF_VAV3001 | VAV | Director Office S-0237 | yes | Director Office S-0237 | this row
|  | RDC_SB_L0_AT-3001 | AT | Director Office S-0237 |  | Director Office S-0237 | SB_GF_VAV3001
SB_GF_VAV3002 | 2 | RDC_SB_GF_VAV3002 | VAV | Office S-0238 | yes
|  | RDC_SB_L0_AT-3002 | AT | Office S-0238
SB_GF_VAV3003 | 2 | RDC_SB_GF_VAV3003 | VAV | Office S-0239 | yes
|  | RDC_SB_L0_AT-3003 | AT | Office S-0239
SB_GF_VAV3004 | 2 | RDC_SB_GF_VAV3004 | VAV | Office S-0240 | yes
|  | RDC_SB_L0_AT-3004 | AT | Office S-0240
SB_GF_VAV3005 | 2 | RDC_SB_GF_VAV3005 | VAV | Office S-0241 | yes
|  | RDC_SB_L0_AT-3005 | AT | Office S-0241
SB_GF_VAV3006 | 2 | RDC_SB_GF_VAV3006 | VAV | Office S-0242 | yes
|  | RDC_SB_L0_AT-3006 | AT | Office S-0242
SB_GF_VAV3007 | 2 | RDC_SB_GF_VAV3007 | VAV | Director Office S-0243 | yes
|  | RDC_SB_L0_AT-3007 | AT | Director Office S-0243
SB_GF_VAV3008 | 1 | RDC_SB_GF_VAV3008 | VAV | Open Plan S-0244 | yes
SB_GF_VAV3009 | 1 | RDC_SB_GF_VAV3009 | VAV | Open Plan S-0244 | yes
SB_GF_VAV3010 | 2 | RDC_SB_GF_VAV3010 | VAV | Open Plan S-0244 | yes
|  | RDC_SB_L0_AT-3010 | AT | Open Plan S-0244
SB_GF_VAV3011 | 2 | RDC_SB_GF_VAV3011 | VAV | Meeting Room S-0245 | yes
|  | RDC_SB_L0_AT-3011 | AT | Meeting Room S-0245
SB_GF_VAV3012 | 2 | RDC_SB_GF_VAV3012 | VAV | Office S-0246 | yes
|  | RDC_SB_L0_AT-3012 | AT | Office S-0246
SB_GF_VAV3013 | 2 | RDC_SB_GF_VAV3013 | VAV | Office S-0247 | yes
|  | RDC_SB_L0_AT-3013 | AT | Office S-0247
SB_GF_VAV3014 | 2 | RDC_SB_GF_VAV3014 | VAV | Office S-0248 | yes
|  | RDC_SB_L0_AT-3014 | AT | Office S-0248
SB_GF_VAV3015 | 2 | RDC_SB_GF_VAV3015 | VAV | Security S-0249 | yes
|  | RDC_SB_L0_AT-3015 | AT | Security S-0249
SB_GF_VAV3016 | 2 | RDC_SB_GF_VAV3016 | VAV | Corridor S-0250 | yes
|  | RDC_SB_L0_AT-3016 | AT | Corridor S-0250
SB_GF_VAV3017 | 2 | RDC_SB_GF_VAV3017 | VAV | Office S-0251 | yes
|  | RDC_SB_L0_AT-3017 | AT | Office S-0251
SB_GF_VAV3018 | 2 | RDC_SB_GF_VAV3018 | VAV | Corridor S-0251 | different room
|  | RDC_SB_L0_AT-3018 | AT | Corridor S-0251B
SB_GF_VAV3019 | 2 | RDC_SB_GF_VAV3019 | VAV | Corridor S-0251 | different room
|  | RDC_SB_L0_AT-3019 | AT | Corridor S-0251B
SB_GF_VAV3020 | 2 | RDC_SB_GF_VAV3020 | VAV | Office S-0252 | yes
|  | RDC_SB_L0_AT-3020 | AT | Office S-0252
SB_GF_VAV3021 | 2 | RDC_SB_GF_VAV3021 | VAV | Office S-0252 | yes
|  | RDC_SB_L0_AT-3021 | AT | Office S-0252
SB_GF_VAV3022 | 2 | RDC_SB_GF_VAV3022 | VAV | Office S-0253 | yes
|  | RDC_SB_L0_AT-3022 | AT | Office S-0253
SB_GF_VAV3023 | 2 | RDC_SB_GF_VAV3023 | VAV | Office S-0253 | yes
|  | RDC_SB_L0_AT-3023 | AT | Office S-0253
SB_GF_VAV3024 | 2 | RDC_SB_GF_VAV3024 | VAV | Office S-0254 | yes
|  | RDC_SB_L0_AT-3024 | AT | Office S-0254
SB_GF_VAV3025 | 2 | RDC_SB_GF_VAV3025 | VAV | Office S-0255 | yes
|  | RDC_SB_L0_AT-3025 | AT | Office S-0255
SB_GF_VAV3026 | 2 | RDC_SB_GF_VAV3026 | VAV | Office S-0256 | yes
|  | RDC_SB_L0_AT-3026 | AT | Office S-0256
SB_GF_VAV3027 | 2 | RDC_SB_GF_VAV3027 | VAV | Office S-0257 | yes
|  | RDC_SB_L0_AT-3027 | AT | Office S-0257
SB_GF_VAV3028 | 2 | RDC_SB_GF_VAV3028 | VAV | Office S-0258 | yes
|  | RDC_SB_L0_AT-3028 | AT | Office S-0258
SB_GF_VAV3029 | 1 | RDC_SB_GF_VAV3029 | VAV | Open Plan S-0261 | yes
SB_GF_VAV3030 | 1 | RDC_SB_GF_VAV3030 | VAV | Open Plan S-0262 | yes
SB_GF_VAV3031 | 2 | RDC_SB_GF_VAV3031 | VAV | Server S-0264 | wording only
|  | RDC_SB_L0_AT-3031 | AT | IT Server S-0264
SB_GF_VAV3032 | 2 | RDC_SB_GF_VAV3032 | VAV | Open Plan S-0265 | yes
|  | RDC_SB_L0_AT-3032 | AT | Open Plan S-0265
SB_GF_VAV3033 | 2 | RDC_SB_GF_VAV3033 | VAV | Corridor / Print / Emergency Elec Rm / Normal Elec Rm S-0251 / S-0263 / S-0266 / S-0267 | different room
|  | RDC_SB_L0_AT-3033 | AT | Emergency Elec. S-0266
SB_GF_VAV3034 | 2 | RDC_SB_GF_VAV3034 | VAV | Vestibule S-0293 | wording only
|  | RDC_SB_L0_AT-3034 | AT | Reception / Vestibule S-0293
SB_GF_VAV3035 | 2 | RDC_SB_GF_VAV3035 | VAV | Lobby S-0294 | yes
|  | RDC_SB_L0_AT-3035 | AT | Lobby S-0294
SB_GF_VAV3036 | 2 | RDC_SB_GF_VAV3036 | VAV | Lobby S-0294 | yes
|  | RDC_SB_L0_AT-3036 | AT | Lobby S-0294
SB_GF_VAV3501 | 1 | RDC_SB_GF_VAV3501 | VAV | Lobby S-0294 | yes
SB_GF_VAV3502 | 1 | RDC_SB_GF_VAV3502 | VAV | Lobby S-0294 | yes
SB_GF_VAV3503 | 1 | RDC_SB_GF_VAV3503 | VAV | Vestibule S-0293 | yes
NB_1F_VAV4510 | 1 | RDC_NB_1F_VAV4510 | VAV | Corridor N-1202A | yes
NB_1F_VAV4515_EV4516 | 1 | RDC_NB_1F_VAV4515_EV4516 | EV | Emergency Electrical Room N-1203 | yes
NB_1F_VAV4520_EV4521 | 1 | RDC_NB_1F_VAV4520_EV4521 | EV | Normal Electrical Room N-1204 | yes
NB_1F_VAV4525_EV4526 | 1 | RDC_NB_1F_VAV4525_EV4526 | EV | Conference Room N-1205 | yes | Conference Room N-1205 | this row
NB_1F_VAV4530_EV4531 | 1 | RDC_NB_1F_VAV4530_EV4531 | EV | Office N-1206 | yes | Office N-1206 | this row
NB_1F_VAV4535_EV4536 | 1 | RDC_NB_1F_VAV4535_EV4536 | EV | Office N-1207 | yes | Office N-1207 | this row
NB_1F_VAV4540_EV4541 | 1 | RDC_NB_1F_VAV4540_EV4541 | EV | Office N-1208 | yes | Office N-1208 | this row
NB_1F_VAV4545_EV4546 | 1 | RDC_NB_1F_VAV4545_EV4546 | EV | Office N-1209 | yes | Office N-1209 | this row
NB_1F_VAV4550_EV4551 | 1 | RDC_NB_1F_VAV4550_EV4551 | EV | Office N-1210 | yes | Office N-1210 | this row
NB_1F_VAV4555_EV4556 | 1 | RDC_NB_1F_VAV4555_EV4556 | EV | Confer Room N-1211 | yes
NB_1F_VAV4560_EV4561 | 1 | RDC_NB_1F_VAV4560_EV4561 | EV | Office N-1212 | yes | Office N-1212 | this row
NB_1F_VAV4565_EV4566 | 1 | RDC_NB_1F_VAV4565_EV4566 | EV | Conference N-1213 | yes | Storage Room N-1215 | this row
NB_1F_VAV4570_EV4571 | 1 | RDC_NB_1F_VAV4570_EV4571 | EV | Office 04 N-1214 | yes | Office N-1214 | this row
NB_1F_VAV4575_EV4576 | 1 | RDC_NB_1F_VAV4575_EV4576 | EV | Storage N-1215 | yes
NB_1F_VAV4580 | 1 | RDC_NB_1F_VAV4580 | VAV | Photovoltaic Lab N-1216A | yes
NB_1F_VAV4600 | 1 | RDC_NB_1F_VAV4600 | VAV | Testing Room N-1216B | yes
NB_1F_VAV4601 | 1 | RDC_NB_1F_VAV4601 | VAV | Testing Room N-1216B | yes
NB_1F_VAV4620_VEV4621 | 1 | RDC_NB_1F_VAV4620_VEV4621 | VEV | EL Shop N-1216C | yes
NB_1F_VAV4630_VEV4631 | 1 | RDC_NB_1F_VAV4630_VEV4631 | VEV | GIS N-1216D | yes | GIS N-1216D | this row
NB_1F_VAV4650 | 2 | RDC_NB_1F_VAV4650 | VAV | Breakout N-1225 | yes
|  | RDC_NB_1F_AT-4650 | AT | Breakout N-1225
NB_1F_VAV4660 | 2 | RDC_NB_1F_VAV4660 | VAV | Expansion Workstation N-1227 | yes
|  | RDC_NB_1F_AT-4660 | AT | Expansion Workstation N-1227
NB_1F_VAV4665 | 2 | RDC_NB_1F_VAV4665 | VAV | Office N-1228 | yes
|  | RDC_NB_1F_AT-4665 | AT | Office N-1228
NB_1F_VAV4670 | 1 | RDC_NB_1F_VAV4670 | VAV | Office N-1229 | yes
NB_1F_VAV4675 | 1 | RDC_NB_1F_VAV4675 | VAV | Office N-1230 | yes
NB_1F_VAV4680 | 2 | RDC_NB_1F_VAV4680 | VAV | Office N-1231 | yes
|  | RDC_NB_1F_AT-4680 | AT | Office N-1231
NB_1F_VAV4685 | 1 | RDC_NB_1F_VAV4685 | VAV | Workstation N-1232 | yes
NB_1F_VAV4690 | 2 | RDC_NB_1F_VAV4690 | VAV | Office N-1233 | yes
|  | RDC_NB_1F_AT-4690 | AT | Office N-1233
NB_1F_VAV4695 | 1 | RDC_NB_1F_VAV4695 | VAV | Office N-1234 | yes
NB_1F_VAV4700 | 1 | RDC_NB_1F_VAV4700 | VAV | Office N-1235 | yes
NB_1F_VAV4705 | 2 | RDC_NB_1F_VAV4705 | VAV | Office N-1236 | yes
|  | RDC_NB_1F_AT-4705 | AT | Office N-1236
NB_1F_VAV4710 | 1 | RDC_NB_1F_VAV4710 | VAV | Workstation N-1237 | yes
NB_1F_VAV4715 | 1 | RDC_NB_1F_VAV4715 | VAV | Office N-1238 | yes
NB_1F_VAV4720 | 2 | RDC_NB_1F_VAV4720 | VAV | Office N-1239 | yes
|  | RDC_NB_1F_AT-4720 | AT | Office N-1239
NB_1F_VAV4725 | 1 | RDC_NB_1F_VAV4725 | VAV | Office N-1240 | yes
NB_1F_VAV4730 | 2 | RDC_NB_1F_VAV4730 | VAV | Office N-1241 | yes
|  | RDC_NB_1F_AT-4730 | AT | Office N-1241
NB_1F_VAV4735 | 1 | RDC_NB_1F_VAV4735 | VAV | Workstation N-1242 | yes | Work Station N-1242 | this row
NB_1F_VAV4740 | 1 | RDC_NB_1F_VAV4740 | VAV | Exp Office N-1243 | yes | Office N-1244 | this row
NB_1F_VAV4745 | 2 | RDC_NB_1F_VAV4745 | VAV | Office N-1244 | yes
|  | RDC_NB_1F_AT-4745 | AT | Office N-1244
NB_1F_VAV4900P | 1 | RDC_NB_1F_VAV4900P | VAV | Normal Electric N-2102 | yes
NB_1F_VAV4910P | 1 | RDC_NB_1F_VAV4910P | VAV | Emergency Electr N-2103 | yes | Emer. Elec. N-2104 | this row
NB_1F_VAV5500 | 1 | RDC_NB_1F_VAV5500 | VAV | Lobby N-1101 | yes
NB_1F_VAV5501 | 1 | RDC_NB_1F_VAV5501 | VAV | Lobby N-1101 | yes
NB_1F_VAV5510_EV5511 | 1 | RDC_NB_1F_VAV5510_EV5511 | EV | Conference N-1101A | yes | Conference Room N-1101A | this row
NB_1F_VAV5515_EV5516 | 1 | RDC_NB_1F_VAV5515_EV5516 | EV | Emergency Electrical Room N-1102 | yes
NB_1F_VAV5520_EV5521 | 1 | RDC_NB_1F_VAV5520_EV5521 | EV | Conference N-1106 | yes
NB_1F_VAV5525_EV5526 | 1 | RDC_NB_1F_VAV5525_EV5526 | EV | Conference N-1107 | yes
NB_1F_VAV5535_EV5536 | 1 | RDC_NB_1F_VAV5535_EV5536 | EV | Conference N-1112 | yes
NB_1F_VAV5540_EV5541 | 1 | RDC_NB_1F_VAV5540_EV5541 | EV | Normal Electrical Room N-1113 | yes
NB_1F_VAV5550_VEV5551 | 1 | RDC_NB_1F_VAV5550_VEV5551 | VEV | PCR N-1115A | yes
NB_1F_VAV5560_VEV5561 | 1 | RDC_NB_1F_VAV5560_VEV5561 | VEV | PRE-PCR N-1115B | yes
NB_1F_VAV5570 | 1 | RDC_NB_1F_VAV5570 | VAV | Met/Prot Lab N-1115C | yes
NB_1F_VAV5571 | 1 | RDC_NB_1F_VAV5571 | VAV | Met/Prot Lab N-1115C | yes
NB_1F_VAV5580_VEV5581 | 1 | RDC_NB_1F_VAV5580_VEV5581 | VEV | DNA/RNA N-1115D | yes
NB_1F_VAV5590 | 1 | RDC_NB_1F_VAV5590 | VAV | Cell Culture N-1115E | yes
NB_1F_VAV5600_VEV5601 | 1 | RDC_NB_1F_VAV5600_VEV5601 | VEV | Library N-1115H | yes
NB_1F_VAV5610_VEV5611 | 1 | RDC_NB_1F_VAV5610_VEV5611 | VEV | Robotics N-1115J | yes | Cold Room N-1115F | this row
NB_1F_VAV5620_VEV5622 | 1 | RDC_NB_1F_VAV5620_VEV5622 | VEV | Sequence Lab N-1115K | yes
NB_1F_VAV5621_VEV5623 | 1 | RDC_NB_1F_VAV5621_VEV5623 | VEV | Sequence Lab N-1115K | yes
NB_1F_VAV5630_VEV5631 | 1 | RDC_NB_1F_VAV5630_VEV5631 | VEV | Genom Med Lab N-1115K1 | yes
NB_1F_VAV5650 | 2 | RDC_NB_1F_VAV5650 | VAV | Office N-1120 | yes
|  | RDC_NB_1F_AT-5650 | AT | Office N-1120
NB_1F_VAV5655_EV5656 | 2 | RDC_NB_1F_VAV5655_EV5656 | EV | Store N-1120B | yes
|  | RDC_NB_1F_AT-5655 | AT | Store N-1120B
NB_1F_VAV5660 | 2 | RDC_NB_1F_VAV5660 | VAV | Office N-1121 | yes | Office N-1121 | this row
|  | RDC_NB_1F_AT-5660 | AT | Office N-1121 |  | Office N-1121 | NB_1F_VAV5660
NB_1F_VAV5665 | 2 | RDC_NB_1F_VAV5665 | VAV | Office N-1122 | yes
|  | RDC_NB_1F_AT-5665 | AT | Office N-1122
NB_1F_VAV5670 | 2 | RDC_NB_1F_VAV5670 | VAV | Office N-1123 | yes | Office N-1123 | this row
|  | RDC_NB_1F_AT-5670 | AT | Office N-1123 |  | Office N-1123 | NB_1F_VAV5670
NB_1F_VAV5675 | 2 | RDC_NB_1F_VAV5675 | VAV | Office N-1124 | yes
|  | RDC_NB_1F_AT-5675 | AT | Office N-1124
NB_1F_VAV5680 | 2 | RDC_NB_1F_VAV5680 | VAV | Office N-1125 | yes | Office N-1125 | this row
|  | RDC_NB_1F_AT-5680 | AT | Office N-1125 |  | Office N-1125 | NB_1F_VAV5680
NB_1F_VAV5685 | 2 | RDC_NB_1F_VAV5685 | VAV | Corridor N-1126 | yes
|  | RDC_NB_1F_AT-5685 | AT | Corridor N-1126
NB_1F_VAV5690 | 2 | RDC_NB_1F_VAV5690 | VAV | Office N-1127 | yes
|  | RDC_NB_1F_AT-5690 | AT | Office N-1127
NB_1F_VAV5695 | 2 | RDC_NB_1F_VAV5695 | VAV | Office N-1128 | yes | Office N-1128 | this row
|  | RDC_NB_1F_AT-5695 | AT | Office N-1128 |  | Office N-1128 | NB_1F_VAV5695
NB_1F_VAV5700 | 2 | RDC_NB_1F_VAV5700 | VAV | Office N-1129 | yes
|  | RDC_NB_1F_AT-5700 | AT | Office N-1129
NB_1F_VAV5705 | 2 | RDC_NB_1F_VAV5705 | VAV | Office N-1130 | yes
|  | RDC_NB_1F_AT-5705 | AT | Office N-1130
NB_1F_VAV5710 | 2 | RDC_NB_1F_VAV5710 | VAV | Office N-1131 | yes
|  | RDC_NB_1F_AT-5710 | AT | Office N-1131
NB_1F_VAV5715_EV5716 | 2 | RDC_NB_1F_VAV5715_EV5716 | EV | Conf Rm N-1132 | yes | Conf. Rm N-1132 | this row
|  | RDC_NB_1F_AT-5715 | AT | Conf Rm N-1132 |  | Conf. Rm N-1132 | NB_1F_VAV5715_EV5716
NB_1F_VAV5730_EV5731 | 2 | RDC_NB_1F_VAV5730_EV5731 | EV | Store N-1135 | yes | Store N-1135 | this row
|  | RDC_NB_1F_AT-5730 | AT | Store N-1135 |  | Store N-1135 | NB_1F_VAV5730_EV5731
NB_1F_VAV5735_EV5736 | 2 | RDC_NB_1F_VAV5735_EV5736 | EV | Normal Elec. N-1136 | yes
|  | RDC_NB_1F_AT-5735 | AT | Normal Elec. N-1136
NB_1F_VAV5740_EV5741 | 2 | RDC_NB_1F_VAV5740_EV5741 | EV | Emer. Elec. N-1137 | yes | Emer. Elec. N-1137 | this row
|  | RDC_NB_1F_AT-5740 | AT | Emer. Elec. N-1137 |  | Emer. Elec. N-1137 | NB_1F_VAV5740_EV5741
NB_1F_VAV5745 | 2 | RDC_NB_1F_VAV5745 | VAV | Corridor N-1138 | yes
|  | RDC_NB_1F_AT-5745 | AT | Corridor N-1138
NB_1F_VAV5760_EV5761 | 2 | RDC_NB_1F_VAV5760_EV5761 | EV | Conf N-1143 | yes
|  | RDC_NB_1F_AT-5760 | AT | Conf N-1143
NB_1F_VAV5770_VEV5771 | 1 | RDC_NB_1F_VAV5770_VEV5771 | VEV | Histology N-1144A | yes
NB_1F_VAV5780_VEV5781 | 1 | RDC_NB_1F_VAV5780_VEV5781 | VEV | Culture & Gel Rm N-1144B | yes
NB_1F_VAV5790 | 1 | RDC_NB_1F_VAV5790 | VAV | Shafallah N-1144C | yes
NB_1F_VAV5792_VEV5793 | 1 | RDC_NB_1F_VAV5792_VEV5793 | VEV | Sample Accession N-1144C1 | yes
NB_1F_VAV5794_VEV5795A | 1 | RDC_NB_1F_VAV5794_VEV5795A | VAV | Storage and Archives N-1144C2 | yes
NB_1F_VAV5800_VEV5801 | 1 | RDC_NB_1F_VAV5800_VEV5801 | VEV | Pre-PCR N-1144D | yes
NB_1F_VAV5810 | 1 | RDC_NB_1F_VAV5810 | VAV | Nano Lab N-1144E | yes
NB_1F_VAV5814 | 1 | RDC_NB_1F_VAV5814 | VAV | Nano Lab N-1144E | yes
NB_1F_VAV5835_EV5836 | 2 | RDC_NB_1F_VAV5835_EV5836 | EV | P/C/S Pantry N-1146 | yes
|  | RDC_NB_1F_AT-5835 | AT | P/C/S Pantry N-1146
NB_1F_VAV5840 | 2 | RDC_NB_1F_VAV5840 | VAV | Corridor N-1150 | yes
|  | RDC_NB_1F_AT-5840 | AT | Corridor N-1150
NB_1F_VAV5845 | 1 | RDC_NB_1F_VAV5845 | VAV | Reception+N-1151B Storage N-1151 | yes
NB_1F_VAV5850 | 1 | RDC_NB_1F_VAV5850 | VAV | Office 04 N-1151A | yes
NB_1F_VAV5855 | 1 | RDC_NB_1F_VAV5855 | VAV | Office 04 N-1152 | yes
NB_1F_VAV5860 | 2 | RDC_NB_1F_VAV5860 | VAV | Office N-1154 | yes
|  | RDC_NB_1F_AT-5860 | AT | Office N-1154
NB_1F_VAV5865 | 2 | RDC_NB_1F_VAV5865 | VAV | Office N-1155 | yes
|  | RDC_NB_1F_AT-5865 | AT | Office N-1155
NB_1F_VAV5870 | 2 | RDC_NB_1F_VAV5870 | VAV | Exp Office N-1156 | yes
|  | RDC_NB_1F_AT-5870 | AT | Exp Office N-1156
NB_1F_VAV5875 | 2 | RDC_NB_1F_VAV5875 | VAV | Office N-1157 | yes
|  | RDC_NB_1F_AT-5875 | AT | Office N-1157
NB_1F_VAV5880 | 2 | RDC_NB_1F_VAV5880 | VAV | Office N-1158 | yes
|  | RDC_NB_1F_AT-5880 | AT | Office N-1158
NB_1F_VAV5885 | 2 | RDC_NB_1F_VAV5885 | VAV | Office N-1159 | yes
|  | RDC_NB_1F_AT-5885 | AT | Office N-1159
NB_1F_VAV5890 | 2 | RDC_NB_1F_VAV5890 | VAV | Workstation N-1160 | yes
|  | RDC_NB_1F_AT-5890 | AT | Workstation N-1160
NB_1F_VAV5895 | 2 | RDC_NB_1F_VAV5895 | VAV | Office N-1161 | yes
|  | RDC_NB_1F_AT-5895 | AT | Office N-1161
NB_1F_VAV5900 | 2 | RDC_NB_1F_VAV5900 | VAV | Office N-1162 | yes
|  | RDC_NB_1F_AT-5900 | AT | Office N-1162
NB_1F_VAV5905 | 2 | RDC_NB_1F_VAV5905 | VAV | Office N-1163 | yes
|  | RDC_NB_1F_AT-5905 | AT | Office N-1163
NB_1F_VAV5910 | 2 | RDC_NB_1F_VAV5910 | VAV | Office N-1164 | yes
|  | RDC_NB_1F_AT-5910 | AT | Office N-1164
NB_1F_VAV5915 | 2 | RDC_NB_1F_VAV5915 | VAV | Office N-1167 | yes
|  | RDC_NB_1F_AT-5915 | AT | Office N-1167
NB_1F_VAV5920 | 2 | RDC_NB_1F_VAV5920 | VAV | Workstation N-1168 | yes
|  | RDC_NB_1F_AT-5920 | AT | Workstation N-1168
NB_1F_VAV5925 | 2 | RDC_NB_1F_VAV5925 | VAV | Office N-1169 | yes
|  | RDC_NB_1F_AT-5925 | AT | Office N-1169
NB_1F_VAV5930 | 2 | RDC_NB_1F_VAV5930 | VAV | Office N-1170 | yes
|  | RDC_NB_1F_AT-5930 | AT | Office N-1170
NB_1F_VAV5930P | 1 | RDC_NB_1F_VAV5930P | VAV | Normal Elec. N-2105 | yes
NB_1F_VAV5935 | 2 | RDC_NB_1F_VAV5935 | VAV | Office N-1166 | yes
|  | RDC_NB_1F_AT-5935 | AT | Office N-1166
NB_1F_VAV5940 | 2 | RDC_NB_1F_VAV5940 | VAV | Workstation N-1165 | yes
|  | RDC_NB_1F_AT-5940 | AT | Workstation N-1165
NB_1F_VAV5940P | 1 | RDC_NB_1F_VAV5940P | VAV | Emer. Elec. N-2106 | yes
NB_1F_VAV6505_EV6506 | 1 | RDC_NB_1F_VAV6505_EV6506 | EV | Conference N-1302 | yes
NB_1F_VAV6510_EV6511 | 1 | RDC_NB_1F_VAV6510_EV6511 | EV | Conference N-1303 | yes
NB_1F_VAV6525_EV6526 | 1 | RDC_NB_1F_VAV6525_EV6526 | EV | Normal Electrical Room N-1310 | yes
NB_1F_VAV6530_VEV6531 | 1 | RDC_NB_1F_VAV6530_VEV6531 | VEV | AAV N-1316A | yes
NB_1F_VAV6540 | 1 | RDC_NB_1F_VAV6540 | VAV | Tissure Culture 1 N-1316B | yes
NB_1F_VAV6550 | 1 | RDC_NB_1F_VAV6550 | VAV | Gene Therapy Lab N-1316C | yes
NB_1F_VAV6551 | 1 | RDC_NB_1F_VAV6551 | VAV | Gene Therapy Lab N-1316C | yes
NB_1F_VAV6560_VEV6561 | 1 | RDC_NB_1F_VAV6560_VEV6561 | VEV | TC2 N-1316D | yes
NB_1F_VAV6570_VEV6571 | 1 | RDC_NB_1F_VAV6570_VEV6571 | VEV | STORE ROOM N-1316E | yes
NB_1F_VAV6590_VEV6591 | 1 | RDC_NB_1F_VAV6590_VEV6591 | VEV | LENTIV N-1316G | yes
NB_1F_VAV6600_VEV6601 | 1 | RDC_NB_1F_VAV6600_VEV6601 | VEV | Analytical Core N-1316H | yes
NB_1F_VAV6610_VEV6611 | 1 | RDC_NB_1F_VAV6610_VEV6611 | VEV | Microscope Room N-1316H | yes
NB_1F_VAV6620_VEV6621 | 1 | RDC_NB_1F_VAV6620_VEV6621 | VEV | Mscopy1 N-1316K | yes
NB_1F_VAV6630A | 1 | RDC_NB_1F_VAV6630A | VAV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_VAV6630B | 1 | RDC_NB_1F_VAV6630B | VAV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_VAV6631A | 1 | RDC_NB_1F_VAV6631A | VAV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_VAV6631B | 1 | RDC_NB_1F_VAV6631B | VAV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_VAV6650 | 2 | RDC_NB_1F_VAV6650 | VAV | Office N-1319 | yes
|  | RDC_NB_1F_AT-6650 | AT | Office N-1319
NB_1F_VAV6655 | 2 | RDC_NB_1F_VAV6655 | VAV | Office N-1320 | yes
|  | RDC_NB_1F_AT-6655 | AT | Office N-1320
NB_1F_VAV6660 | 2 | RDC_NB_1F_VAV6660 | VAV | Workstation N-1321 | yes
|  | RDC_NB_1F_AT-6660 | AT | Workstation N-1321
NB_1F_VAV6665 | 2 | RDC_NB_1F_VAV6665 | VAV | Office N-1322 | yes
|  | RDC_NB_1F_AT-6665 | AT | Office N-1322
NB_1F_VAV6670 | 2 | RDC_NB_1F_VAV6670 | VAV | Office N-1323 | yes
|  | RDC_NB_1F_AT-6670 | AT | Office N-1323
NB_1F_VAV6675 | 2 | RDC_NB_1F_VAV6675 | VAV | Workstation N-1324 | yes
|  | RDC_NB_1F_AT-6675 | AT | Workstation N-1324
NB_1F_VAV6680 | 2 | RDC_NB_1F_VAV6680 | VAV | Office N-1325 | yes
|  | RDC_NB_1F_AT-6680 | AT | Office N-1325
NB_1F_VAV6685 | 2 | RDC_NB_1F_VAV6685 | VAV | Office N-1326 | yes
|  | RDC_NB_1F_AT-6685 | AT | Office N-1326
NB_1F_VAV6690 | 2 | RDC_NB_1F_VAV6690 | VAV | Exp. Workstation N-1327 | yes
|  | RDC_NB_1F_AT-6690 | AT | Exp. Workstation N-1327
NB_1F_VAV6695 | 2 | RDC_NB_1F_VAV6695 | VAV | Office N-1328 | yes
|  | RDC_NB_1F_AT-6695 | AT | Office N-1328
NB_1F_VAV6700_EV6701 | 2 | RDC_NB_1F_VAV6700_EV6701 | EV | NORMAL ELEC. N-1329 | yes
|  | RDC_NB_1F_AT-6700 | AT | NORMAL ELEC. N-1329
NB_1F_VAV6705 | 2 | RDC_NB_1F_VAV6705 | VAV | Office N-1330 | yes
|  | RDC_NB_1F_AT-6705 | AT | Office N-1330
NB_1F_VAV6710 | 2 | RDC_NB_1F_VAV6710 | VAV | Office N-1331 | yes
|  | RDC_NB_1F_AT-6710 | AT | Office N-1331
NB_1F_VAV6715 | 2 | RDC_NB_1F_VAV6715 | VAV | Office N-1332 | yes
|  | RDC_NB_1F_AT-6715 | AT | Office N-1332
NB_1F_VAV6720 | 2 | RDC_NB_1F_VAV6720 | VAV | Corridor N-1335 | yes
|  | RDC_NB_1F_AT-6720 | AT | Corridor N-1335
NB_1F_VAV6725_EV6726 | 2 | RDC_NB_1F_VAV6725_EV6726 | EV | Emer. Elec. N-1336 | yes
|  | RDC_NB_1F_AT-6725 | AT | Emer. Elec. N-1336
NB_1F_VAV6750 | 1 | RDC_NB_1F_VAV6750 | VAV | Tissue Culture 1 N-1345A | yes
NB_1F_VAV6760 | 1 | RDC_NB_1F_VAV6760 | VAV | Diabetes Lab N-1345B | yes
NB_1F_VAV6761 | 1 | RDC_NB_1F_VAV6761 | VAV | Diabetes Lab N-1345B | yes
NB_1F_VAV6800_VEV6801 | 1 | RDC_NB_1F_VAV6800_VEV6801 | VEV | Tissue Culture 3 N-1345D | yes
NB_1F_VAV6810_VEV6811 | 1 | RDC_NB_1F_VAV6810_VEV6811 | VEV | Calc Imaging N-1345E | yes
NB_1F_VAV6820_VEV6821 | 1 | RDC_NB_1F_VAV6820_VEV6821 | VEV | Electro Physics N-1345F | yes
NB_1F_VAV6830_VEV6831 | 2 | RDC_NB_1F_VAV6830_VEV6831 | VEV | Shared Cold Lab N-1345G | yes
|  | RDC_NB_1F_CEV-6831 | CEV | SHARED COLD LAB N-1345G
NB_1F_VAV6840_VEV6841 | 1 | RDC_NB_1F_VAV6840_VEV6841 | VEV | Bacterlgy Lab N-1345H | yes
NB_1F_VAV6850 | 1 | RDC_NB_1F_VAV6850 | VAV | Bio-Med Chem Lab 2 N-1345J | yes
NB_1F_VAV6851 | 1 | RDC_NB_1F_VAV6851 | VAV | Bio-Med Chem Lab 2 N-1345J | yes
NB_1F_VAV6870_EV6871 | 1 | RDC_NB_1F_VAV6870_EV6871 | EV | Emergency Electrical Room N-1353 | yes
NB_1F_VAV6880 | 1 | RDC_NB_1F_VAV6880 | VAV | Reception+N-1355C Storage N-1355 | yes
NB_1F_VAV6885 | 1 | RDC_NB_1F_VAV6885 | VAV | Office 04 N-1355A | yes
NB_1F_VAV6890_EV6891 | 1 | RDC_NB_1F_VAV6890_EV6891 | EV | Conference Room N-1355B | yes
NB_1F_VAV6895 | 1 | RDC_NB_1F_VAV6895 | VAV | Office 04 N-1356 | yes
NB_1F_VAV6900 | 2 | RDC_NB_1F_VAV6900 | VAV | Office N-1357 | yes | Office N-357 | this row
|  | RDC_NB_1F_AT-6900 | AT | Office N-1357 |  | Office N-357 | NB_1F_VAV6900
NB_1F_VAV6905 | 2 | RDC_NB_1F_VAV6905 | VAV | Open Plan N-1358 | yes
|  | RDC_NB_1F_AT-6905 | AT | Open Plan N-1358
NB_1F_VAV6910 | 2 | RDC_NB_1F_VAV6910 | VAV | Office N-1359 | yes | Office N-359 | this row
|  | RDC_NB_1F_AT-6910 | AT | Office N-1359 |  | Office N-359 | NB_1F_VAV6910
NB_1F_VAV6915 | 2 | RDC_NB_1F_VAV6915 | VAV | Office N-1360 | yes | Office N-360 | this row
|  | RDC_NB_1F_AT-6915 | AT | Office N-1360 |  | Office N-360 | NB_1F_VAV6915
NB_1F_VAV6920 | 2 | RDC_NB_1F_VAV6920 | VAV | Office N-1360B | yes | Office N-360B | this row
|  | RDC_NB_1F_AT-6920 | AT | Office N-1360B |  | Office N-360B | NB_1F_VAV6920
NB_1F_VAV6925 | 2 | RDC_NB_1F_VAV6925 | VAV | Office N-1361 | yes
|  | RDC_NB_1F_AT-6925 | AT | Office N-1361
NB_1F_VAV6930 | 2 | RDC_NB_1F_VAV6930 | VAV | Office N-1362 | yes
|  | RDC_NB_1F_AT-6930 | AT | Office N-1362
NB_1F_VAV6935 | 2 | RDC_NB_1F_VAV6935 | VAV | Workstation N-1363 | yes
|  | RDC_NB_1F_AT-6935 | AT | Workstation N-1363
NB_1F_VAV6940 | 2 | RDC_NB_1F_VAV6940 | VAV | Office N-1364 | yes
|  | RDC_NB_1F_AT-6940 | AT | Office N-1364
NB_1F_VAV6945 | 2 | RDC_NB_1F_VAV6945 | VAV | Office N-1365 | yes
|  | RDC_NB_1F_AT-6945 | AT | Office N-1365
NB_1F_VAV6950 | 2 | RDC_NB_1F_VAV6950 | VAV | Office N-1366 | yes
|  | RDC_NB_1F_AT-6950 | AT | Office N-1366
NB_1F_VAV6955 | 2 | RDC_NB_1F_VAV6955 | VAV | Office N-1367 | yes
|  | RDC_NB_1F_AT-6955 | AT | Office N-1367
NB_1F_VAV6960 | 2 | RDC_NB_1F_VAV6960 | VAV | Workstation N-1368 | yes
|  | RDC_NB_1F_AT-6960 | AT | Workstation N-1368
NB_1F_VAV6965 | 2 | RDC_NB_1F_VAV6965 | VAV | Office N-1369 | yes
|  | RDC_NB_1F_AT-6965 | AT | Office N-1369
NB_1F_VAV6967 | 2 | RDC_NB_1F_VAV6967 | VAV | Office N-1370 | yes
|  | RDC_NB_1F_AT-6967 | AT | Office N-1370
NB_1F_VAV6968 | 2 | RDC_NB_1F_VAV6968 | VAV | Workstation N-1371 | yes
|  | RDC_NB_1F_AT-6968 | AT | Workstation N-1371
NB_1F_VAV6970_EV6971 | 2 | RDC_NB_1F_VAV6970_EV6971 | EV | PANTRY N-1372 | yes
|  | RDC_NB_1F_AT-6970 | AT | PANTRY N-1372
NB_1F_VAV6972 | 1 | RDC_NB_1F_VAV6972 | VAV | Office N-1374 | yes
NB_1F_VAV6974 | 1 | RDC_NB_1F_VAV6974 | VAV | Office N-1375 | yes
NB_1F_VAV6976 | 1 | RDC_NB_1F_VAV6976 | VAV | Office N-1376 | yes
NB_1F_VAV6978 | 1 | RDC_NB_1F_VAV6978 | VAV | Office N-1377 | yes
NB_1F_VAV6979P | 1 | RDC_NB_1F_VAV6979P | VAV | Normal Elec. N-2107 | yes
NB_1F_VAV6980P | 1 | RDC_NB_1F_VAV6980P | VAV | Emer. Elec. N-2108 | yes | IDF N-2110 | this row
NB_1F_VAV7510_VEV7511 | 1 | RDC_NB_1F_VAV7510_VEV7511 | VEV | TC1 N-1404A | yes
NB_1F_VAV7530_VEV7532 | 1 | RDC_NB_1F_VAV7530_VEV7532 | VEV | Cell Bio N-1404C | yes
NB_1F_VAV7531_VEV7533 | 1 | RDC_NB_1F_VAV7531_VEV7533 | VEV | Cell Bio N-1404C | yes
NB_1F_VAV7540_VEV7541 | 1 | RDC_NB_1F_VAV7540_VEV7541 | VEV | Shared Eq Rm N-1404D | yes
NB_1F_VAV7550_VEV7551 | 1 | RDC_NB_1F_VAV7550_VEV7551 | VEV | TC2 N-1404E | yes
NB_1F_VAV7560_VEV7561 | 1 | RDC_NB_1F_VAV7560_VEV7561 | VEV | Imaging N-1404F | yes | Imaging N-404F | this row
NB_1F_VAV7570_VEV7571 | 1 | RDC_NB_1F_VAV7570_VEV7571 | VEV | Cell Bio Lab2 N-1404G | yes
NB_1F_VAV7580_VEV7581 | 2 | RDC_NB_1F_VAV7580_VEV7581 | VEV | TC3 N-1404H | yes
|  | RDC_NB_1F_CEV-7581 | CEV | TC3 N-1404H
NB_1F_VAV7600_VEV7601 | 1 | RDC_NB_1F_VAV7600_VEV7601 | VEV | Cell Bio Lab3 N-1404K | yes
NB_1F_VAV7620 | 2 | RDC_NB_1F_VAV7620 | VAV | Office N-1415 | yes
|  | RDC_NB_1F_AT-7620 | AT | Office N-1415
NB_1F_VAV7625 | 2 | RDC_NB_1F_VAV7625 | VAV | Office N-1416 | yes
|  | RDC_NB_1F_AT-7625 | AT | Office N-1416
NB_1F_VAV7630 | 2 | RDC_NB_1F_VAV7630 | VAV | Office 05 - 2 WKS- N-1407 | yes
|  | RDC_NB_1F_AT-7630 | AT | Office 05 - 2 WKS- N-1407
NB_1F_VAV7635 | 2 | RDC_NB_1F_VAV7635 | VAV | Office N-1418 | yes
|  | RDC_NB_1F_AT-7635 | AT | Office N-1418
NB_1F_VAV7640 | 2 | RDC_NB_1F_VAV7640 | VAV | Office N-1419 | yes
|  | RDC_NB_1F_AT-7640 | AT | Office N-1419
NB_1F_VAV7645 | 2 | RDC_NB_1F_VAV7645 | VAV | Exp. Workstation N-1420 | yes
|  | RDC_NB_1F_AT-7645 | AT | Exp. Workstation N-1420
NB_1F_VAV7650 | 2 | RDC_NB_1F_VAV7650 | VAV | Office N-1421 | yes
|  | RDC_NB_1F_AT-7650 | AT | Office N-1421
NB_1F_VAV7655 | 2 | RDC_NB_1F_VAV7655 | VAV | Office N-1422 | yes
|  | RDC_NB_1F_AT-7655 | AT | Office N-1422
NB_1F_VAV7660 | 2 | RDC_NB_1F_VAV7660 | VAV | Office 05 - 2 WKS- N-1401 | yes | Workstation N-1423 | this row
|  | RDC_NB_1F_AT-7660 | AT | Office 05 - 2 WKS- N-1401 |  | Workstation N-1423 | NB_1F_VAV7660
NB_1F_VAV7665_EV7666 | 2 | RDC_NB_1F_VAV7665_EV7666 | EV | Normal Elec. N-1425 | yes
|  | RDC_NB_1F_AT-7665 | AT | Normal Elec. N-1425
NB_1F_VAV7670 | 2 | RDC_NB_1F_VAV7670 | VAV | Office N-1426 | yes
|  | RDC_NB_1F_AT-7670 | AT | Office N-1426
NB_1F_VAV7675 | 2 | RDC_NB_1F_VAV7675 | VAV | Office N-1428 | yes
|  | RDC_NB_1F_AT-7675 | AT | Office N-1428
NB_1F_VAV7680_EV7681 | 2 | RDC_NB_1F_VAV7680_EV7681 | EV | Conf N-1429 | yes
|  | RDC_NB_1F_AT-7680 | AT | Conf N-1429
NB_1F_VAV7685 | 2 | RDC_NB_1F_VAV7685 | VAV | Office N-1433 | yes
|  | RDC_NB_1F_AT-7685 | AT | Office N-1433
NB_1F_VAV7690 | 2 | RDC_NB_1F_VAV7690 | VAV | Office N-1435 | yes
|  | RDC_NB_1F_AT-7690 | AT | Office N-1435
NB_1F_VAV7695 | 2 | RDC_NB_1F_VAV7695 | VAV | Office N-1437 | yes
|  | RDC_NB_1F_AT-7695 | AT | Office N-1437
NB_1F_VAV7700_EV7701 | 2 | RDC_NB_1F_VAV7700_EV7701 | EV | Emer. Elec. N-1438 | yes
|  | RDC_NB_1F_AT-7700 | AT | Emer. Elec. N-1438
NB_1F_VAV7705 | 2 | RDC_NB_1F_VAV7705 | VAV | Office 05 - 24 WKS + N-1441 Room N-1442 | different room
|  | RDC_NB_1F_AT-7705 | AT | Expansion WORKstation N-1442
NB_1F_VAV7710 | 2 | RDC_NB_1F_VAV7710 | VAV | Workstation N-1442 | different room
|  | RDC_NB_1F_AT-7710 | AT | Office 05 - 24 WKS + N-1441 Room N-1442
NB_1F_VAV7730_VEV7731 | 1 | RDC_NB_1F_VAV7730_VEV7731 | VEV | Microscope 2 N-1450A | yes
NB_1F_VAV7740_VEV7741 | 1 | RDC_NB_1F_VAV7740_VEV7741 | VEV | LN2 Stor N-1450B | yes
NB_1F_VAV7750_VEV7751 | 1 | RDC_NB_1F_VAV7750_VEV7751 | VEV | Flow Cyto N-1450C | yes
NB_1F_VAV7770_VEV7771 | 1 | RDC_NB_1F_VAV7770_VEV7771 | VEV | Qurnt N-1450E | yes
NB_1F_VAV7780_VEV7781 | 1 | RDC_NB_1F_VAV7780_VEV7781 | VEV | iPS-TC N-1450F | yes
NB_1F_VAV7800_VEV7801 | 1 | RDC_NB_1F_VAV7800_VEV7801 | VEV | IPS TISSUE CULTURE N-1450J | yes | IPS Tissue Culture N-450J | this row
NB_1F_VAV7810_VEV7811 | 1 | RDC_NB_1F_VAV7810_VEV7811 | VEV | TC1 N-1450L | yes
NB_1F_VAV7820_VEV7822 | 1 | RDC_NB_1F_VAV7820_VEV7822 | VEV | STEM/PCR Open Lab N-1450M | yes
NB_1F_VAV7821_VEV7823 | 1 | RDC_NB_1F_VAV7821_VEV7823 | VEV | STEM/PCR Open Lab N-1450M | yes | STEM/PCR Open Lab N-450M | this row
NB_1F_VAV7830_VEV7831 | 1 | RDC_NB_1F_VAV7830_VEV7831 | VEV | TC2 N-1450N | yes
NB_1F_VAV7840_EV7841 | 2 | RDC_NB_1F_VAV7840_EV7841 | EV | Conf N-1458 | yes
|  | RDC_NB_1F_AT-7840 | AT | Conf N-1458
NB_1F_VAV7845_EV7846 | 2 | RDC_NB_1F_VAV7845_EV7846 | EV | Conf N-1459 | yes
|  | RDC_NB_1F_AT-7845 | AT | Conf N-1459
NB_1F_VAV7850 | 2 | RDC_NB_1F_VAV7850 | VAV | Office N-1459A | yes
|  | RDC_NB_1F_AT-7850 | AT | Office N-1459A
NB_1F_VAV7860 | 2 | RDC_NB_1F_VAV7860 | VAV | Exp. Workstation N-1461 | yes
|  | RDC_NB_1F_AT-7860 | AT | Exp. Workstation N-1461
NB_1F_VAV7865 | 2 | RDC_NB_1F_VAV7865 | VAV | Workstation N-1461A | yes
|  | RDC_NB_1F_AT-7865 | AT | Workstation N-1461A
NB_1F_VAV7870 | 2 | RDC_NB_1F_VAV7870 | VAV | Office N-1462 | yes
|  | RDC_NB_1F_AT-7870 | AT | Office N-1462
NB_1F_VAV7875 | 2 | RDC_NB_1F_VAV7875 | VAV | Office N-1463 | yes
|  | RDC_NB_1F_AT-7875 | AT | Office N-1463
NB_1F_VAV7880 | 2 | RDC_NB_1F_VAV7880 | VAV | Office N-1464 | yes
|  | RDC_NB_1F_AT-7880 | AT | Office N-1464
NB_1F_VAV7885 | 2 | RDC_NB_1F_VAV7885 | VAV | Office N-1465 | yes
|  | RDC_NB_1F_AT-7885 | AT | Office N-1465
NB_1F_VAV7890 | 2 | RDC_NB_1F_VAV7890 | VAV | Workstation N-1466 | yes
|  | RDC_NB_1F_AT-7890 | AT | Workstation N-1466
NB_1F_VAV7895 | 2 | RDC_NB_1F_VAV7895 | VAV | Office N-1467 | yes
|  | RDC_NB_1F_AT-7895 | AT | Office N-1467
NB_1F_VAV7900 | 2 | RDC_NB_1F_VAV7900 | VAV | Office N-1468 | yes
|  | RDC_NB_1F_AT-7900 | AT | Office N-1468
NB_1F_VAV7905 | 2 | RDC_NB_1F_VAV7905 | VAV | Office N-1469 | yes
|  | RDC_NB_1F_AT-7905 | AT | Office N-1469
NB_1F_VAV7910 | 2 | RDC_NB_1F_VAV7910 | VAV | Office N-1470 | yes
|  | RDC_NB_1F_AT-7910 | AT | Office N-1470
NB_1F_VAV7915 | 2 | RDC_NB_1F_VAV7915 | VAV | Workstation N-1471 | yes
|  | RDC_NB_1F_AT-7915 | AT | Workstation N-1471
NB_1F_VAV7920 | 2 | RDC_NB_1F_VAV7920 | VAV | Office N-1472 | yes
|  | RDC_NB_1F_AT-7920 | AT | Office N-1472
NB_1F_VAV7925 | 2 | RDC_NB_1F_VAV7925 | VAV | Office N-1473 | yes
|  | RDC_NB_1F_AT-7925 | AT | Office N-1473
NB_1F_VAV7930 | 2 | RDC_NB_1F_VAV7930 | VAV | Office N-1474 | yes
|  | RDC_NB_1F_AT-7930 | AT | Office N-1474
NB_1F_VAV7935 | 2 | RDC_NB_1F_VAV7935 | VAV | Office N-1475 | yes
|  | RDC_NB_1F_AT-7935 | AT | Office N-1475
NB_1F_VAV7940 | 2 | RDC_NB_1F_VAV7940 | VAV | Workstation N-1476 | yes
|  | RDC_NB_1F_AT-7940 | AT | Workstation N-1476
NB_1F_VAV7945 | 2 | RDC_NB_1F_VAV7945 | VAV | Office N-1477 | yes
|  | RDC_NB_1F_AT-7945 | AT | Office N-1477
NB_1F_VAV7950 | 2 | RDC_NB_1F_VAV7950 | VAV | Office N-1478 | yes
|  | RDC_NB_1F_AT-7950 | AT | Office N-1478
NB_1F_VAV7955 | 2 | RDC_NB_1F_VAV7955 | VAV | Office N-1479 | yes
|  | RDC_NB_1F_AT-7955 | AT | Office N-1479
NB_1F_VAV7960 | 2 | RDC_NB_1F_VAV7960 | VAV | Office N-1480 | yes
|  | RDC_NB_1F_AT-7960 | AT | Office N-1480
NB_1F_VAV7975P | 1 | RDC_NB_1F_VAV7975P | VAV | Normal Elec. N-2111 | yes
NB_1F_VAV7980P | 1 | RDC_NB_1F_VAV7980P | VAV | Emer. Elec. N-2112 | yes
NB_1F_FCU4910 | 1 | RDC_NB_1F_FCU4910 | FCU | Stair 1 N-1ST01 | yes
NB_1F_FCU4914 | 1 | RDC_NB_1F_FCU4914 | FCU | Mech/ FPC N- L1 A2.1 | yes
NB_1F_FCU4915 | 1 | RDC_NB_1F_FCU4915 | FCU | MDF N-1201 | yes
NB_1F_FCU4916 | 1 | RDC_NB_1F_FCU4916 | FCU | Stair 1 N-1ST01 | yes
NB_1F_FCU4917 | 1 | RDC_NB_1F_FCU4917 | FCU | Stair N-1ST02 | yes
NB_1F_FCU5983 | 1 | RDC_NB_1F_FCU5983 | FCU | IDF N-1140 | yes
NB_1F_FCU5984 | 1 | RDC_NB_1F_FCU5984 | FCU | ROBOTICS N-115J | yes
NB_1F_FCU5985 | 1 | RDC_NB_1F_FCU5985 | FCU | Corridor N-1142 | yes
NB_1F_FCU5986 | 1 | RDC_NB_1F_FCU5986 | FCU | Corridor N-1142 | yes
NB_1F_FCU5987 | 1 | RDC_NB_1F_FCU5987 | FCU | Stair 3 N-L1 A2.3 | yes
NB_1F_FCU5993 | 1 | RDC_NB_1F_FCU5993 | FCU | Conference Room N-L0 A2.2 | yes
NB_1F_FCU5994 | 1 | RDC_NB_1F_FCU5994 | FCU | Conference Room N-L0 A2.2 | yes
NB_1F_FCU6988 | 1 | RDC_NB_1F_FCU6988 | FCU | Service Corridor N-1337 | yes | Service Corridor N-337 | this row
NB_1F_FCU6989 | 1 | RDC_NB_1F_FCU6989 | FCU | Service Corridor N-1337 | yes | Service Corridor N-337 | this row
NB_1F_FCU6990 | 1 | RDC_NB_1F_FCU6990 | FCU | Mech/ FPC N-L1 A2.3 | yes
NB_1F_FCU6991 | 1 | RDC_NB_1F_FCU6991 | FCU | Mech/ FPC N-L1 A2.3 | yes
NB_1F_FCU6992 | 1 | RDC_NB_1F_FCU6992 | FCU | Stair 4 N-L1 A2.3 | yes
NB_1F_FCU7790 | 1 | RDC_NB_1F_FCU7790 | FCU | Stair 6 N-1ST06 | yes
NB_1F_FCU7984 | 1 | RDC_NB_1F_FCU7984 | FCU | Stair 6 N-1ST06 | yes
NB_1F_FCU7985 | 1 | RDC_NB_1F_FCU7985 | FCU | IDF N-1424 | yes
NB_1F_FCU7986 | 1 | RDC_NB_1F_FCU7986 | FCU | IDF N-1424 | yes
NB_1F_FCU7987 | 1 | RDC_NB_1F_FCU7987 | FCU | Service Corridor N-1446 | yes
NB_1F_FCU7988 | 1 | RDC_NB_1F_FCU7988 | FCU | Service Corridor N-1446 | yes
NB_1F_FCU7989 | 1 | RDC_NB_1F_FCU7989 | FCU | Stair 5 N-1ST05 | yes
NB_2F_FCU4918 | 1 | RDC_NB_2F_FCU4918 | FCU | IDF N-2104 | yes
NB_2F_FCU4919 | 1 | RDC_NB_2F_FCU4919 | FCU | IDF N-2104 | yes
NB_2F_FCU5988 | 1 | RDC_NB_2F_FCU5988 | FCU | Mechanical (AHU 8512) | yes
NB_2F_FCU5989 | 1 | RDC_NB_2F_FCU5989 | FCU | Stair 2 N-2ST02 | yes
NB_2F_FCU5990 | 1 | RDC_NB_2F_FCU5990 | FCU | Mechanical (AHU 8512/8514) | yes
NB_2F_FCU6993 | 1 | RDC_NB_2F_FCU6993 | FCU | Mechanical (AHU 8516) | yes
NB_2F_FCU6994 | 1 | RDC_NB_2F_FCU6994 | FCU | Normal Elec. N-2105 | yes
NB_2F_FCU6995 | 1 | RDC_NB_2F_FCU6995 | FCU | IDF N-2110 | yes
NB_2F_FCU6996 | 1 | RDC_NB_2F_FCU6996 | FCU | IDF N-2110 | yes
NB_2F_FCU7991 | 1 | RDC_NB_2F_FCU7991 | FCU | Normal Elec. N-2111 | yes
NB_2F_FCU7992 | 1 | RDC_NB_2F_FCU7992 | FCU | Emer. Elec. N-2112 | yes
NB_GF_FCU4911 | 1 | RDC_NB_GF_FCU4911 | FCU | MDF Room N-0206A | yes
NB_GF_FCU4912 | 1 | RDC_NB_GF_FCU4912 | FCU | MDF Room N-0206A | yes
NB_GF_FCU4913 | 1 | RDC_NB_GF_FCU4913 | FCU | Store N-0201 | yes
NB_GF_FCU4920 | 1 | RDC_NB_GF_FCU4920 | FCU | Emergency Electrical Landing Room N-0205 | yes
NB_GF_FCU5980 | 1 | RDC_NB_GF_FCU5980 | FCU | Serv Core N-0136 | yes
NB_GF_FCU5981 | 1 | RDC_NB_GF_FCU5981 | FCU | Serv Core N-0136 | yes
NB_GF_FCU5982 | 1 | RDC_NB_GF_FCU5982 | FCU | Stair 3 N-OST03 | yes
NB_GF_FCU5991 | 1 | RDC_NB_GF_FCU5991 | FCU | Vestibule N-0103 | yes
NB_GF_FCU5992 | 1 | RDC_NB_GF_FCU5992 | FCU | Vestibule N-0102 | yes
NB_GF_FCU6981 | 1 | RDC_NB_GF_FCU6981 | FCU | IDF N-0133 | yes
NB_GF_FCU6982 | 1 | RDC_NB_GF_FCU6982 | FCU | Mech/FPC N-0128 | yes | IDF N-0133 | this row
NB_GF_FCU6983 | 1 | RDC_NB_GF_FCU6983 | FCU | Service Corridor N-0344 | yes | Service Corridor N-0344 | this row
NB_GF_FCU6984 | 1 | RDC_NB_GF_FCU6984 | FCU | Service Corridor N-0344 | yes
NB_GF_FCU6985 | 1 | RDC_NB_GF_FCU6985 | FCU | IDF N-0311 | yes
NB_GF_FCU6986 | 1 | RDC_NB_GF_FCU6986 | FCU | IDF N-0311 | yes
NB_GF_FCU6987 | 1 | RDC_NB_GF_FCU6987 | FCU | Stair 4 N-0ST04 | yes
NB_GF_FCU7981 | 1 | RDC_NB_GF_FCU7981 | FCU | SURF ANALYSIS LAB N-0404F | yes
NB_GF_FCU7982 | 1 | RDC_NB_GF_FCU7982 | FCU | SURF ANALYSIS LAB N-0404F | yes
NB_GF_FCU7983 | 1 | RDC_NB_GF_FCU7983 | FCU | Stair 5 N-0ST05 | yes
NB_SB_Walkway_FCU9001 | 1 | RDC_NB_SB_Walkway_FCU9001 | FCU | Pedestrian Walkway between North & South Buildings | yes | Pedestrian Walkway B/W North & South | this row
NB_SB_Walkway_FCU9002 | 1 | RDC_NB_SB_Walkway_FCU9002 | FCU | Pedestrian Walkway between North & South Buildings | yes
NB_SB_Walkway_FCU9003 | 1 | RDC_NB_SB_Walkway_FCU9003 | FCU | Pedestrian Walkway between North & South Buildings | yes | Pedestrian Walkway B/W North & South | this row
NB_SB_Walkway_FCU9004 | 1 | RDC_NB_SB_Walkway_FCU9004 | FCU | Pedestrian Walkway between North & South Buildings | yes
NB_SB_Walkway_FCU9005 | 1 | RDC_NB_SB_Walkway_FCU9005 | FCU | Pedestrian Walkway between North & South Buildings | yes
SB_1F_FCU0501 | 1 | RDC_SB_1F_FCU0501 | FCU | STAIR-04 1ST04 | yes
SB_1F_FCU0502 | 1 | RDC_SB_1F_FCU0502 | FCU | UPS ROOM S-1107D | yes
SB_1F_FCU0503 | 1 | RDC_SB_1F_FCU0503 | FCU | UPS ROOM S-1107D | yes
SB_1F_FCU1501 | 1 | RDC_SB_1F_FCU1501 | FCU | IDF ROOM S-1156 | yes
SB_1F_FCU1502 | 1 | RDC_SB_1F_FCU1502 | FCU | IDF ROOM S-1156 | yes
SB_1F_FCU1503 | 1 | RDC_SB_1F_FCU1503 | FCU | STAIR-01 1ST01 | yes
SB_1F_FCU2501 | 1 | RDC_SB_1F_FCU2501 | FCU | STAIR-03 1ST03 | yes
SB_1F_FCU2502 | 1 | RDC_SB_1F_FCU2502 | FCU | IDF ROOM S-1244 | yes
SB_1F_FCU2503 | 1 | RDC_SB_1F_FCU2503 | FCU | IDF ROOM S-1244 | yes
SB_1F_FCU2504 | 1 | RDC_SB_1F_FCU2504 | FCU | UPS ROOM S-1276 | yes
SB_1F_FCU2505 | 1 | RDC_SB_1F_FCU2505 | FCU | UPS ROOM S-1276 | yes
SB_1F_FCU3501 | 1 | RDC_SB_1F_FCU3501 | FCU | STAIR-04 1ST04 | yes
SB_2F_FCU0201 | 1 | RDC_SB_2F_FCU0201 | FCU | South Penthouse S-2101 | yes
SB_2F_FCU0202 | 1 | RDC_SB_2F_FCU0202 | FCU | South Penthouse S-2101 | yes | South Penthouse S-2101 | this row
SB_2F_FCU0203 | 1 | RDC_SB_2F_FCU0203 | FCU | South Penthouse S-2101 | yes
SB_2F_FCU0204 | 1 | RDC_SB_2F_FCU0204 | FCU | South Penthouse S-2101 | yes
SB_2F_FCU0205 | 1 | RDC_SB_2F_FCU0205 | FCU | Normal Elec. S-2103 | yes
SB_2F_FCU0206 | 1 | RDC_SB_2F_FCU0206 | FCU | Normal Elec. S-2103 | yes | South Penthouse S-2101 | this row
SB_2F_FCU0207 | 1 | RDC_SB_2F_FCU0207 | FCU | Emerg. Elec. S-2104 | yes
SB_2F_FCU0208 | 1 | RDC_SB_2F_FCU0208 | FCU | Emerg. Elec. S-2104 | yes | South Penthouse S-2101 | this row
SB_2F_FCU1201 | 1 | RDC_SB_2F_FCU1201 | FCU | IDF S-2102 | yes
SB_2F_FCU1202 | 1 | RDC_SB_2F_FCU1202 | FCU | IDF S-2102 | yes
SB_2F_FCU2201 | 1 | RDC_SB_2F_FCU2201 | FCU | South Penthouse S-2101 | yes
SB_2F_FCU2202 | 1 | RDC_SB_2F_FCU2202 | FCU | South Penthouse S-2101 | yes
SB_2F_FCU2203 | 1 | RDC_SB_2F_FCU2203 | FCU | South Penthouse S-2101 | yes
SB_2F_FCU2204 | 1 | RDC_SB_2F_FCU2204 | FCU | Emerg. Elec. S-2105 | yes | Emergency Elec. S-2105 | this row
SB_2F_FCU2205 | 1 | RDC_SB_2F_FCU2205 | FCU | Emerg. Elec. S-2105 | yes | South Penthouse S-2101 | this row
SB_2F_FCU2206 | 1 | RDC_SB_2F_FCU2206 | FCU | Normal Elec. S-2106 | yes
SB_2F_FCU2207 | 1 | RDC_SB_2F_FCU2207 | FCU | Normal Elec. S-2106 | yes
SB_2F_FCU2208 | 1 | RDC_SB_2F_FCU2208 | FCU | IDF S-2107 | yes
SB_2F_FCU2209 | 1 | RDC_SB_2F_FCU2209 | FCU | IDF S-2107 | yes
SB_2F_FCU2210 | 1 | RDC_SB_2F_FCU2210 | FCU | South Penthouse S-2101 | yes
SB_GF_FCU0001 | 1 | RDC_SB_GF_FCU0001 | FCU | STAIR-02 S-02T02 | yes
SB_GF_FCU1001 | 1 | RDC_SB_GF_FCU1001 | FCU | QTEL ROOM S-0132 | yes
SB_GF_FCU1002 | 1 | RDC_SB_GF_FCU1002 | FCU | QTEL ROOM S-0132 | yes
SB_GF_FCU1003 | 1 | RDC_SB_GF_FCU1003 | FCU | IDF ROOM S-0133 | yes
SB_GF_FCU1004 | 1 | RDC_SB_GF_FCU1004 | FCU | IDF ROOM S-0133 | yes
SB_GF_FCU1005 | 1 | RDC_SB_GF_FCU1005 | FCU | EC MDF ROOM S-0134 | yes | EC MDF S-0134 | this row
SB_GF_FCU1006 | 1 | RDC_SB_GF_FCU1006 | FCU | EC MDF ROOM S-0134 | yes | EC MDF S-0134 | this row
SB_GF_FCU1007 | 1 | RDC_SB_GF_FCU1007 | FCU | MECHANICAL ROOM S-0136 | yes | Mech S-0136 | this row
SB_GF_FCU1008 | 1 | RDC_SB_GF_FCU1008 | FCU | STAIR-01 S-01T01 | yes | Stair 1 S-0ST01 | this row
SB_GF_FCU2001 | 1 | RDC_SB_GF_FCU2001 | FCU | STAIR-03 S-0ST03 | yes
SB_GF_FCU2002 | 1 | RDC_SB_GF_FCU2002 | FCU | AV ROOM S-0210 | yes | AV S-0210 | this row
SB_GF_FCU2003 | 1 | RDC_SB_GF_FCU2003 | FCU | AV ROOM S-0210 | yes
SB_GF_FCU2004 | 1 | RDC_SB_GF_FCU2004 | FCU | IDF ROOM S-0271 | yes
SB_GF_FCU2005 | 1 | RDC_SB_GF_FCU2005 | FCU | IDF ROOM S-0271 | yes
SB_GF_FCU3001 | 1 | RDC_SB_GF_FCU3001 | FCU | STAIR-04 S-0ST04 | yes
UB_GF_FCU8001 | 1 | RDC_UB_GF_FCU8001 | FCU | GENERAL STORAGE ROOM U-0129 | yes
UB_GF_FCU8002 | 1 | RDC_UB_GF_FCU8002 | FCU | SHOP U-0135 | yes | Shop U-0135 | this row
UB_GF_FCU8003 | 1 | RDC_UB_GF_FCU8003 | FCU | MAIL ROOM U-0128 | yes
UB_GF_FCU8004 | 1 | RDC_UB_GF_FCU8004 | FCU | GENERAL STORAGE U-0108 | yes
UB_GF_FCU8005 | 1 | RDC_UB_GF_FCU8005 | FCU | RECYCLING ROOM U-0109 | yes
UB_GF_FCU8006 | 1 | RDC_UB_GF_FCU8006 | FCU | CYLINDER STORAGE U-0105 | yes
UB_GF_FCU8007 | 1 | RDC_UB_GF_FCU8007 | FCU | LN2 DISPENSER U-0104 | yes
UB_GF_FCU8008 | 1 | RDC_UB_GF_FCU8008 | FCU | FLAMMABLE STORAGE U-0103 | yes
UB_GF_FCU8009 | 1 | RDC_UB_GF_FCU8009 | FCU | FLAMMABLE WASTE STORAGE U-0102 | yes
UB_GF_FCU8010 | 1 | RDC_UB_GF_FCU8010 | FCU | BMS ROOM U-0117 | yes
UB_GF_FCU8011 | 1 | RDC_UB_GF_FCU8011 | FCU | BREAK ROOM U-0118 | yes
UB_GF_FCU8012 | 1 | RDC_UB_GF_FCU8012 | FCU | OFFICE SPACE U-0119 | yes
UB_GF_FCU8013 | 1 | RDC_UB_GF_FCU8013 | FCU | WET/MECH/FIRE ROOM U-0120 | yes
UB_GF_FCU8014 | 1 | RDC_UB_GF_FCU8014 | FCU | WET/MECH/FIRE ROOM U-0120 | yes
UB_GF_FCU8502 | 1 | RDC_UB_GF_FCU8502 | FCU | SHIPPING AND RECEIVING L0 | yes
UB_GF_FCU8503 | 1 | RDC_UB_GF_FCU8503 | FCU | SHIPPING AND RECEIVING L0 | yes
UB_GF_FCU8504 | 1 | RDC_UB_GF_FCU8504 | FCU | SHIPPING AND RECEIVING L0 | yes
UB_GF_FCU8505 | 1 | RDC_UB_GF_FCU8505 | FCU | SHIPPING AND RECEIVING L0 | yes
UB_GF_FCU8512 | 1 | RDC_UB_GF_FCU8512 | FCU | WET/MECH/FIRE ROOM U-0120 | yes
UB_GF_FCU8513 | 1 | RDC_UB_GF_FCU8513 | FCU | WET/MECH/FIRE ROOM U-0120 | yes
UB_GF_FCU8514 | 1 | RDC_UB_GF_FCU8514 | FCU | WET/MECH/FIRE ROOM U-0120 | yes | Pump Room U-0121 | this row
UB_GF_FCU8515 | 1 | RDC_UB_GF_FCU8515 | FCU | WET/MECH/FIRE ROOM U-0120 | yes
UB_MF_FCU8501 | 1 | RDC_UB_MF_FCU8501 | FCU | MECHANICAL ROOM U-1101 | yes
UB_MF_FCU8506 | 1 | RDC_UB_MF_FCU8506 | FCU | MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
UB_MF_FCU8507 | 1 | RDC_UB_MF_FCU8507 | FCU | MECHANICAL ROOM U-1101 | yes
UB_MF_FCU8508 | 1 | RDC_UB_MF_FCU8508 | FCU | MECHANICAL ROOM U-1101 | yes
UB_MF_FCU8509 | 1 | RDC_UB_MF_FCU8509 | FCU | MECHANICAL ROOM U-1101 | yes
UB_MF_FCU8510 | 1 | RDC_UB_MF_FCU8510 | FCU | MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
UB_MF_FCU8511 | 1 | RDC_UB_MF_FCU8511 | FCU | MECHANICAL ROOM U-1101 | yes | Mechanical U-101 | this row
SB_L0_AT-1001 | 2 | RDC_SB_L0_AT-1001 | AT | Corridor S-0137 | different room
|  | RDC_SB_L0_EV-1001 | EV | Computer Lab S-0139
SB_L0_AT-1005 | 1 | RDC_SB_L0_AT-1005 | AT | Normal & Emergency Elec. Landing S-0142 | yes
SB_L0_AT-1006 | 1 | RDC_SB_L0_AT-1006 | AT | Corridor S-0137 | yes
SB_L0_AT-1007 | 1 | RDC_SB_L0_AT-1007 | AT | UPS S-0145 | yes
SB_L0_AT-1009 | 1 | RDC_SB_L0_AT-1009 | AT | Service Dock S-0151 | yes
NB_GF_AT-4035 | 1 | RDC_NB_GF_AT-4035 | AT | Corridor N-0207A | yes
NB_GF_AT-4170 | 1 | RDC_NB_GF_AT-4170 | AT | Storage Room N-0237 | yes
NB_GF_CEV-4031 | 1 | RDC_NB_GF_CEV-4031 | CEV | Service Corridor N-0207 | yes
NB_GF_EV-4028 | 1 | RDC_NB_GF_EV-4028 | EV | MDF ROOM N-0206A | yes
NB_GF_EV-4236 | 1 | RDC_NB_GF_EV-4236 | EV | Office 05 -8WS- N-0250 | yes
NB_GF_EV-4261 | 1 | RDC_NB_GF_EV-4261 | EV | Office 05 -8WS- N-0255 | yes
NB_GF_EV-4286 | 1 | RDC_NB_GF_EV-4286 | EV | Office 05 -8WS- N-0260 | yes
NB_GF_EV-4311 | 1 | RDC_NB_GF_EV-4311 | EV | WORKSTATION N-0265 | yes
NB_GF_VEV-4041 | 1 | RDC_NB_GF_VEV-4041 | VEV | Air Quality High Bay N-0215A | yes
NB_GF_FEV-4193 | 1 | RDC_NB_GF_FEV-4193 | FEV | CSP Lab N-0240B | yes
NB_GF_FEV-4194 | 1 | RDC_NB_GF_FEV-4194 | FEV | CSP Lab N-0240B | yes
NB_GF_VEV-4213A | 1 | RDC_NB_GF_VEV-4213A | VEV | Desal Lab N-0240D | yes
NB_GF_VEV-4213B | 1 | RDC_NB_GF_VEV-4213B | VEV | Desal Lab N-0240D | yes
NB_GF_FEV-4214 | 1 | RDC_NB_GF_FEV-4214 | FEV | Desal Lab N-0240D | yes
NB_GF_FEV-4215 | 1 | RDC_NB_GF_FEV-4215 | FEV | Desal Lab N-0240D | yes
NB_GF_FEV-4216 | 1 | RDC_NB_GF_FEV-4216 | FEV | Desal Lab N-0240D | yes
SB_L0_AT-0006 | 1 | RDC_SB_L0_AT-0006 | AT | Normal Elec. S-0107 | yes
SB_L0_AT-0015 | 1 | RDC_SB_L0_AT-0015 | AT | Corridor S-0117 | yes
SB_L0_AT-0020 | 1 | RDC_SB_L0_AT-0020 | AT | Storage S-0120B | yes
SB_L0_AT-0021 | 1 | RDC_SB_L0_AT-0021 | AT | Vestibule S-0125 | yes
SB_L0_AT-0022 | 1 | RDC_SB_L0_AT-0022 | AT | Men S-0126 | yes
SB_L0_AT-0023 | 1 | RDC_SB_L0_AT-0023 | AT | Women S-0127 | yes
SB_L0_AT-0024 | 1 | RDC_SB_L0_AT-0024 | AT | NORM. ELEC. S-0129 | yes
NB_GF_AT-4315 | 1 | RDC_NB_GF_AT-4315 | AT | Vestibule N-0270A | yes
NB_GF_AT-5160 | 1 | RDC_NB_GF_AT-5160 | AT | MENS ROOM N-0130 | yes
NB_GF_AT-5280 | 1 | RDC_NB_GF_AT-5280 | AT | Store N-0146 | yes | Serv Core N-0136 | this row
NB_GF_AT-5290 | 1 | RDC_NB_GF_AT-5290 | AT | Pantry N-0148 | yes
NB_GF_AT-5320 | 1 | RDC_NB_GF_AT-5320 | AT | Office N-0154 | yes
NB_GF_AT-5350 | 1 | RDC_NB_GF_AT-5350 | AT | Open Office N-0160 | yes
NB_GF_AT-5375 | 1 | RDC_NB_GF_AT-5375 | AT | Open Office N-0165 | yes
NB_GF_EV-4316 | 1 | RDC_NB_GF_EV-4316 | EV | Vestibule N-0270A | yes
NB_GF_EV-5026 | 1 | RDC_NB_GF_EV-5026 | EV | Corridor N-0110 | yes
NB_GF_EV-5161 | 1 | RDC_NB_GF_EV-5161 | EV | Womens+N-0130A+N-0132 JC N-0130 | yes
NB_GF_EV-5163 | 1 | RDC_NB_GF_EV-5163 | EV | IDF N-0133 | yes
NB_GF_EV-5291 | 1 | RDC_NB_GF_EV-5291 | EV | Pantry N-0148 | yes
NB_GF_VEV-5052A | 1 | RDC_NB_GF_VEV-5052A | VEV | Analytical Core Lab 1 N-0114A | yes
NB_GF_VEV-5052B | 1 | RDC_NB_GF_VEV-5052B | VEV | Analytical Core Lab 1 N-0114A | yes
NB_GF_FEV-5053 | 1 | RDC_NB_GF_FEV-5053 | FEV | Analytical Core Lab 1 N-0114A | yes
NB_GF_VEV-5055 | 1 | RDC_NB_GF_VEV-5055 | VEV | Analytical Core Lab 1 N-0114A | yes
NB_GF_FEV-5062 | 1 | RDC_NB_GF_FEV-5062 | FEV | Clean Lab N-0114B | yes
NB_GF_VEV-5071 | 1 | RDC_NB_GF_VEV-5071 | VEV | Dirty Lab N-0114C | yes
NB_GF_FEV-5072 | 1 | RDC_NB_GF_FEV-5072 | FEV | Dirty Lab N-0114C | yes
NB_GF_FEV-5073 | 1 | RDC_NB_GF_FEV-5073 | FEV | Dirty Lab N-0114C | yes
NB_GF_FEV-5074 | 1 | RDC_NB_GF_FEV-5074 | FEV | Dirty Lab N-0114C | yes
NB_GF_FEV-5082 | 1 | RDC_NB_GF_FEV-5082 | FEV | Bio Analyt N-0114D | yes
NB_GF_FEV-5083 | 1 | RDC_NB_GF_FEV-5083 | FEV | Bio Analyt N-0114D | yes
NB_GF_VEV-5092 | 1 | RDC_NB_GF_VEV-5092 | VEV | Air Quality N-0114F | yes
NB_GF_FEV-5093 | 1 | RDC_NB_GF_FEV-5093 | FEV | Air Quality N-0114F | yes
NB_GF_FEV-5094 | 1 | RDC_NB_GF_FEV-5094 | FEV | Air Quality N-0114F | yes
NB_GF_FEV-5095A | 1 | RDC_NB_GF_FEV-5095A | FEV | Air Quality N-0114F | yes
NB_GF_FEV-5095B | 1 | RDC_NB_GF_FEV-5095B | FEV | Air Quality N-0114F | yes
NB_GF_VEV-5182A | 1 | RDC_NB_GF_VEV-5182A | VEV | Analyt Core-2 N-0140A | yes
NB_GF_VEV-5182B | 1 | RDC_NB_GF_VEV-5182B | VEV | Analyt Core-2 N-0140A | yes
NB_GF_FEV-5183 | 1 | RDC_NB_GF_FEV-5183 | FEV | Analytical Core Lab 2 N-0140A | yes
NB_GF_VEV-5192a | 1 | RDC_NB_GF_VEV-5192a | VEV | Furnace Room N-0140B | yes
NB_GF_VEV-5192b | 1 | RDC_NB_GF_VEV-5192b | VEV | Furnace Room N-0140B | yes
NB_GF_FEV-5203 | 1 | RDC_NB_GF_FEV-5203 | FEV | Prep Lab N-0140C | yes
NB_GF_VEV-5211 | 1 | RDC_NB_GF_VEV-5211 | VEV | Sputter Room N-0140D | yes | MBE EVAP Room N-0140E | this row
NB_GF_VEV-5221 | 1 | RDC_NB_GF_VEV-5221 | VEV | MBE/Evap Room N-0140E | yes
NB_GF_FEV-5222 | 1 | RDC_NB_GF_FEV-5222 | FEV | Evap Room N-0140E | yes
NB_GF_FEV-5223 | 1 | RDC_NB_GF_FEV-5223 | FEV | Evap Room N-0140E | yes
NB_GF_VEV-5231 | 1 | RDC_NB_GF_VEV-5231 | VEV | ALD Room N-0140F | yes
NB_GF_CEV-5241 | 1 | RDC_NB_GF_CEV-5241 | CEV | Air Lock N-0140G | yes
NB_GF_FEV-5271 | 1 | RDC_NB_GF_FEV-5271 | FEV | Org Chem N-0140K | yes
NB_GF_FEV-5272 | 1 | RDC_NB_GF_FEV-5272 | FEV | Org Chem N-0140K | yes
NB_GF_FEV-5273 | 1 | RDC_NB_GF_FEV-5273 | FEV | Org Chem N-0140K | yes
NB_GF_FEV-5274 | 1 | RDC_NB_GF_FEV-5274 | FEV | Org Chem N-0140K | yes
NB_GF_FEV-5275 | 1 | RDC_NB_GF_FEV-5275 | FEV | Org Chem N-0140K | yes
NB_GF_FEV-5276 | 1 | RDC_NB_GF_FEV-5276 | FEV | Org Chem N-0140K | yes
NB_GF_FEV-5277 | 1 | RDC_NB_GF_FEV-5277 | FEV | Org Chem N-0140K | yes
SB_L0_AT-0004 | 1 | RDC_SB_L0_AT-0004 | AT | Corridor S-0104 | yes
SB_L0_AT-0005 | 1 | RDC_SB_L0_AT-0005 | AT | Men S-0105 | yes
SB_L0_A1.2_AT-2001 | 1 | RDC_SB_L0_A1.2_AT-2001 | AT | High-Density Room S-0206 | yes
SB_L0_A1.3_AT-2001 | 1 | RDC_SB_L0_A1.3_AT-2001 | AT | WOMEN S-0205 | yes
NB_GF_AT-5005 | 1 | RDC_NB_GF_AT-5005 | AT | Vestibule N-0105 | yes
NB_GF_AT-5020 | 1 | RDC_NB_GF_AT-5020 | AT | Mens + Vestibule + N-0109 N-0108 | yes
NB_GF_AT-6005 | 1 | RDC_NB_GF_AT-6005 | AT | Vestibule N-0302 | yes
NB_GF_AT-6015 | 1 | RDC_NB_GF_AT-6015 | AT | Men N-0306 | yes
NB_GF_AT-6020 | 1 | RDC_NB_GF_AT-6020 | AT | Vestibule N-0308 | yes
NB_GF_EV-5021 | 1 | RDC_NB_GF_EV-5021 | EV | Mens + Vestibule + N-0109 N-0108 | yes
NB_GF_EV-5035 | 1 | RDC_NB_GF_EV-5035 | EV | Confr Room N-0112 | yes
NB_GF_EV-6016 | 1 | RDC_NB_GF_EV-6016 | EV | Men N-0306 | yes
NB_GF_EV-6127 | 1 | RDC_NB_GF_EV-6127 | EV | IDF N-0311 | yes
SB_L0_AT-0115 | 1 | RDC_SB_L0_AT-0115 | AT | Office S-0233A | yes
SB_L0_AT-0116 | 1 | RDC_SB_L0_AT-0116 | AT | Office S-0232A | yes
SB_L0_AT-0117 | 1 | RDC_SB_L0_AT-0117 | AT | Open Plan S-0228 | yes
SB_L0_AT-0118 | 1 | RDC_SB_L0_AT-0118 | AT | Open Plan S-0228B | yes
SB_L0_AT-0120 | 1 | RDC_SB_L0_AT-0120 | AT | Open Plan S-0228A | yes
SB_L0_AT-0122 | 1 | RDC_SB_L0_AT-0122 | AT | Office S-0211A | yes
SB_L0_AT-0123 | 1 | RDC_SB_L0_AT-0123 | AT | Office S-0211B | yes
SB_L0_AT-0124 | 1 | RDC_SB_L0_AT-0124 | AT | Technical Open Plan S-0211 | yes
NB_GF_AT-7005 | 1 | RDC_NB_GF_AT-7005 | AT | WOMEN N-0402 | yes
NB_GF_AT-7380 | 1 | RDC_NB_GF_AT-7380 | AT | Pipe Chase N-0443B | yes
NB_GF_AT-6280 | 1 | RDC_NB_GF_AT-6280 | AT | Pantry N-0356 | yes
NB_GF_EV-6141 | 1 | RDC_NB_GF_EV-6141 | EV | Workstation N-0317 | yes
NB_GF_EV-6156 | 1 | RDC_NB_GF_EV-6156 | EV | Workstation N-0320 | yes
NB_GF_EV-6176 | 1 | RDC_NB_GF_EV-6176 | EV | Workstation N-0324 | yes
NB_GF_EV-6281 | 1 | RDC_NB_GF_EV-6281 | EV | Pantry N-0356 | yes
NB_GF_EV-6356 | 1 | RDC_NB_GF_EV-6356 | EV | Office 05-8-WKS N-0372 | yes
NB_GF_EV-6381 | 1 | RDC_NB_GF_EV-6381 | EV | Office 05-8-WKS N-0378 | yes
NB_GF_EV-6401 | 1 | RDC_NB_GF_EV-6401 | EV | Office 05-8-WKS N-0381 | yes
NB_GF_EV-7006 | 1 | RDC_NB_GF_EV-7006 | EV | WOMEN N-0402 | yes
NB_GF_EV-7381 | 1 | RDC_NB_GF_EV-7381 | EV | Pipe Chase N-0443B | yes
NB_GF_VEV-6053 | 1 | RDC_NB_GF_VEV-6053 | VEV | Open Lab 1 N-0310C | yes
NB_GF_VEV-6061 | 1 | RDC_NB_GF_VEV-6061 | VEV | Lab Support 3 N-0310D | yes
NB_GF_VEV-6071 | 1 | RDC_NB_GF_VEV-6071 | VEV | Lab Support 4 N-0310E | yes
NB_GF_VEV-6081 | 1 | RDC_NB_GF_VEV-6081 | VEV | Lab Support 5 N-0310F | yes
NB_GF_VEV-6091 | 1 | RDC_NB_GF_VEV-6091 | VEV | Lab Support 6 N-0310G | yes
NB_GF_VAV-6080 | 1 | RDC_NB_GF_VAV-6080 | VAV | Lab Support 5 N-0310F | yes
NB_GF_FCU6997 | 1 | RDC_NB_GF_FCU6997 | FCU | Lab Sup 2 N-0310B | yes
SB_L0_AT-0101 | 1 | RDC_SB_L0_AT-0101 | AT | Office S-0244A | yes
SB_L0_AT-0102 | 1 | RDC_SB_L0_AT-0102 | AT | Office S-0244B | yes
SB_L0_AT-0103 | 1 | RDC_SB_L0_AT-0103 | AT | Office S-0244C | yes
SB_L0_AT-0104 | 1 | RDC_SB_L0_AT-0104 | AT | Office S-0244D | yes
SB_L0_AT-0105 | 1 | RDC_SB_L0_AT-0105 | AT | Office S-0244E | yes
SB_L0_AT-0107 | 1 | RDC_SB_L0_AT-0107 | AT | Office S-0262A | yes
SB_L0_AT-0108 | 1 | RDC_SB_L0_AT-0108 | AT | Office S-0262B | yes
SB_L0_AT-0109 | 1 | RDC_SB_L0_AT-0109 | AT | Office S-0262C | yes
SB_L0_AT-0110 | 1 | RDC_SB_L0_AT-0110 | AT | Office S-0262H | yes
SB_L0_AT-0111 | 1 | RDC_SB_L0_AT-0111 | AT | Office S-0262E | yes
SB_L0_AT-0112 | 1 | RDC_SB_L0_AT-0112 | AT | Office S-0262F | yes
SB_L0_AT-0113 | 1 | RDC_SB_L0_AT-0113 | AT | Office S-0262G | yes
SB_L0_AT-0114 | 1 | RDC_SB_L0_AT-0114 | AT | Office S-0262D | yes
NB_GF_EV-7091 | 1 | RDC_NB_GF_EV-7091 | EV | Office N-0412A | yes
NB_GF_EV-7106 | 1 | RDC_NB_GF_EV-7106 | EV | Office N-0415A | yes
NB_GF_EV-7121 | 1 | RDC_NB_GF_EV-7121 | EV | Office 05-4-WS N-0418 | yes
NB_GF_EV-7122 | 1 | RDC_NB_GF_EV-7122 | EV | IDF Room N-0419 | yes
NB_GF_EV-7396 | 1 | RDC_NB_GF_EV-7396 | EV | Office 05-8-WKS N-0446 | yes
NB_GF_EV-7426 | 1 | RDC_NB_GF_EV-7426 | EV | Office 05-8-WKS N-0452 | yes
NB_GF_EV-7461 | 1 | RDC_NB_GF_EV-7461 | EV | Office 05-8-WKS N-0457 | yes
NB_GF_EV-7486 | 1 | RDC_NB_GF_EV-7486 | EV | Office 05-8-WKS N-0462 | yes
NB_GF_VEV-7022A | 1 | RDC_NB_GF_VEV-7022A | VEV | NMR Lab N-0404A | yes
NB_GF_VEV-7022B | 1 | RDC_NB_GF_VEV-7022B | VEV | NMR Lab N-0404A | yes
NB_GF_VEV-7023A | 1 | RDC_NB_GF_VEV-7023A | VEV | NMR Lab N-0404A | yes
NB_GF_VEV-7023B | 1 | RDC_NB_GF_VEV-7023B | VEV | NMR Lab N-0404A | yes
NB_GF_VEV-7024A | 1 | RDC_NB_GF_VEV-7024A | VEV | NMR Lab N-0404A | yes
NB_GF_VEV-7024B | 1 | RDC_NB_GF_VEV-7024B | VEV | NMR Lab N-0404A | yes
NB_GF_FEV-7052 | 1 | RDC_NB_GF_FEV-7052 | FEV | EM Prep 1 - MAT N-0404D | yes
NB_GF_FEV-7053 | 1 | RDC_NB_GF_FEV-7053 | FEV | EM Prep 1 - MAT N-0404D | yes
NB_GF_FEV-7062 | 1 | RDC_NB_GF_FEV-7062 | FEV | EM Prep 2 - BIO N-0404E | yes
NB_GF_VEV-7072A | 1 | RDC_NB_GF_VEV-7072A | VEV | Surf Analysis Lab N-0404F | yes
NB_GF_VEV-7072B | 1 | RDC_NB_GF_VEV-7072B | VEV | Surf Analysis Lab N-0404F | yes
NB_GF_VEV-7073 | 1 | RDC_NB_GF_VEV-7073 | VEV | Surf Analysis Lab N-0404F | yes
NB_GF_FEV-7074 | 1 | RDC_NB_GF_FEV-7074 | FEV | Surf Analysis Lab N-0404F | yes
NB_GF_FEV-7075 | 1 | RDC_NB_GF_FEV-7075 | FEV | Surf Analysis Lab N-0404F | yes
NB_GF_FEV-7232 | 1 | RDC_NB_GF_FEV-7232 | FEV | Inter Lab N-0442A | yes
NB_GF_VEV-7241B | 1 | RDC_NB_GF_VEV-7241B | VEV | Optical Lab N-0442B | yes
NB_GF_VEV-7301 | 1 | RDC_NB_GF_VEV-7301 | VEV | A/L 1 N-0442H | yes
NB_GF_FCU7993 | 1 | RDC_NB_GF_FCU7993 | FCU | Stair 5 N-0ST05 | yes
SB_1F_AT-1504 | 1 | RDC_SB_1F_AT-1504 | AT | Corridor S-1122 | yes
SB_1F_AT-1535 | 1 | RDC_SB_1F_AT-1535 | AT | Pantry S-1149A | yes
SB_1F_AT-1537 | 1 | RDC_SB_1F_AT-1537 | AT | Normal Elec. S-1147 | yes
NB_1F_EV-4500 | 1 | RDC_NB_1F_EV-4500 | EV | MDF N-1201 | yes
NB_1F_CEV-4502 | 1 | RDC_NB_1F_CEV-4502 | CEV | Corridor N-1202 | yes
NB_1F_EV-4661 | 1 | RDC_NB_1F_EV-4661 | EV | Office 05 - 8 WKS- N-1227 | yes
NB_1F_EV-4686 | 1 | RDC_NB_1F_EV-4686 | EV | Office 05 - 8 WKS- N-1232 | yes
NB_1F_EV-4711 | 1 | RDC_NB_1F_EV-4711 | EV | Office 05 - 8 WKS- N-1237 | yes
NB_1F_EV-4736 | 1 | RDC_NB_1F_EV-4736 | EV | Office 05 - 8 WKS- N-1242 | yes
NB_1F_VEV-4602 | 1 | RDC_NB_1F_VEV-4602 | VEV | Testing Room N-1216B | yes
NB_1F_FEV-4603 | 1 | RDC_NB_1F_FEV-4603 | FEV | Testing Room N-1216B | yes
NB_1F_FEV-4604 | 1 | RDC_NB_1F_FEV-4604 | FEV | Testing Room N-1216B | yes
NB_1F_FEV-4605 | 1 | RDC_NB_1F_FEV-4605 | FEV | Testing Room N-1216B | yes
NB_1F_FEV-4606 | 1 | RDC_NB_1F_FEV-4606 | FEV | Testing Room N-1216B | yes
NB_1F_FEV-4622 | 1 | RDC_NB_1F_FEV-4622 | FEV | EL Shop N-1216C | yes
NB_1F_CAV-4581B | 1 | RDC_NB_1F_CAV-4581B | CAV | Photovoltaic Lab N-1216A | yes
NB_1F_VEV-4585A | 1 | RDC_NB_1F_VEV-4585A | VEV | Photovoltaic Lab N-1216A | yes
NB_1F_VEV-4585B | 1 | RDC_NB_1F_VEV-4585B | VEV | Photovoltaic Lab N-1216A | yes
NB_1F_VEV-4586A | 1 | RDC_NB_1F_VEV-4586A | VEV | Photovoltaic Lab N-1216A | yes
NB_1F_VEV-4586B | 1 | RDC_NB_1F_VEV-4586B | VEV | Photovoltaic Lab N-1216A | yes
NB_1F_FEV-4587 | 1 | RDC_NB_1F_FEV-4587 | FEV | Photovoltaic Lab N-1216A | yes
NB_1F_FEV-4588 | 1 | RDC_NB_1F_FEV-4588 | FEV | Photovoltaic Lab N-1216A | yes
NB_1F_FCU2004 | 1 | RDC_NB_1F_FCU2004 | FCU | Corridor N-1202 | yes
SB_1F_AT-0501 | 1 | RDC_SB_1F_AT-0501 | AT | Lobby S-1102 | yes
SB_1F_AT-0502 | 1 | RDC_SB_1F_AT-0502 | AT | Vestibule S-1105 | yes
SB_1F_AT-0503 | 1 | RDC_SB_1F_AT-0503 | AT | Women S-1106B | yes
SB_1F_AT-0504 | 1 | RDC_SB_1F_AT-0504 | AT | Vestibule S-1107 | yes
SB_1F_AT-0505 | 1 | RDC_SB_1F_AT-0505 | AT | EMERGENCY Elec. S-1107B | yes
SB_1F_AT-0515 | 1 | RDC_SB_1F_AT-0515 | AT | Corridor S-1122 | yes
SB_1F_AT-0516 | 1 | RDC_SB_1F_AT-0516 | AT | Pantry S-1158 | yes
SB_1F_AT-0517 | 1 | RDC_SB_1F_AT-0517 | AT | Normal Elec. S-1160 | yes
SB_1F_AT-0524 | 1 | RDC_SB_1F_AT-0524 | AT | Women S-1169 | yes
SB_1F_AT-0525 | 1 | RDC_SB_1F_AT-0525 | AT | Men S-1170 | yes
SB_1F_AT-0534 | 1 | RDC_SB_1F_AT-0534 | AT | CORRIDOR S-1180 | yes
SB_1F_AT-0535 | 1 | RDC_SB_1F_AT-0535 | AT | Cooridor S-1180 | yes
SB_1F_AT-1541 | 1 | RDC_SB_1F_AT-1541 | AT | Cooridor S-1181 | yes
NB_1F_AT-5720 | 1 | RDC_NB_1F_AT-5720 | AT | Men N-1134 | yes
NB_1F_AT-5750 | 1 | RDC_NB_1F_AT-5750 | AT | Store N-1141 | yes
NB_1F_AT-4640 | 1 | RDC_NB_1F_AT-4640 | AT | Women N-1221 | yes
NB_1F_EV-5686 | 1 | RDC_NB_1F_EV-5686 | EV | Corridor N-1126 | yes
NB_1F_EV-5721 | 1 | RDC_NB_1F_EV-5721 | EV | Men N-1134 | yes
NB_1F_EV-5747 | 1 | RDC_NB_1F_EV-5747 | EV | IDF N-1140 | yes
NB_1F_EV-4641 | 1 | RDC_NB_1F_EV-4641 | EV | Women N-1221 | yes
NB_1F_EV-5891 | 1 | RDC_NB_1F_EV-5891 | EV | Office 05 - 8 WKS- North N-1160 | yes
NB_1F_EV-5921 | 1 | RDC_NB_1F_EV-5921 | EV | Office 05 - 8 WKS- N-1168 | yes
NB_1F_EV-5941 | 1 | RDC_NB_1F_EV-5941 | EV | Office 05 - 8 WKS- N-1165 | yes
NB_1F_FEV-5624 | 1 | RDC_NB_1F_FEV-5624 | FEV | Sequence Lab N-1115K | yes | Robotics N-1115J | this row
NB_1F_VEV-5572 | 1 | RDC_NB_1F_VEV-5572 | VEV | Met/Prot Lab N-1115C | yes
NB_1F_VEV-5573A | 1 | RDC_NB_1F_VEV-5573A | VEV | Met/Prot Lab N-1115C | yes
NB_1F_VEV-5573B | 1 | RDC_NB_1F_VEV-5573B | VEV | Met/Prot Lab N-1115C | yes
NB_1F_FEV-5574 | 1 | RDC_NB_1F_FEV-5574 | FEV | Met/Prot Lab N-1115C | yes | PRe-PCR N-1115B | this row
NB_1F_FEV-5575 | 1 | RDC_NB_1F_FEV-5575 | FEV | Met/Prot Lab N-1115C | yes | Cell Culture N-1115E | this row
NB_1F_VEV-5591 | 1 | RDC_NB_1F_VEV-5591 | VEV | Cell Culture N-1115E | yes
NB_1F_FEV-5772 | 1 | RDC_NB_1F_FEV-5772 | FEV | Histology N-1144A | yes
NB_1F_VEV-5791 | 1 | RDC_NB_1F_VEV-5791 | VEV | Shafallah N-1144C | yes | Culture & Gel Rm N-1144B | this row
NB_1F_VEV-5795B | 1 | RDC_NB_1F_VEV-5795B | VEV | Storage and Archives N-1144C2 | yes | PRE-PCR N-1144D | this row
NB_1F_FEV-5796 | 1 | RDC_NB_1F_FEV-5796 | FEV | Shafallah N-1144C | yes | PRE-PCR N-1144D | this row
NB_1F_VEV-5811A | 1 | RDC_NB_1F_VEV-5811A | VEV | Nano Lab N-1144E | yes
NB_1F_VEV-5811B | 1 | RDC_NB_1F_VEV-5811B | VEV | Nano Lab N-1144E | yes
NB_1F_FEV-5812 | 1 | RDC_NB_1F_FEV-5812 | FEV | Nano Lab N-1144E | yes
NB_1F_FEV-5813 | 1 | RDC_NB_1F_FEV-5813 | FEV | Nano Lab N-1144E | yes
NB_1F_VEV-5821 | 1 | RDC_NB_1F_VEV-5821 | VEV | Nano Lab N-1144E | yes
SB_1F_AT-2507 | 1 | RDC_SB_1F_AT-2507 | AT | Female S-1204 | yes
SB_1F_AT-4260 | 1 | RDC_SB_1F_AT-4260 | AT | Office 05 -8WS- N-0255 | yes
NB_1F_AT-6740 | 1 | RDC_NB_1F_AT-6740 | AT | Men N-1340 | yes
NB_1F_AT-7500 | 1 | RDC_NB_1F_AT-7500 | AT | Women N-1403 | yes
NB_1F_AT-6372 | 1 | RDC_NB_1F_AT-6372 | AT | Office N-1374 | yes
NB_1F_AT-6374 | 1 | RDC_NB_1F_AT-6374 | AT | Office N-1375 | yes
NB_1F_AT-6376 | 1 | RDC_NB_1F_AT-6376 | AT | Office N-1376 | yes
NB_1F_AT-6378 | 1 | RDC_NB_1F_AT-6378 | AT | Office N-1377 | yes
NB_1F_EV-6661 | 1 | RDC_NB_1F_EV-6661 | EV | Workstation N-1321 | yes
NB_1F_EV-6676 | 1 | RDC_NB_1F_EV-6676 | EV | Workstation N-1324 | yes
NB_1F_EV-6691 | 1 | RDC_NB_1F_EV-6691 | EV | Exp. Workstation N-1327 | yes
NB_1F_EV-6741 | 1 | RDC_NB_1F_EV-6741 | EV | Men N-1340 | yes
NB_1F_EV-7501 | 1 | RDC_NB_1F_EV-7501 | EV | Women N-1403 | yes
NB_1F_EV-6936 | 1 | RDC_NB_1F_EV-6936 | EV | Workstation N-1363 | yes
NB_1F_EV-6961 | 1 | RDC_NB_1F_EV-6961 | EV | Workstation N-1368 | yes
NB_1F_EV-6969 | 1 | RDC_NB_1F_EV-6969 | EV | Workstation N-1371 | yes
NB_1F_VEV-6541 | 1 | RDC_NB_1F_VEV-6541 | VEV | TC1 N-1316B | yes
NB_1F_VEV-6552 | 1 | RDC_NB_1F_VEV-6552 | VEV | Gene Therapy Lab N-1316C | yes
NB_1F_VEV-6553 | 1 | RDC_NB_1F_VEV-6553 | VEV | Gene Therapy Lab N-1316C | yes
NB_1F_FEV-6554 | 1 | RDC_NB_1F_FEV-6554 | FEV | Gene Therapy Lab N-1316C | yes
NB_1F_FEV-6555 | 1 | RDC_NB_1F_FEV-6555 | FEV | Gene Therapy Lab N-1316C | yes
NB_1F_CEV-6581 | 1 | RDC_NB_1F_CEV-6581 | CEV | TC3 N-1316F | yes
NB_1F_FEV-6602 | 1 | RDC_NB_1F_FEV-6602 | FEV | Analytical Core N-1316H | yes
NB_1F_FEV-6632 | 1 | RDC_NB_1F_FEV-6632 | FEV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_FEV-6633 | 1 | RDC_NB_1F_FEV-6633 | FEV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_FEV-6634 | 1 | RDC_NB_1F_FEV-6634 | FEV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_FEV-6635 | 1 | RDC_NB_1F_FEV-6635 | FEV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_FEV-6636 | 1 | RDC_NB_1F_FEV-6636 | FEV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_FEV-6637 | 1 | RDC_NB_1F_FEV-6637 | FEV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_FEV-6638 | 1 | RDC_NB_1F_FEV-6638 | FEV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_FEV-6639 | 1 | RDC_NB_1F_FEV-6639 | FEV | Bio-Med Chem Lab 1 N-1316L | yes
NB_1F_FEV-6731 | 1 | RDC_NB_1F_FEV-6731 | FEV | SERIVICE CORRRIDOR N-1337 | yes
NB_1F_VEV-6751 | 1 | RDC_NB_1F_VEV-6751 | VEV | TC1 N-1345A | yes
NB_1F_VEV-6762 | 1 | RDC_NB_1F_VEV-6762 | VEV | Diabetes Lab / Open Lab N-1345B | yes
NB_1F_VEV-6763 | 1 | RDC_NB_1F_VEV-6763 | VEV | Diabetes Lab / Open Lab N-1345B | yes
NB_1F_FEV-6764 | 1 | RDC_NB_1F_FEV-6764 | FEV | Diabetes Lab / Open Lab N-1345B | yes
NB_1F_FEV-6765 | 1 | RDC_NB_1F_FEV-6765 | FEV | Diabetes Lab / Open Lab N-1345B | yes
NB_1F_FEV-6766 | 1 | RDC_NB_1F_FEV-6766 | FEV | Diabetes Lab / Open Lab N-1345B | yes
NB_1F_CEV-6791 | 1 | RDC_NB_1F_CEV-6791 | CEV | TC2 N-1345C | yes
NB_1F_FEV-6852 | 1 | RDC_NB_1F_FEV-6852 | FEV | Bio-Med Chem Lab 2 N-1345J | yes
NB_1F_FEV-6853 | 1 | RDC_NB_1F_FEV-6853 | FEV | Bio-Med Chem Lab 2 N-1345J | yes
NB_1F_FEV-6854 | 1 | RDC_NB_1F_FEV-6854 | FEV | Bio-Med Chem Lab 2 N-1345J | yes
NB_1F_FEV-6855 | 1 | RDC_NB_1F_FEV-6855 | FEV | Bio-Med Chem Lab 2 N-1345J | yes
NB_1F_FEV-6856 | 1 | RDC_NB_1F_FEV-6856 | FEV | Bio-Med Chem Lab 2 N-1345J | yes
NB_1F_FEV-6857 | 1 | RDC_NB_1F_FEV-6857 | FEV | Bio-Med Chem Lab 2 N-1345J | yes
NB_1F_FEV-6858 | 1 | RDC_NB_1F_FEV-6858 | FEV | Bio-Med Chem Lab 2 N-1345J | yes
NB_1F_FEV-6859 | 1 | RDC_NB_1F_FEV-6859 | FEV | Bio-Med Chem Lab 2 N-1345J | yes
SB_1F_AT-3501 | 1 | RDC_SB_1F_AT-3501 | AT | Lobby S-0294 | yes
SB_1F_AT-3502 | 1 | RDC_SB_1F_AT-3502 | AT | Lobby S-0294 | yes
SB_1F_AT-3503 | 1 | RDC_SB_1F_AT-3503 | AT | Reception S-0293 | yes
SB_1F_AT-0207 | 1 | RDC_SB_1F_AT-0207 | AT | Open Plan S-1293A | yes
SB_1F_AT-0208 | 1 | RDC_SB_1F_AT-0208 | AT | Open Plan S-1293 | yes
SB_1F_AT-0201A | 1 | RDC_SB_1F_AT-0201A | AT | Policy Executive Director Office S-1240 | yes
SB_1F_AT-0201B | 1 | RDC_SB_1F_AT-0201B | AT | Open Plan S-1229 | yes
SB_1F_AT-0206 | 1 | RDC_SB_1F_AT-0206 | AT | Policy Executive Director Office S-1240 | yes
NB_1F_EV-7631 | 1 | RDC_NB_1F_EV-7631 | EV | Office 05 - 2 WKS- N-1407 | yes
NB_1F_EV-7646 | 1 | RDC_NB_1F_EV-7646 | EV | Exp. Workstation N-1420 | yes
NB_1F_EV-7661 | 1 | RDC_NB_1F_EV-7661 | EV | Office 05 - 2 WKS- N-1401 | yes
NB_1F_EV-7663 | 1 | RDC_NB_1F_EV-7663 | EV | IDF N-1424 | yes
NB_1F_EV-7711 | 1 | RDC_NB_1F_EV-7711 | EV | Workstation N-1442 | yes
NB_1F_EV-7712 | 1 | RDC_NB_1F_EV-7712 | EV | Workstation N-1442 | yes
NB_1F_EV-7861 | 1 | RDC_NB_1F_EV-7861 | EV | Office 05 - 9 WKS N-1461 | yes
NB_1F_EV-7916 | 1 | RDC_NB_1F_EV-7916 | EV | Office 05 - 8 WKS N-1471 | yes
NB_1F_CEV-7521 | 1 | RDC_NB_1F_CEV-7521 | CEV | Isotope N-1404B | yes
NB_1F_FEV-7522 | 1 | RDC_NB_1F_FEV-7522 | FEV | Isotope N-1404B | yes
NB_1F_CEV-7591 | 1 | RDC_NB_1F_CEV-7591 | CEV | HY Room N-1404J | yes
NB_1F_FEV-7602 | 1 | RDC_NB_1F_FEV-7602 | FEV | CELL BIO LABS N-1404K | yes
NB_1F_CEV-7611 | 1 | RDC_NB_1F_CEV-7611 | CEV | TC1 N-1404L | yes
NB_1F_CEV-7761 | 1 | RDC_NB_1F_CEV-7761 | CEV | A/L N-1450D | yes
NB_1F_CEV-7791 | 1 | RDC_NB_1F_CEV-7791 | CEV | A/L N-1450G | yes
NB_1F_FEV-7824 | 1 | RDC_NB_1F_FEV-7824 | FEV | STEM/PCR Open Lab N-1450M | yes
NB_2F_AT-4900 | 1 | RDC_NB_2F_AT-4900 | AT | Normal Electric N-2102 | yes
NB_2F_AT-4910 | 1 | RDC_NB_2F_AT-4910 | AT | Emergency Electr N-2103 | yes
NB_2F_EV-4920 | 1 | RDC_NB_2F_EV-4920 | EV | IDF N-2104 | yes
NB_2F_AT-5930 | 1 | RDC_NB_2F_AT-5930 | AT | Office 04 N-1170 | yes
NB_2F_AT-5940 | 1 | RDC_NB_2F_AT-5940 | AT | Office 05 - 8 WKS- N-1165 | yes
NB_2F_AT-6979 | 1 | RDC_NB_2F_AT-6979 | AT | Normal Elec. N-2107 | yes
NB_2F_AT-6980 | 1 | RDC_NB_2F_AT-6980 | AT | Emer. Elec. N-2108 | yes
NB_2F_EV-6981 | 1 | RDC_NB_2F_EV-6981 | EV | IDF N-2110 | yes
NB_2F_AT-7975 | 1 | RDC_NB_2F_AT-7975 | AT | Normal Elec. N-2111 | yes
NB_2F_AT-7980 | 1 | RDC_NB_2F_AT-7980 | AT | Emer. Elec. N-2112 | yes

## Conflicts
Kind | Register tag | Type | Room in column D
different room | RDC_NB_GF_VAV6210 | VAV | Corr. +N-033B N-0332C
different room | RDC_NB_GF_AT-6210 | AT | Corridor N-0332C
different room | RDC_SB_GF_VAV1003_VEV1002 | VEV | NOC Lab S-0140A
different room | RDC_SB_L0_AT-1002 | AT | Computer Lab S-0139
different room | RDC_SB_L0_AT-1003 | AT | NOC S-0140A
different room | RDC_SB_L0_EV-1002 | EV | NOC S-0140A
different room | RDC_SB_L0_EV-1003 | EV | UPS S-0145
different room | RDC_SB_GF_VAV1004 | VAV | Corridor S-0137 / S-0143
different room | RDC_SB_L0_AT-1004 | AT | Dedicated Cyber SOC/NOC Lab S-0141
different room | RDC_SB_GF_VAV2018 | VAV | Print Hub S-0225
different room | RDC_SB_L0_AT-2018 | AT | PANTRY S-0226
different room | RDC_SB_GF_VAV2033 | VAV | Store S-0275
different room | RDC_SB_L0_AT-2033 | AT | CORRIDOR S-0273
different room | RDC_SB_GF_VAV2035 | VAV | Pantry S-0270
different room | RDC_SB_L0_AT-2035 | AT | MECH S-0272
different room | RDC_SB_GF_VAV2042 | VAV | Corridor S-0273
different room | RDC_SB_L0_AT-2042 | AT | Lobby S-0294
different room | RDC_SB_GF_VAV2043 | VAV | Women S-0281
different room | RDC_SB_L0_AT-2043 | AT | Lobby S-0294
different room | RDC_SB_GF_VAV3018 | VAV | Corridor S-0251
different room | RDC_SB_L0_AT-3018 | AT | Corridor S-0251B
different room | RDC_SB_GF_VAV3019 | VAV | Corridor S-0251
different room | RDC_SB_L0_AT-3019 | AT | Corridor S-0251B
different room | RDC_SB_GF_VAV3033 | VAV | Corridor / Print / Emergency Elec Rm / Normal Elec Rm S-0251 / S-0263 / S-0266 / S-0267
different room | RDC_SB_L0_AT-3033 | AT | Emergency Elec. S-0266
different room | RDC_NB_1F_VAV7705 | VAV | Office 05 - 24 WKS + N-1441 Room N-1442
different room | RDC_NB_1F_AT-7705 | AT | Expansion WORKstation N-1442
different room | RDC_NB_1F_VAV7710 | VAV | Workstation N-1442
different room | RDC_NB_1F_AT-7710 | AT | Office 05 - 24 WKS + N-1441 Room N-1442
different room | RDC_SB_L0_AT-1001 | AT | Corridor S-0137
different room | RDC_SB_L0_EV-1001 | EV | Computer Lab S-0139
wording only | RDC_NB_GF_VAV4235 | VAV | Office 05 -8WS- N-0250
wording only | RDC_NB_GF_AT-4235 | AT | Workstation N-0250
wording only | RDC_NB_GF_VAV4260 | VAV | Office 05 -8WS- N-0255
wording only | RDC_NB_GF_AT-4260 | AT | Workstation N-0255
wording only | RDC_NB_GF_VAV6205_EV6206 | EV | Conf N-0331
wording only | RDC_NB_GF_AT-6205 | AT | Conference N-0331
wording only | RDC_NB_GF_VAV6285_EV6286 | EV | Conf N-0358
wording only | RDC_NB_GF_AT-6285 | AT | Conference N-0358
wording only | RDC_NB_GF_VAV7425 | VAV | Office 05-8-WKS N-0452
wording only | RDC_NB_GF_AT-7425 | AT | Workstation N-0452
wording only | RDC_NB_GF_VAV7460 | VAV | Office 05-8-WKS N-0457
wording only | RDC_NB_GF_AT-7460 | AT | Workstation N-0457
wording only | RDC_NB_GF_VAV7485 | VAV | Office 05-8-WKS N-0462
wording only | RDC_NB_GF_AT-7485 | AT | WORKSTATION N-0462
wording only | RDC_SB_1F_VAV2531 | VAV | Director Office S-1241
wording only | RDC_SB_1F_AT-2531 | AT | Director Ofice S-1241
wording only | RDC_SB_GF_VAV0002 | VAV | Main Lobby S-0102
wording only | RDC_SB_L0_AT-0002 | AT | Employee Entry Lobby S-0102
wording only | RDC_SB_GF_VAV0007 | VAV | Conference S-0109
wording only | RDC_SB_L0_AT-0007 | AT | Conf S-0109
wording only | RDC_SB_GF_VAV0016 | VAV | Conference S-0118
wording only | RDC_SB_L0_AT-0016 | AT | Conf S-0118
wording only | RDC_SB_GF_VAV1008 | VAV | Cyber Embedded Sys. S-0146
wording only | RDC_SB_L0_AT-1008 | AT | Cyber/Embedded/Dist System Electrical Lab S-0146
wording only | RDC_SB_GF_VAV3031 | VAV | Server S-0264
wording only | RDC_SB_L0_AT-3031 | AT | IT Server S-0264
wording only | RDC_SB_GF_VAV3034 | VAV | Vestibule S-0293
wording only | RDC_SB_L0_AT-3034 | AT | Reception / Vestibule S-0293