## README
QNL Equipment Metadata - Full Metadata
Qatar National Library, Education City BP#7A
What this workbook is
One sheet per equipment type. Every row is a single manufacturer property for a single unit, and carries the source PDF and the page it was read from, so any value can be traced back to the document.
Sheets
AHU | 15 air handling units, AHU-001 to AHU-015. AS BUILT general arrangement drawings, drawing 1844-SD-05-AC-0077, Mercury Mena for Qatar Foundation, 26-10-2015 / 28-11-2015.
Closed Control Units | 5 selection sheets covering CC/B/01 to CC/B/09. Emerson Network Power, issued by Qatar Site & Power, April and October 2013.
Climate Control Units | Museum Climate Controls MCG-10P humidity control unit with its VCB1000 blower option and AF4 intake air filter.
FCU | 28 Euroclima selection sheets covering positions on Basement, 1F and 2F.
Heat Exchangers | 5 Alfa Laval plate heat exchangers, PHX/B/01 to PHX/B/05, with the manufacturer's construction data and the M10-MFM thermal specification.
Pumps | 4 Armstrong horizontal split case chilled water pumps, CHWP/B/01 to CHWP/B/04, with the full Armstrong submittal - pump, motor, seal, materials and dimensions.
Exhaust Fans | 39 exhaust fans - mostly Nuaire, two Colasit - from the supplied schedule spreadsheet.
Generators | One standby diesel generator from the GENERATOR ASSET LIST, a multi-equipment asset register.
Pressurization Unit | PU/B/01 (PRO1) - Armstrong 3750 2 EM-S pressurisation unit plus a Reflex DE10 1000 litre expansion tank.
CAV Units | 42 constant air volume boxes, one row per box, from six schedules.
VAV Units | 180 variable air volume boxes, one row per box, from six schedules.
DX Units | 21 DX split systems, DX/B/01-20 and DX/RP/21, from the schematic riser and the SYSTEM DETAILS equipment schedule, which names models for 16 of them.
Ontology Scope | Every distinct property in this workbook, the reference-model predicate it maps to, and whether it belongs in the ontology at all.
Units | Every source unit, the Dar Cairo unit it maps to, the factor applied, and whether Dar Cairo uses that unit at all.
Columns
Equipment Tag | The position or unit reference exactly as the source document writes it.
Model | Manufacturer model designation where the sheet gives one.
Component | The part of the unit the property belongs to - cooling coil, supply fan, condenser, etc.
Property | The property name, kept close to the source wording.
Value (as printed) | The value exactly as the document prints it. Nothing converted, rounded or inferred.
Unit (as printed) | The unit exactly as the document prints it.
Value (Dar Cairo) | The same quantity converted to the unit Dar Cairo uses for it.
Unit (QUDT) | The QUDT unit token to write into brick:hasUnit.
Conversion | The arithmetic applied, and any assumption behind it. Blank means no conversion was needed.
Source File | The document the value came from - a PDF, a spreadsheet, or a supplied drawing image.
Page | Where in that document: a 1-based page for a PDF, a sheet and row for a spreadsheet, the schedule title for a drawing.
Note | Anything that qualifies the value - a quantity off, a source conflict, a mislabelled row.
Units
- The source documents are transcribed in their own units, and each row then carries the same quantity in the unit Dar Cairo uses for it. Both are kept side by side: the printed pair stays traceable to the page, the converted pair is what goes into brick:hasUnit.
- Targets were read off DarCairo_V93.csv, not assumed. Air flow and water flow both land on unit:L-PER-SEC (para:ratedSupplyAirFlowrate, para:ratedChilledWaterFlowrate and their siblings), power on unit:KiloW (brick:ratedPowerInput, brick:coolingCapacity), length on unit:M (para:ratedHead), relative humidity on unit:PERCENT_RH rather than unit:PERCENT.
- The Units sheet lists every mapping, the factor applied, and the four QUDT units Dar Cairo has never used - mass, mass flow and velocity, which it carries no quantity for. Those need the PARA team's confirmation.
- Converting kg/s to l/s treats water as 1 kg/l. At 7-15 degC it is about 0.9997 kg/l, so the converted flow is high by roughly 0.03%.
What belongs in the ontology
- Most of this workbook is engineering reference, not ontology metadata. Dar Cairo, QF SSC and QF HQ agree on a short vocabulary for equipment - about twenty predicates - and everything outside it has no precedent in any of them.
- Brick 1.4 is checked FIRST, per the class ladder - it is step 2 and the reference models are step 3. Brick has no water or air flow-rate entity property and no heat-exchanger duty property, which is why Dar Cairo minted para:ratedWaterFlowrate, para:ratedChilledWaterFlowrate and the air-flowrate family. Where Brick does carry the term it wins: brick:coolingCapacity for heat exchanger duty, brick:ratedCurrentInput for full load current, brick:operationalStageCount for a fan's speed count, and brick:Condensing_Unit as the entity an outdoor unit's model sits on.
- Every row carries an 'Ontology predicate' and a 'Scope'. core means it maps unambiguously to a Brick 1.4 entity property or a predicate the reference models use. candidate means the match is plausible but needs a decision. reference means neither Brick nor any reference model carries anything like it - dimensions, weights, materials, seal specifications, sound power levels, filter part numbers, psychrometrics, warranty text. Those rows stay because they are useful to engineers, not because they will be modelled.
- The Ontology Scope sheet lists every distinct property with its verdict, the predicate it maps to and where that predicate comes from - Brick 1.4, Dar Cairo, QF SSC or QF HQ.
- The predicates in play: para:ratedSupplyAirFlowrate, rec:modelNumber, rec:manufacturedBy, para:ratedReheatCapacity, brick:ratedPowerInput, para:ratedChilledWaterFlowrate, brick:coolingCapacity, para:ratedSpeed, brick:ratedCurrentInput, para:ratedExhaustAirFlowrate, brick:operationalStageCount, para:ratedHead, para:refrigerant, rec:installationDate, para:ratedWaterFlowrate, para:Rated_Tank_Level.
- One open point: the expansion tank's 1000 litre capacity is written as para:Rated_Tank_Level at the user's direction. brick:volume exists in Brick 1.4 and by the ladder would outrank a para: term - reversible in one line of ontology_map.py if the team prefers it.
- An outdoor DX unit's model belongs on its own brick:Condensing_Unit entity, which Brick 1.4 carries, so no para: class needed to be minted for it. Those entities are not in this workbook yet - it holds the model against the indoor unit that names it.
- A component's own maker is not the equipment's manufacturer. The pump's mechanical seal is made by Armstrong and its motor by WEG; neither becomes rec:manufacturedBy on the pump.
- The QF HQ v0.4 draft was read for structure, not for units - several of its rows carry a wrong brick:hasUnit (an air flow tagged unit:V, a cooling capacity tagged unit:HZ). Dar Cairo remains the authority for unit choice, as the Units sheet records.
Read before using the data
- Values are transcribed from the documents as printed. Where a document contradicts itself the conflict is recorded as a 'Data quality' row rather than resolved - those need the supplier's answer.
- AHU-011 carries two Item 3 ELECTRIC COIL blocks; the first is an unfilled template (capacity POW, stages NST, entering air AON, leaving air AOF). The populated block is the one recorded.
- MCG-10P size is given as 500 x 650 x 650 mm on the specification sheet and 475 x 430 x 400 mm on dimension drawing MCG10P-1. Both are recorded; neither is confirmed.
- On 27 of the 28 Euroclima sheets the air pressure drop row is printed as 'Perdita di carico aria' with the unit [degC]. It is air-side pressure drop in Pa - page 2 labels the same row correctly.
- The CC/B/05,06,07 sheet heading reads M5DUA while its own Unit row reads M5DOA.
- The heat exchanger and pump rows come from an image of a schedule drawing whose title block is cropped out. They carry no drawing number, sheet or revision - ask for the sheet reference before handover.
- The exhaust fan schedule uses two identifier shapes: 28 slash-separated tags (EF/B/nn, EF/RP/n) and 11 underscore-separated (TEF_B01A, KEF_101). Both were kept as written because the tag is the BMS join key. EF/B numbering also runs 4 to 16 with no 1, 2 or 3.
- The pump model designation ends in 55KW. The schedule states no motor rating of its own, so no rated-power property was created from it - confirm against the pump submittal.
- The same schedule drawing carries a SCHEDULE OF PRESSURIZATION UNIT (PU/B/01, Armstrong 3750 2 EM-S). It was not asked for and is not in this workbook; say the word and it gets a sheet.
- On the DX sheet the cooling figure is the load printed on the ROOM box, not a per-unit capacity. Rooms served by two or three units are not split by the schematic, so do not write it as brick:coolingCapacity on a unit without a per-unit duty.
- The DX indoor-to-outdoor pairing recorded from the schematic's matching numbers is NOT reliable. SYSTEM DETAILS Table 3.6 shows DX/B/03, 04, 08, 09 and 14 each take an X2 outdoor model - two condensers per indoor unit - so those five need two DX/OD tags each and the numbering does not say which two. The pipework layout plan is still needed. DX/OD/05 is also marked (ST.BY) while DX/B/05 is not.
- Table 3.6 covers DX/B/01 to DX/B/16 only, so DX/B/17, 18, 19, 20 and DX/RP/21 still carry no model. DX/B/08 reads PUHZ-RP2S0X2 where its twin DX/B/09 reads PUHZ-RP250X2 - almost certainly a misprint, recorded as printed. The PEAD, PCA and PUHZ prefixes are Mitsubishi Electric Mr. Slim naming, but no document states a manufacturer, so none was inferred.
- CAV and VAV schedules write many references as ranges. Each range is split into one row per box, so every box carries its own air flow, heating capacity, model and make, and keeps a 'Scheduled as' row naming the line it came from. A range is only split when its box count matches the stated quantity; three do not and keep the printed reference with a Data quality row instead: VAV/1F/S15/012, VAV/B/S14/009 TO 012 and VAV/B/S10/001 & 008.
- Two drawings schedule the same basement S10/S15 VAV boxes and disagree on VAV/B/S15/001 TO 004 (261 l/s against 251 l/s). Both are recorded against their own drawing. On the second 1F schedule VAV/1F/S15/014 TO 015 also falls inside VAV/1F/S15/013 TO 020 with a different flow and model.
- VAV/1F/S11/022 was scheduled twice; the user confirmed the standalone row governs (220 l/s, NBOQOB200), so the overlapping VAV/1F/S11/022 TO 24 row is read as covering 023 and 024 only. Five further rows carrying out-of-range box numbers were excluded on instruction.
- The fire damper and supply/return grille schedules on the same images were struck through in red and were read as cancelled, so they are not in this workbook.
- PHX/B/05 exists only on the Alfa Laval data and the SYSTEM DETAILS schedule - the drawing schedule stops at PHX/B/04. It is a 300 kW M10-MFM described as the 'Main HEX'. SYSTEM DETAILS states one hot-side temperature across all five rows (15.5 in / 6.5 out) but the M10-MFM specification gives 50.0 in / 20.0 out. Both are recorded; the conflict is unresolved.
- SYSTEM DETAILS writes the pump tags with dashes (CHWP-B-01) and tags the pressurisation unit PRO1, where the drawing schedules write CHWP/B/01 and PU/B/01. The slash forms are used as the Equipment Tag because they match the rest of the workbook; the alternates are recorded as an 'Alternate reference' property on each unit. Confirm which the BMS uses.
- The Armstrong pump submittal is dimensioned in inches and pounds and is marked NOT for CONSTRUCTION. Its weight of 1874 lb converts to 850 kg against the drawing schedule's 843 kg. Its letter callouts (D, HA, HB, ...) are keyed to an outline drawing that does not say which feature each measures.
- The GENERATOR ASSET LIST is a multi-equipment asset register. The row cropped off below the generator belongs to different equipment, so the single row on the Generators sheet is the complete record for this machine. Its ASSET TAG NUMBER column reads 'GENERATOR SET' - the same text as the equipment name - so it does not identify an individual machine; only the serial number does.
- These are equipment selection and as-built documents, not nameplate photographs. Where the installed plant differs from the selection, the installed plant governs.
Source documents
Ahu_manual_1.pdf | 8 pages - AHU-001 to AHU-008 general arrangement drawings
ahu_2.pdf | 7 pages - AHU-009 to AHU-015 general arrangement drawings
qnl_closed_control_units_manual.pdf | 17 pages - Emerson closed control unit selections
climate_control_units_manual.pdf | 7 pages - Museum Climate Controls MCG-10P data sheets
FCU_Manual.pdf | 29 pages - Euroclima fan coil unit selection sheets
MEP schedule drawing | image - Heat exchanger, pump and pressurization unit schedules, supplied as an image in chat. The image crops the title block, so no drawing number, sheet number or revision is recorded against these rows.
Book1.xlsx | Sheet1, 39 rows - Exhaust fan schedule - equipment tag, model, manufacturer and air flow only
CAV and VAV schedules | 6 + 6 schedules - Supplied as drawing images in chat, title blocks cropped. Each schedule is a separate source; the Page column names which.
Armstrong submittal | TENDER301358.1 rev3, p14/22 - Full nameplate for the chilled water pumps - pump design, WEG motor, mechanical seal, materials and imperial dimensions
Alfa Laval PHE data | 2 sheets - Construction comparison for T20-BFG and M10-MFM, and the M10-MFM thermal specification for PHX/B/05
SYSTEM DETAILS | Tables 3.1-3.3, 3.6 - Duty/standby split for the pumps and heat exchangers, the pressurisation unit broken into its two components, and indoor/outdoor models for DX/B/01 to DX/B/16
GENERATOR ASSET LIST | image - Asset register row for a standby diesel generator
DX split system schematic | image - Riser diagram giving the room each DX unit serves, its design condition and a room cooling load

## AHU
AHU
Air handling units AHU-001 to AHU-015 - AS BUILT general arrangement drawings, drawing 1844-SD-05-AC-0077 (Mercury Mena for Qatar Foundation). The drawings give no unit-level model designation, so Model is blank; component models (coil, fan, motor) appear as their own rows.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
AHU-001 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Drawing | Sheet | Sht.001 OF 015 | [5 empty] | reference | Ahu_manual_1.pdf | 1 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-001 |  | Silencer (item 4) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Silencer (item 4) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 1 | Tissue faced complete with perforated plate
AHU-001 |  | Silencer (item 5) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Silencer (item 5) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 1 | Tissue faced complete with perforated plate
AHU-001 |  | Polyseal filter (item 6) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Polyseal filter (item 6) - PRE | Arrestance | 80-85% | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Polyseal filter (item 6) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 1 | Quantity off: 16
AHU-001 |  | Polyseal filter (item 6) - PRE | Part no AHFL-3702001224 (W x H x D mm) | 290X595X48 | mm | 0.29 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 1 | Quantity off: 2
AHU-001 |  | Polyseal filter (item 6) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Polyseal filter (item 6) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Polyseal filter (item 6) - MAIN | Efficiency | 90-95% | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Polyseal filter (item 6) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 1 | Quantity off: 16
AHU-001 |  | Polyseal filter (item 6) - MAIN | Part no AHFL-5234200320 (W x H x D mm) | 287X592X535 | mm | 0.287 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 1 | Quantity off: 2
AHU-001 |  | Polyseal filter (item 6) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Polyseal filter (item 8) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Polyseal filter (item 8) - PRE | Arrestance | 80-85% | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Polyseal filter (item 8) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 1 | Quantity off: 2
AHU-001 |  | Polyseal filter (item 8) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Polyseal filter (item 8) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Polyseal filter (item 8) - MAIN | Efficiency | 90-95% | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Polyseal filter (item 8) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 1 | Quantity off: 2
AHU-001 |  | Polyseal filter (item 8) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Model | 1226C3808517125W0176 |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Rows | 8 | n | 8 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Fin spacing | 2.5 | mm | 0.0025 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Fins | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Connection supply | 4" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Connection return | 4" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Water flow | 9.48 | kg/s | 9.48 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Water pressure drop | 45.13 | kPa | 45130 | unit:PA | kPa x 1000 |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Total capacity | 318.13 | kW | 318.13 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Entering air (DB) | 24.5 | degC | 24.5 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Entering air RH | 41 | % | 41 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Leaving air (DB) | 8.99 | degC | 8.99 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Leaving air RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Connection type | FLANGED DN100 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Drain connection | 1.1/2" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Description | EXTERNAL AUXILIARY COOLING COIL | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Air flow | 9360 | m3/h | 2600 | unit:L-PER-SEC | m3/h / 3.6 |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Air mass flow | 3.12 | kg/s | 3.12 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Water flow | 15493 | l/h | 4.3036 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Water mass flow | 4.3 | kg/s | 4.3 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Water pressure drop | 22.8 | kPa | 22800 | unit:PA | kPa x 1000 |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Entering air | 27.4 | degC | 27.4 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Entering air RH | 57 | % | 57 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Leaving air | 14.5 | degC | 14.5 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Leaving air RH | 98 | % | 98 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Air pressure drop | 23 | Pa | 23 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Total capacity | 144 | kW | 144 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Tubes | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Electric coil | Total capacity | 57 | kW | 57 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Electric coil | Entering air | 19 | degC | 19 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Electric coil | Leaving air | 22 | degC | 22 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Fan model | TZAF 630 T2L |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 1 | on the fan sub-entity, not the parent unit
AHU-001 |  | Supply fan | Impeller type | BC | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Air flow | 14.9 | m3/s | 14900 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | External static pressure | 540 | Pa | 540 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Fan static pressure | 1367 | Pa | 1367 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Speed | 2517 | rpm | 2517 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Absorbed power | 13.06 | kW | 13.06 | unit:KiloW |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 92 / 90 / 93 / 87 / 85 / 79 / 74 / 70 | dB | 92 / 90 / 93 / 87 / 85 / 79 / 74 / 70 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Drain plug | YES | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Fan pulley | SPB 200x2 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Note | BOTH FANS RUNNING AT 50% DUTY | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Rating | 18.5 | kW | 18.5 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Frame type | 180 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Full load speed | 2517 | rpm | 2517 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Full load current | 34 | A | 34 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 1 | Brick 1.4 entity property; no reference model uses it yet
AHU-001 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Motor pulley | SPB 236x2 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Belts | 2 | n | 2 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Belt type | SPB 1900 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Fan model | TZAF 630 T1 |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 1 | on the fan sub-entity, not the parent unit
AHU-001 |  | Return fan | Impeller type | BC | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Air flow | 14.9 | m3/s | 14900 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | Ahu_manual_1.pdf | 1 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-001 |  | Return fan | External static pressure | 335 | Pa | 335 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Fan static pressure | 719 | Pa | 719 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Speed | 2012 | rpm | 2012 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Absorbed power | 7.82 | kW | 7.82 | unit:KiloW |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 89 / 87 / 90 / 84 / 82 / 76 / 71 / 67 | dB | 89 / 87 / 90 / 84 / 82 / 76 / 71 / 67 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Volume control | INVERTER CONTROL | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Finish | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Shaft guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Inspection door | YES | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Inlet guards | YES | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Stainless steel shaft | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Drain plug | YES | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Spark minimising features | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | AVM type | SPRING | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan | Fan pulley | SPZ 200x3 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Rating | 11 | kW | 11 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Frame type | 160 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Full load speed | 2012 | rpm | 2012 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Full load current | 21 | A | 21 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 1 | Brick 1.4 entity property; no reference model uses it yet
AHU-001 |  | Return fan drive motor | Winding type | SINGLE | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Starting method | INVERTER | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Motor pulley | SPZ 190x3 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Belts | 3 | n | 3 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Belt type | SPZ 1562 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Finish | Frames | NATURAL | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Finish | Extract fan base | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-001 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | Ahu_manual_1.pdf | 1
AHU-002 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Drawing | Sheet | Sht.002 OF 015 | [5 empty] | reference | Ahu_manual_1.pdf | 2 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-002 |  | Silencer (item 1) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Silencer (item 1) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 2 | Tissue faced complete with perforated plate
AHU-002 |  | Silencer (item 6) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 2 | Tissue faced complete with perforated plate
AHU-002 |  | Polyseal filter (item 2) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Polyseal filter (item 2) - PRE | Arrestance | 80-85% | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 2 | Quantity off: 12
AHU-002 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702001224 (W x H x D mm) | 290X595X48 | mm | 0.29 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 2 | Quantity off: 3
AHU-002 |  | Polyseal filter (item 2) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Polyseal filter (item 2) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Polyseal filter (item 2) - MAIN | Efficiency | 90-95% | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 595X595X535 | mm | 0.595 x 0.595 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 2 | Quantity off: 12
AHU-002 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234200320 (W x H x D mm) | 290X595X535 | mm | 0.29 x 0.595 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 2 | Quantity off: 3
AHU-002 |  | Polyseal filter (item 2) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Model | 1226C6408261120W02(64+64) |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Rows | 8 | n | 8 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Fin spacing | 2 | mm | 0.002 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Fins | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Connection supply | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Connection return | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Water flow | 12.52 | kg/s | 12.52 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Water pressure drop | 20.3 | kPa | 20300 | unit:PA | kPa x 1000 |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Total capacity | 419.67 | kW | 419.67 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Entering air (DB) | 27.6 | degC | 27.6 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Entering air RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Leaving air (DB) | 9.98 | degC | 9.98 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Leaving air RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Drain connection | 1.1/2" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Note | SINGLE BLOCK COIL | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Electric coil | Total capacity | 47 | kW | 47 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Electric coil | Entering air | 18.5 | degC | 18.5 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Electric coil | Leaving air | 21.5 | degC | 21.5 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Fan model | TZAF 800 T2L |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 2 | on the fan sub-entity, not the parent unit
AHU-002 |  | Supply fan | Impeller type | BC | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Air flow | 12.3 | m3/s | 12300 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | External static pressure | 485 | Pa | 485 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Fan static pressure | 1455 | Pa | 1455 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Speed | 1245 | rpm | 1245 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Absorbed power | 22.36 | kW | 22.36 | unit:KiloW |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 89 / 90 / 94 / 90 / 87 / 80 / 77 / 70 | dB | 89 / 90 / 94 / 90 / 87 / 80 / 77 / 70 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Drain plug | YES | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Frame type | 200 | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 2 | Brick 1.4 entity property; no reference model uses it yet
AHU-002 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Finish | Frames | NATURAL | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Finish | Extract fan base | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-002 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | Ahu_manual_1.pdf | 2
AHU-003 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Drawing | Sheet | Sht.003 OF 015 | [5 empty] | reference | Ahu_manual_1.pdf | 3 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-003 |  | Silencer (item 1) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Silencer (item 1) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 3 | Tissue faced complete with perforated plate
AHU-003 |  | Silencer (item 6) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 3 | Tissue faced complete with perforated plate
AHU-003 |  | Polyseal filter (item 2) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Polyseal filter (item 2) - PRE | Arrestance | 80-85% | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 3 | Quantity off: 12
AHU-003 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702001224 (W x H x D mm) | 290X595X48 | mm | 0.29 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 3 | Quantity off: 3
AHU-003 |  | Polyseal filter (item 2) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Polyseal filter (item 2) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Polyseal filter (item 2) - MAIN | Efficiency | 90-95% | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 595X595X535 | mm | 0.595 x 0.595 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 3 | Quantity off: 12
AHU-003 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234200320 (W x H x D mm) | 290X595X535 | mm | 0.29 x 0.595 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 3 | Quantity off: 3
AHU-003 |  | Polyseal filter (item 2) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Model | 1226C6408261120W02(64+64) |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Rows | 8 | n | 8 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Fin spacing | 2 | mm | 0.002 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Fins | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Connection supply | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Connection return | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Water flow | 12.52 | kg/s | 12.52 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Water pressure drop | 20.3 | kPa | 20300 | unit:PA | kPa x 1000 |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Total capacity | 419.67 | kW | 419.67 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Entering air (DB) | 27.6 | degC | 27.6 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Entering air RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Leaving air (DB) | 9.98 | degC | 9.98 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Leaving air RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Drain connection | 1.1/2" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Note | SINGLE BLOCK COIL | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Electric coil | Total capacity | 47 | kW | 47 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Electric coil | Entering air | 18.5 | degC | 18.5 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Electric coil | Leaving air | 21.5 | degC | 21.5 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Fan model | TZAF 800 T2L |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 3 | on the fan sub-entity, not the parent unit
AHU-003 |  | Supply fan | Impeller type | BC | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Air flow | 12.3 | m3/s | 12300 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | External static pressure | 510 | Pa | 510 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Fan static pressure | 1455 | Pa | 1455 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Speed | 1245 | rpm | 1245 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Absorbed power | 22.41 | kW | 22.41 | unit:KiloW |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 89 / 90 / 94 / 90 / 87 / 80 / 77 / 70 | dB | 89 / 90 / 94 / 90 / 87 / 80 / 77 / 70 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Drain plug | YES | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Frame type | 200 | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 3 | Brick 1.4 entity property; no reference model uses it yet
AHU-003 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Finish | Frames | NATURAL | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Finish | Extract fan base | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-003 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | Ahu_manual_1.pdf | 3
AHU-004 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Drawing | Sheet | Sht.004 OF 015 | [5 empty] | reference | Ahu_manual_1.pdf | 4 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-004 |  | Silencer (item 1) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Silencer (item 1) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 4 | Tissue faced complete with perforated plate
AHU-004 |  | Silencer (item 6) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 4 | Tissue faced complete with perforated plate
AHU-004 |  | Polyseal filter (item 2) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Polyseal filter (item 2) - PRE | Arrestance | 80-85% | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 4 | Quantity off: 12
AHU-004 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702001224 (W x H x D mm) | 290X595X48 | mm | 0.29 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 4 | Quantity off: 3
AHU-004 |  | Polyseal filter (item 2) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Polyseal filter (item 2) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Polyseal filter (item 2) - MAIN | Efficiency | 90-95% | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 595X595X535 | mm | 0.595 x 0.595 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 4 | Quantity off: 12
AHU-004 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234200320 (W x H x D mm) | 290X595X535 | mm | 0.29 x 0.595 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 4 | Quantity off: 3
AHU-004 |  | Polyseal filter (item 2) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Model | 1226C6408261120W01(64+64) |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Rows | 8 | n | 8 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Fin spacing | 2 | mm | 0.002 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Fins | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Connection supply | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Connection return | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Water flow | 12.52 | kg/s | 12.52 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Water pressure drop | 20.3 | kPa | 20300 | unit:PA | kPa x 1000 |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Total capacity | 419.67 | kW | 419.67 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Entering air (DB) | 27.6 | degC | 27.6 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Entering air RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Leaving air (DB) | 9.98 | degC | 9.98 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Leaving air RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Drain connection | 1.1/2" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Note | SINGLE BLOCK COIL | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Electric coil | Total capacity | 47 | kW | 47 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Electric coil | Entering air | 18.5 | degC | 18.5 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Electric coil | Leaving air | 21.5 | degC | 21.5 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Fan model | TZAF 800 T2L |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 4 | on the fan sub-entity, not the parent unit
AHU-004 |  | Supply fan | Impeller type | BC | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Air flow | 12.3 | m3/s | 12300 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | External static pressure | 390 | Pa | 390 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Fan static pressure | 1201 | Pa | 1201 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Speed | 1317 | rpm | 1317 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Absorbed power | 18.98 | kW | 18.98 | unit:KiloW |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 88 / 89 / 93 / 89 / 86 / 79 / 76 / 69 | dB | 88 / 89 / 93 / 89 / 86 / 79 / 76 / 69 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Drain plug | YES | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Fan pulley | 212ø (SPBx4) | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Frame type | 200 | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Full load speed | 1482 | rpm | 1482 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 4 | Brick 1.4 entity property; no reference model uses it yet
AHU-004 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Motor pulley | 190ø (SPBx4) | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Belts | 4 | n | 4 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Belt type | SPB 1800 | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Finish | Frames | NATURAL | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Finish | Extract fan base | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-004 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | Ahu_manual_1.pdf | 4
AHU-005 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Drawing | Sheet | Sht.005 OF 015 | [5 empty] | reference | Ahu_manual_1.pdf | 5 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-005 |  | Silencer (item 1) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Silencer (item 1) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 5 | Tissue faced complete with perforated plate
AHU-005 |  | Silencer (item 6) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 5 | Tissue faced complete with perforated plate
AHU-005 |  | Polyseal filter (item 2) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Polyseal filter (item 2) - PRE | Arrestance | 80-85% | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 5 | Quantity off: 18
AHU-005 |  | Polyseal filter (item 2) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Polyseal filter (item 2) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Polyseal filter (item 2) - MAIN | Efficiency | 90-95% | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 5 | Quantity off: 18
AHU-005 |  | Polyseal filter (item 2) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Model | 1226C6408352125W01(64+64) |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Rows | 8 | n | 8 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Fin spacing | 2.5 | mm | 0.0025 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Fins | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Connection supply | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Connection return | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Water flow | 15.69 | kg/s | 15.69 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Water pressure drop | 37.38 | kPa | 37380 | unit:PA | kPa x 1000 |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Total capacity | 526.13 | kW | 526.13 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Entering air (DB) | 26.6 | degC | 26.6 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Entering air RH | 52.4 | % | 52.4 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Leaving air (DB) | 10.7 | degC | 10.7 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Leaving air RH | 99.9 | % | 99.9 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Drain connection | 1.1/2" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Note | SINGLE BLOCK COIL | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Electric coil | Total capacity | 63 | kW | 63 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Electric coil | Entering air | 18.8 | degC | 18.8 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Electric coil | Leaving air | 21.8 | degC | 21.8 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Fan model | TZAF 900 T2L |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 5 | on the fan sub-entity, not the parent unit
AHU-005 |  | Supply fan | Impeller type | BC | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Air flow | 16.5 | m3/s | 16500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | External static pressure | 770 | Pa | 770 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Fan static pressure | 1583 | Pa | 1583 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Speed | 1313 | rpm | 1313 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Absorbed power | 32.87 | kW | 32.87 | unit:KiloW |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 94 / 95 / 95 / 92 / 87 / 80 / 76 / 71 | dB | 94 / 95 / 95 / 92 / 87 / 80 / 76 / 71 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Drain plug | YES | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Fan pulley | 355ø (SPBx3) | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Rating | 45 | kW | 45 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Frame type | 225 | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Efficiency class | IE2 | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Full load speed | 1480 | rpm | 1480 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Full load current | 81 | A | 81 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 5 | Brick 1.4 entity property; no reference model uses it yet
AHU-005 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Motor pulley | 315ø (SPBx3) | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Belts | 3 | n | 3 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Belt type | SPB 2680 | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Finish | Frames | NATURAL | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Finish | Extract fan base | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-005 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | Ahu_manual_1.pdf | 5
AHU-006 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Drawing | Sheet | Sht.006 OF 015 | [5 empty] | reference | Ahu_manual_1.pdf | 6 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-006 |  | Silencer (item 1) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Silencer (item 1) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 6 | Tissue faced complete with perforated plate
AHU-006 |  | Silencer (item 6) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 6 | Tissue faced complete with perforated plate
AHU-006 |  | Polyseal filter (item 2) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Polyseal filter (item 2) - PRE | Arrestance | 80-85% | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 6 | Quantity off: 18
AHU-006 |  | Polyseal filter (item 2) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Polyseal filter (item 2) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Polyseal filter (item 2) - MAIN | Efficiency | 90-95% | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 6 | Quantity off: 18
AHU-006 |  | Polyseal filter (item 2) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Model | 1226C6408352125W01(64+64) |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Rows | 8 | n | 8 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Fin spacing | 2.5 | mm | 0.0025 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Fins | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Connection supply | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Connection return | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Water flow | 15.68 | kg/s | 15.68 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Water pressure drop | 37.15 | kPa | 37150 | unit:PA | kPa x 1000 |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Total capacity | 525.67 | kW | 525.67 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Entering air (DB) | 26.6 | degC | 26.6 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Entering air RH | 53 | % | 53 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Leaving air (DB) | 9.64 | degC | 9.64 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Leaving air RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Drain connection | 1.1/2" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Note | SINGLE BLOCK COIL | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Electric coil | Total capacity | 63 | kW | 63 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Electric coil | Entering air | 18.8 | degC | 18.8 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Electric coil | Leaving air | 21.8 | degC | 21.8 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Fan model | TZAF 900 T2L |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 6 | on the fan sub-entity, not the parent unit
AHU-006 |  | Supply fan | Impeller type | BC | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Air flow | 16.5 | m3/s | 16500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | External static pressure | 630 | Pa | 630 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Fan static pressure | 1420 | Pa | 1420 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Speed | 1285 | rpm | 1285 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Absorbed power | 29.86 | kW | 29.86 | unit:KiloW |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 94 / 95 / 95 / 92 / 87 / 80 / 76 / 71 | dB | 94 / 95 / 95 / 92 / 87 / 80 / 76 / 71 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Drain plug | YES | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Fan pulley | SPB-180x4 | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Rating | 37 | kW | 37 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Frame type | 250 | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Efficiency class | IE2 | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Full load speed | 980 | rpm | 980 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Full load current | 67.3 | A | 67.3 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 6 | Brick 1.4 entity property; no reference model uses it yet
AHU-006 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Motor pulley | SPB-236x4 | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Belt type | SPB-2120x4 | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Finish | Frames | NATURAL | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Finish | Extract fan base | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-006 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | Ahu_manual_1.pdf | 6
AHU-007 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Drawing | Sheet | Sht.007 OF 015 | [5 empty] | reference | Ahu_manual_1.pdf | 7 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-007 |  | Silencer (item 1) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Silencer (item 1) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 7 | Tissue faced complete with perforated plate
AHU-007 |  | Silencer (item 6) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 7 | Tissue faced complete with perforated plate
AHU-007 |  | Polyseal filter (item 2) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Polyseal filter (item 2) - PRE | Arrestance | 80-85% | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 7 | Quantity off: 18
AHU-007 |  | Polyseal filter (item 2) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Polyseal filter (item 2) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Polyseal filter (item 2) - MAIN | Efficiency | 90-95% | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 7 | Quantity off: 18
AHU-007 |  | Polyseal filter (item 2) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Model | 1226C6408352125W01(64+64) |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Rows | 8 | n | 8 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Fin spacing | 2.5 | mm | 0.0025 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Fins | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Connection supply | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Connection return | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Water flow | 15.68 | kg/s | 15.68 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Water pressure drop | 37.15 | kPa | 37150 | unit:PA | kPa x 1000 |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Total capacity | 525.67 | kW | 525.67 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Entering air (DB) | 26.6 | degC | 26.6 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Entering air RH | 53.6 | % | 53.6 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Leaving air (DB) | 9.64 | degC | 9.64 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Leaving air RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Drain connection | 1.1/2" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Note | SINGLE BLOCK COIL | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Electric coil | Total capacity | 63 | kW | 63 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Electric coil | Entering air | 18.8 | degC | 18.8 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Electric coil | Leaving air | 21.8 | degC | 21.8 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Fan model | TZAF 900 T2 |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 7 | on the fan sub-entity, not the parent unit
AHU-007 |  | Supply fan | Impeller type | BC | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Air flow | 16.5 | m3/s | 16500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | External static pressure | 960 | Pa | 960 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Fan static pressure | 1823 | Pa | 1823 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Speed | 1316 | rpm | 1316 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Absorbed power | 37.3 | kW | 37.3 | unit:KiloW |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 95 / 96 / 96 / 93 / 88 / 81 / 77 / 72 | dB | 95 / 96 / 96 / 93 / 88 / 81 / 77 / 72 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Drain plug | YES | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Fan pulley | SPB-315x3 | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Rating | 45 | kW | 45 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Frame type | 225 | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Efficiency class | IE2 | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Full load speed | 1480 | rpm | 1480 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Full load current | 81 | A | 81 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 7 | Brick 1.4 entity property; no reference model uses it yet
AHU-007 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Motor pulley | SPB-250x3 | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Belt type | SPB-2680 | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Finish | Frames | NATURAL | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Finish | Extract fan base | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-007 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | Ahu_manual_1.pdf | 7
AHU-008 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Drawing | Sheet | Sht.008 OF 015 | [5 empty] | reference | Ahu_manual_1.pdf | 8 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-008 |  | Silencer (item 1) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Silencer (item 1) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 8 | Tissue faced complete with perforated plate
AHU-008 |  | Silencer (item 6) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 8 | Tissue faced complete with perforated plate
AHU-008 |  | Polyseal filter (item 2) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Polyseal filter (item 2) - PRE | Arrestance | 80-85% | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 8 | Quantity off: 9
AHU-008 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702001224 (W x H x D mm) | 290X595X48 | mm | 0.29 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 8 | Quantity off: 3
AHU-008 |  | Polyseal filter (item 2) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Polyseal filter (item 2) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Polyseal filter (item 2) - MAIN | Efficiency | 90-95% | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 8 | Quantity off: 9
AHU-008 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234200320 (W x H x D mm) | 287X592X535 | mm | 0.287 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 8 | Quantity off: 3
AHU-008 |  | Polyseal filter (item 2) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Model | 1226C6408189120W0164 |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Rows | 8 | n | 8 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Fin spacing | 2 | mm | 0.002 | unit:M | mm / 1000 |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Fins | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Connection supply | 4" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Connection return | 4" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Water flow | 9.04 | kg/s | 9.04 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Water pressure drop | 47.1 | kPa | 47100 | unit:PA | kPa x 1000 |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Total capacity | 303.68 | kW | 303.68 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Entering air (DB) | 27.2 | degC | 27.2 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Entering air RH | 47 | % | 47 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Leaving air (DB) | 9.12 | degC | 9.12 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Leaving air RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Connection type | FLANGED DN100 | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Drain connection | 1.1/2" | BSP |  |  | thread designation, not a quantity |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Electric coil | Total capacity | 35 | kW | 35 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Electric coil | Entering air | 17.9 | degC | 17.9 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Electric coil | Leaving air | 20.9 | degC | 20.9 | unit:DEG_C |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Fan model | TZAF 710 FF T2L |  |  |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 8 | on the fan sub-entity, not the parent unit
AHU-008 |  | Supply fan | Impeller type | BC | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Air flow | 9.2 | m3/s | 9200 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | External static pressure | 975 | Pa | 975 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Fan static pressure | 1830 | Pa | 1830 | unit:PA |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Speed | 2517 | rpm | 2517 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Absorbed power | 20.9 | kW | 20.9 | unit:KiloW |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 90 / 89 / 94 / 88 / 87 / 80 / 76 / 70 | dB | 90 / 89 / 94 / 88 / 87 / 80 / 76 / 70 | unit:DeciB |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Drain plug | YES | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Fan pulley | SPA 400-02 | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Frame type | 200 | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Efficiency class | IE2 | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Full load speed | 2517 | rpm | 2517 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 8 | Brick 1.4 entity property; no reference model uses it yet
AHU-008 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Motor pulley | SPA 400-02 | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Belts | 2 | n | 2 | unit:UNITLESS |  |  | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Belt type | SPA 3282 LP | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Finish | Frames | NATURAL | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Finish | Extract fan base | N/A | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-008 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | Ahu_manual_1.pdf | 8
AHU-009 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Drawing | Sheet | Sht.009 OF 015 | [5 empty] | reference | ahu_2.pdf | 1 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-009 |  | Silencer (item 1) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 1
AHU-009 |  | Silencer (item 1) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | ahu_2.pdf | 1 | Tissue faced complete with perforated plate
AHU-009 |  | Silencer (item 6) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 1
AHU-009 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | ahu_2.pdf | 1 | Tissue faced complete with perforated plate
AHU-009 |  | Polyseal filter (item 2) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Polyseal filter (item 2) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 1 | Quantity off: 12
AHU-009 |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702001224 (W x H x D mm) | 290X595X48 | mm | 0.29 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 1 | Quantity off: 3
AHU-009 |  | Polyseal filter (item 2) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Polyseal filter (item 2) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Polyseal filter (item 2) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 595X595X535 | mm | 0.595 x 0.595 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 1 | Quantity off: 12
AHU-009 |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234200320 (W x H x D mm) | 290X595X535 | mm | 0.29 x 0.595 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 1 | Quantity off: 3
AHU-009 |  | Polyseal filter (item 2) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Model | 1226C6408261120W 02(64+64) |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Rows | 8 | n | 8 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Fin spacing | 2 | mm | 0.002 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Fins | Cu | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Connection supply | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Connection return | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Water flow | 12.05 | kg/s | 12.05 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Water pressure drop | 18.75 | kPa | 18750 | unit:PA | kPa x 1000 |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Total capacity | 400.82 | kW | 400.82 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Entering air (DB) | 27.3 | degC | 27.3 | unit:DEG_C |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Entering air RH | 51 | % | 51 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Leaving air (DB) | 10 | degC | 10 | unit:DEG_C |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Leaving air RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Drain connection | 1.1/2" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Note | SINGLE BLOCK COIL | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Electric coil | Total capacity | 46 | kW | 46 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 1
AHU-009 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Electric coil | Entering air | 18.6 | degC | 18.6 | unit:DEG_C |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Electric coil | Leaving air | 21.6 | degC | 21.6 | unit:DEG_C |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Fan model | TZAF 800 T2L |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 1 | on the fan sub-entity, not the parent unit
AHU-009 |  | Supply fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Air flow | 12 | m3/s | 12000 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 1
AHU-009 |  | Supply fan | External static pressure | 585 | Pa | 585 | unit:PA |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Fan static pressure | 1435 | Pa | 1435 | unit:PA |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Speed | 1176 | rpm | 1176 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Absorbed power | 21.44 | kW | 21.44 | unit:KiloW |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 89 / 90 / 94 / 90 / 87 / 80 / 77 / 70 | dB | 89 / 90 / 94 / 90 / 87 / 80 / 77 / 70 | unit:DeciB |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Frame type | 200 | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 1 | Brick 1.4 entity property; no reference model uses it yet
AHU-009 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 1
AHU-009 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Finish | Frames | NATURAL | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Finish | Extract fan base | N/A | [5 empty] | reference | ahu_2.pdf | 1
AHU-009 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | ahu_2.pdf | 1
AHU-010 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Drawing | Sheet | Sht.010 OF 015 | [5 empty] | reference | ahu_2.pdf | 2 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-010 |  | Silencer (item 5) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 2
AHU-010 |  | Silencer (item 5) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | ahu_2.pdf | 2 | Tissue faced complete with perforated plate
AHU-010 |  | Silencer (item 6) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 2
AHU-010 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | ahu_2.pdf | 2 | Tissue faced complete with perforated plate
AHU-010 |  | Polyseal filter (item 1) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Polyseal filter (item 1) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Polyseal filter (item 1) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 2 | Quantity off: 3
AHU-010 |  | Polyseal filter (item 1) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Polyseal filter (item 1) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Polyseal filter (item 1) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Polyseal filter (item 1) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 2 | Quantity off: 3
AHU-010 |  | Polyseal filter (item 1) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Polyseal filter (item 7) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Polyseal filter (item 7) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Polyseal filter (item 7) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 2 | Quantity off: 9
AHU-010 |  | Polyseal filter (item 7) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Polyseal filter (item 7) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Polyseal filter (item 7) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Polyseal filter (item 7) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 2 | Quantity off: 9
AHU-010 |  | Polyseal filter (item 7) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Model | 1226C5808161120W0158 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Rows | 8 | n | 8 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Fin spacing | 2 | mm | 0.002 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Fins | Cu | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Connection supply | 3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Connection return | 3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Water flow | 5.6 | kg/s | 5.6 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Water pressure drop | 25.84 | kPa | 25840 | unit:PA | kPa x 1000 |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Total capacity | 187.83 | kW | 187.83 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Entering air (DB) | 26.2 | degC | 26.2 | unit:DEG_C |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Entering air RH | 41 | % | 41 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Leaving air (DB) | 9.12 | degC | 9.12 | unit:DEG_C |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Leaving air RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Drain connection | 1.1/2" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Electric coil | Total capacity | 28 | kW | 28 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 2
AHU-010 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Electric coil | Entering air | 18.3 | degC | 18.3 | unit:DEG_C |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Electric coil | Leaving air | 21.3 | degC | 21.3 | unit:DEG_C |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Fan model | TZAF 630 T2L |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 2 | on the fan sub-entity, not the parent unit
AHU-010 |  | Supply fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Air flow | 7.2 | m3/s | 7200 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 2
AHU-010 |  | Supply fan | External static pressure | 770 | Pa | 770 | unit:PA |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Fan static pressure | 1547 | Pa | 1547 | unit:PA |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Speed | 1640 | rpm | 1640 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Absorbed power | 14.04 | kW | 14.04 | unit:KiloW |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 90 / 88 / 91 / 85 / 83 / 77 / 72 / 68 | dB | 90 / 88 / 91 / 85 / 83 / 77 / 72 / 68 | unit:DeciB |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Rating | 18.5 | kW | 18.5 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Frame type | 180 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Full load current | 34 | A | 34 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 2 | Brick 1.4 entity property; no reference model uses it yet
AHU-010 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Fan model | TZAF 710 T1 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 2 | on the fan sub-entity, not the parent unit
AHU-010 |  | Return fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Air flow | 7.2 | m3/s | 7200 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 2 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-010 |  | Return fan | External static pressure | 510 | Pa | 510 | unit:PA |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Fan static pressure | 886 | Pa | 886 | unit:PA |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Speed | 1080 | rpm | 1080 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 2
AHU-010 |  | Return fan | Absorbed power | 8.06 | kW | 8.06 | unit:KiloW |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 88 / 90 / 85 / 81 / 79 / 73 / 70 / 63 | dB | 88 / 90 / 85 / 81 / 79 / 73 / 70 / 63 | unit:DeciB |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Rating | 11 | kW | 11 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Frame type | 160 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Full load speed | 960 | rpm | 960 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Full load current | 22.9 | A | 22.9 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 2 | Brick 1.4 entity property; no reference model uses it yet
AHU-010 |  | Return fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 2
AHU-010 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Finish | Frames | NATURAL | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Finish | Extract fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 2
AHU-010 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | ahu_2.pdf | 2
AHU-011 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Drawing | Sheet | Sht.011 OF 015 | [5 empty] | reference | ahu_2.pdf | 3 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-011 |  | Silencer (item 5) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 3
AHU-011 |  | Silencer (item 5) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | ahu_2.pdf | 3 | Tissue faced complete with perforated plate
AHU-011 |  | Silencer (item 6) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 3
AHU-011 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | ahu_2.pdf | 3 | Tissue faced complete with perforated plate
AHU-011 |  | Polyseal filter (item 1) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Polyseal filter (item 1) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Polyseal filter (item 1) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 3 | Quantity off: 5
AHU-011 |  | Polyseal filter (item 1) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Polyseal filter (item 1) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Polyseal filter (item 1) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Polyseal filter (item 1) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 3 | Quantity off: 5
AHU-011 |  | Polyseal filter (item 1) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Polyseal filter (item 7) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Polyseal filter (item 7) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Polyseal filter (item 7) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 3 | Quantity off: 15
AHU-011 |  | Polyseal filter (item 7) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Polyseal filter (item 7) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Polyseal filter (item 7) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Polyseal filter (item 7) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 3 | Quantity off: 15
AHU-011 |  | Polyseal filter (item 7) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Model | UCUC-FEZN P404R7R-23T-28924-2.0PA4OC2 1/2" |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Rows | 7 | n | 7 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Fin spacing | 2 | mm | 0.002 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Fins | Cu | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Connection supply | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Connection return | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Water flow | 16.26 | kg/s | 16.26 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Water pressure drop | 48 | kPa | 48000 | unit:PA | kPa x 1000 |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Total capacity | 545.2 | kW | 545.2 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Entering air (DB) | 22.5 | degC | 22.5 | unit:DEG_C |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Entering air RH | 40.5 | % | 40.5 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Leaving air (DB) | 12 | degC | 12 | unit:DEG_C |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Leaving air RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Drain connection | 1" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Note | SINGLE BLOCK COIL | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Electric coil | Total capacity | 51 | kW | 51 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 3
AHU-011 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Electric coil | Entering air | 17.8 | degC | 17.8 | unit:DEG_C |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Electric coil | Leaving air | 20.8 | degC | 20.8 | unit:DEG_C |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Fan model | TZAF 900 T1 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 3 | on the fan sub-entity, not the parent unit
AHU-011 |  | Supply fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Air flow | 13.4 | m3/s | 13400 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 3
AHU-011 |  | Supply fan | External static pressure | 813 | Pa | 813 | unit:PA |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Fan static pressure | 1403 | Pa | 1403 | unit:PA |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Speed | 1097 | rpm | 1097 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Absorbed power | 23.1 | kW | 23.1 | unit:KiloW |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 91 / 96 / 91 / 88 / 84 / 77 / 73 / 67 | dB | 91 / 96 / 91 / 88 / 84 / 77 / 73 / 67 | unit:DeciB |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Frame type | 225 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Full load speed | 980 | rpm | 980 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Full load current | 56.2 | A | 56.2 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 3 | Brick 1.4 entity property; no reference model uses it yet
AHU-011 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Fan model | TZAF 900 T1 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 3 | on the fan sub-entity, not the parent unit
AHU-011 |  | Return fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Air flow | 13.4 | m3/s | 13400 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 3 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-011 |  | Return fan | External static pressure | 413 | Pa | 413 | unit:PA |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Fan static pressure | 793 | Pa | 793 | unit:PA |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Speed | 827 | rpm | 827 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 3
AHU-011 |  | Return fan | Absorbed power | 13.98 | kW | 13.98 | unit:KiloW |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 88 / 93 / 88 / 85 / 81 / 74 / 70 / 64 | dB | 88 / 93 / 88 / 85 / 81 / 74 / 70 / 64 | unit:DeciB |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Rating | 18.5 | kW | 18.5 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Frame type | 200 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Full load speed | 975 | rpm | 975 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Full load current | 36.4 | A | 36.4 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 3 | Brick 1.4 entity property; no reference model uses it yet
AHU-011 |  | Return fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 3
AHU-011 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Finish | Frames | NATURAL | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Finish | Extract fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | ahu_2.pdf | 3
AHU-011 |  | Data quality | Drawing anomaly | Item 3 ELECTRIC COIL appears twice: the first block is an unfilled template (TOTAL CAPACITY=POW, STAGES=NST, ENTERING AIR=AON, LEAVING AIR=AOF, description cell reads BLOCKHEIGHT). The second, populated block is recorded here. | [6 empty] | ahu_2.pdf | 3 | Confirm with the supplier before use
AHU-012 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Drawing | Sheet | Sht.012 OF 015 | [5 empty] | reference | ahu_2.pdf | 4 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-012 |  | Silencer (item 5) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 4
AHU-012 |  | Silencer (item 5) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | ahu_2.pdf | 4 | Tissue faced complete with perforated plate
AHU-012 |  | Silencer (item 6) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 4
AHU-012 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | ahu_2.pdf | 4 | Tissue faced complete with perforated plate
AHU-012 |  | Polyseal filter (item 1) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Polyseal filter (item 1) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Polyseal filter (item 1) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 4 | Quantity off: 3
AHU-012 |  | Polyseal filter (item 1) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Polyseal filter (item 1) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Polyseal filter (item 1) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Polyseal filter (item 1) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 4 | Quantity off: 3
AHU-012 |  | Polyseal filter (item 1) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Polyseal filter (item 7) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Polyseal filter (item 7) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Polyseal filter (item 7) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 4 | Quantity off: 9
AHU-012 |  | Polyseal filter (item 7) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Polyseal filter (item 7) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Polyseal filter (item 7) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Polyseal filter (item 7) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 4 | Quantity off: 9
AHU-012 |  | Polyseal filter (item 7) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Model | 1226C5606179120W0256 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Rows | 6 | n | 6 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Fin spacing | 2 | mm | 0.002 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Fins | Cu | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Connection supply | 3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Connection return | 3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Water flow | 6.29 | kg/s | 6.29 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Water pressure drop | 28 | kPa | 28000 | unit:PA | kPa x 1000 |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Total capacity | 211.5 | kW | 211.5 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Entering air (DB) | 27 | degC | 27 | unit:DEG_C |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Entering air RH | 53 | % | 53 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Leaving air (DB) | 12.1 | degC | 12.1 | unit:DEG_C |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Leaving air RH | 99.6 | % | 99.6 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Drain connection | 1" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Electric coil | Total capacity | 29 | kW | 29 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 4
AHU-012 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Electric coil | Entering air | 18 | degC | 18 | unit:DEG_C |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Electric coil | Leaving air | 21 | degC | 21 | unit:DEG_C |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Fan model | TZAF 710 T1 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 4 | on the fan sub-entity, not the parent unit
AHU-012 |  | Supply fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Air flow | 7.5 | m3/s | 7500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 4
AHU-012 |  | Supply fan | External static pressure | 625 | Pa | 625 | unit:PA |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Fan static pressure | 1209 | Pa | 1209 | unit:PA |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Speed | 1175 | rpm | 1175 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Absorbed power | 11.3 | kW | 11.3 | unit:KiloW |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 85 / 84 / 89 / 83 / 82 / 75 / 71 / 65 | dB | 85 / 84 / 89 / 83 / 82 / 75 / 71 / 65 | unit:DeciB |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Rating | 15 | kW | 15 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Frame type | 160 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Full load speed | 1460 | rpm | 1460 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Full load current | 28.1 | A | 28.1 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 4 | Brick 1.4 entity property; no reference model uses it yet
AHU-012 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Fan model | TZFA 710 T1 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 4 | on the fan sub-entity, not the parent unit
AHU-012 |  | Return fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Air flow | 7.5 | m3/s | 7500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 4 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-012 |  | Return fan | External static pressure | 305 | Pa | 305 | unit:PA |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Fan static pressure | 682 | Pa | 682 | unit:PA |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Speed | 1020 | rpm | 1020 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 4
AHU-012 |  | Return fan | Absorbed power | 6.75 | kW | 6.75 | unit:KiloW |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 86 / 88 / 83 / 79 / 77 / 71 / 68 / 61 | dB | 86 / 88 / 83 / 79 / 77 / 71 / 68 / 61 | unit:DeciB |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Rating | 11 | kW | 11 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Frame type | 160 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Full load speed | 960 | rpm | 960 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Full load current | 22.9 | A | 22.9 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 4 | Brick 1.4 entity property; no reference model uses it yet
AHU-012 |  | Return fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 4
AHU-012 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Finish | Frames | NATURAL | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Finish | Extract fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 4
AHU-012 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | ahu_2.pdf | 4
AHU-013 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Drawing | Sheet | Sht.013 OF 015 | [5 empty] | reference | ahu_2.pdf | 5 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-013 |  | Silencer (item 5) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 5
AHU-013 |  | Silencer (item 5) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | ahu_2.pdf | 5 | Tissue faced complete with perforated plate
AHU-013 |  | Silencer (item 6) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 5
AHU-013 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | ahu_2.pdf | 5 | Tissue faced complete with perforated plate
AHU-013 |  | Polyseal filter (item 1) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Polyseal filter (item 1) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Polyseal filter (item 1) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 5 | Quantity off: 3
AHU-013 |  | Polyseal filter (item 1) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Polyseal filter (item 1) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Polyseal filter (item 1) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Polyseal filter (item 1) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 5 | Quantity off: 3
AHU-013 |  | Polyseal filter (item 1) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Polyseal filter (item 7) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Polyseal filter (item 7) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Polyseal filter (item 7) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 5 | Quantity off: 9
AHU-013 |  | Polyseal filter (item 7) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Polyseal filter (item 7) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Polyseal filter (item 7) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Polyseal filter (item 7) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 5 | Quantity off: 9
AHU-013 |  | Polyseal filter (item 7) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Model | 1226C6206179130W0162 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Rows | 6 | n | 6 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Fin spacing | 3 | mm | 0.003 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Fins | Cu | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Connection supply | 3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Connection return | 3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Water flow | 6.81 | kg/s | 6.81 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Water pressure drop | 28.38 | kPa | 28380 | unit:PA | kPa x 1000 |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Total capacity | 228 | kW | 228 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Entering air (DB) | 27.8 | degC | 27.8 | unit:DEG_C |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Entering air RH | 52 | % | 52 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Leaving air (DB) | 12 | degC | 12 | unit:DEG_C |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Leaving air RH | 99.3 | % | 99.3 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Drain connection | 1" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Electric coil | Total capacity | 32 | kW | 32 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 5
AHU-013 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Electric coil | Entering air | 17.7 | degC | 17.7 | unit:DEG_C |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Electric coil | Leaving air | 20.7 | degC | 20.7 | unit:DEG_C |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Fan model | TZAF 710 T1 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 5 | on the fan sub-entity, not the parent unit
AHU-013 |  | Supply fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Air flow | 8.5 | m3/s | 8500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 5
AHU-013 |  | Supply fan | External static pressure | 826 | Pa | 826 | unit:PA |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Fan static pressure | 1410 | Pa | 1410 | unit:PA |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Speed | 1317 | rpm | 1317 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Absorbed power | 14.93 | kW | 14.93 | unit:KiloW |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 87 / 86 / 91 / 85 / 84 / 77 / 73 / 67 | dB | 87 / 86 / 91 / 85 / 84 / 77 / 73 / 67 | unit:DeciB |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Rating | 18.5 | kW | 18.5 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Frame type | 180 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Full load current | 34 | A | 34 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 5 | Brick 1.4 entity property; no reference model uses it yet
AHU-013 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Fan model | TZAF 710 T1 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 5 | on the fan sub-entity, not the parent unit
AHU-013 |  | Return fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Air flow | 8.5 | m3/s | 8500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 5 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-013 |  | Return fan | External static pressure | 606 | Pa | 606 | unit:PA |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Fan static pressure | 997 | Pa | 997 | unit:PA |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Speed | 1175 | rpm | 1175 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 5
AHU-013 |  | Return fan | Absorbed power | 10.92 | kW | 10.92 | unit:KiloW |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 84 / 83 / 88 / 82 / 81 / 74 / 70 / 64 | dB | 84 / 83 / 88 / 82 / 81 / 74 / 70 / 64 | unit:DeciB |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Rating | 15 | kW | 15 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Frame type | 160 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Full load speed | 1460 | rpm | 1460 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Supply | 415V/50Hz | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Full load current | 28.1 | A | 28.1 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 5 | Brick 1.4 entity property; no reference model uses it yet
AHU-013 |  | Return fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 5
AHU-013 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Finish | Frames | NATURAL | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Finish | Extract fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 5
AHU-013 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | ahu_2.pdf | 5
AHU-014 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Drawing | Sheet | Sht.014 OF 015 | [5 empty] | reference | ahu_2.pdf | 6 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-014 |  | Silencer (item 5) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 6
AHU-014 |  | Silencer (item 5) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | ahu_2.pdf | 6 | Tissue faced complete with perforated plate
AHU-014 |  | Silencer (item 6) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 6
AHU-014 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | ahu_2.pdf | 6 | Tissue faced complete with perforated plate
AHU-014 |  | Polyseal filter (item 1) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Polyseal filter (item 1) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Polyseal filter (item 1) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 6 | Quantity off: 4
AHU-014 |  | Polyseal filter (item 1) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Polyseal filter (item 1) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Polyseal filter (item 1) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Polyseal filter (item 1) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 6 | Quantity off: 4
AHU-014 |  | Polyseal filter (item 1) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Polyseal filter (item 7) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Polyseal filter (item 7) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Polyseal filter (item 7) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 6 | Quantity off: 12
AHU-014 |  | Polyseal filter (item 7) - PRE | Part no AHFL-3702001224 (W x H x D mm) | 290X595X48 | mm | 0.29 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 6 | Quantity off: 3
AHU-014 |  | Polyseal filter (item 7) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Polyseal filter (item 7) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Polyseal filter (item 7) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Polyseal filter (item 7) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 6 | Quantity off: 12
AHU-014 |  | Polyseal filter (item 7) - MAIN | Part no AHFL-5234200320 (W x H x D mm) | 287X592X535 | mm | 0.287 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 6 | Quantity off: 3
AHU-014 |  | Polyseal filter (item 7) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Model | 1226C6405255120W0280 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Rows | 5 | n | 5 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Fin spacing | 2 | mm | 0.002 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Fins | Cu | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Connection supply | 4" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Connection return | 4" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Water flow | 9.33 | kg/s | 9.33 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Water pressure drop | 26.44 | kPa | 26440 | unit:PA | kPa x 1000 |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Total capacity | 313 | kW | 313 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Entering air (DB) | 26.2 | degC | 26.2 | unit:DEG_C |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Entering air RH | 54 | % | 54 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Leaving air (DB) | 11.8 | degC | 11.8 | unit:DEG_C |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Leaving air RH | 99.7 | % | 99.7 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Connection type | FLANGED DN100 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Drain connection | 1" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Electric coil | Total capacity | 45 | kW | 45 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 6
AHU-014 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Electric coil | Entering air | 18.3 | degC | 18.3 | unit:DEG_C |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Electric coil | Leaving air | 21.3 | degC | 21.3 | unit:DEG_C |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Fan model | TZAF 800 T2L |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 6 | on the fan sub-entity, not the parent unit
AHU-014 |  | Supply fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Air flow | 11.8 | m3/s | 11800 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 6
AHU-014 |  | Supply fan | External static pressure | 737 | Pa | 737 | unit:PA |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Fan static pressure | 1324 | Pa | 1324 | unit:PA |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Speed | 1176 | rpm | 1176 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Absorbed power | 19.56 | kW | 19.56 | unit:KiloW |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 88 / 89 / 93 / 89 / 86 / 79 / 76 / 69 | dB | 88 / 89 / 93 / 89 / 86 / 79 / 76 / 69 | unit:DeciB |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Frame type | 200 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Supply | 400V/50Hz | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 6 | Brick 1.4 entity property; no reference model uses it yet
AHU-014 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Fan model | TZAF 800 T1 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 6 | on the fan sub-entity, not the parent unit
AHU-014 |  | Return fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Air flow | 11.8 | m3/s | 11800 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 6 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-014 |  | Return fan | External static pressure | 442 | Pa | 442 | unit:PA |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Fan static pressure | 827 | Pa | 827 | unit:PA |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Speed | 1026 | rpm | 1026 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 6
AHU-014 |  | Return fan | Absorbed power | 13.25 | kW | 13.25 | unit:KiloW |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 90 / 91 / 89 / 86 / 83 / 77 / 72 / 64 | dB | 90 / 91 / 89 / 86 / 83 / 77 / 72 / 64 | unit:DeciB |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Rating | 18.5 | kW | 18.5 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Frame type | 200 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Full load speed | 975 | rpm | 975 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Supply | 400V/50Hz | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Full load current | 36.4 | A | 36.4 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 6 | Brick 1.4 entity property; no reference model uses it yet
AHU-014 |  | Return fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 6
AHU-014 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Finish | Frames | NATURAL | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Finish | Extract fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 6
AHU-014 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | ahu_2.pdf | 6
AHU-015 |  | Drawing | Drawing number | 1844-SD-05-AC-0077 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Drawing | Sheet | Sht.015 OF 015 | [5 empty] | reference | ahu_2.pdf | 7 | AS BUILT general arrangement, Mercury Mena / Qatar Foundation
AHU-015 |  | Silencer (item 5) | Silencer length | 900 | mm | 0.9 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 7
AHU-015 |  | Silencer (item 5) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | dB | 8 / 12 / 21 / 30 / 39 / 38 / 27 / 23 | unit:DeciB |  |  | reference | ahu_2.pdf | 7 | Tissue faced complete with perforated plate
AHU-015 |  | Silencer (item 6) | Silencer length | 1200 | mm | 1.2 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 7
AHU-015 |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | dB | 9 / 15 / 28 / 38 / 48 / 47 / 33 / 27 | unit:DeciB |  |  | reference | ahu_2.pdf | 7 | Tissue faced complete with perforated plate
AHU-015 |  | Polyseal filter (item 1) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Polyseal filter (item 1) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Polyseal filter (item 1) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 7 | Quantity off: 6
AHU-015 |  | Polyseal filter (item 1) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Polyseal filter (item 1) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Polyseal filter (item 1) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Polyseal filter (item 1) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 7 | Quantity off: 6
AHU-015 |  | Polyseal filter (item 1) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Polyseal filter (item 7) - PRE | Media | AmerGlas5700 G3 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Polyseal filter (item 7) - PRE | Arrestance | 80-85% | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Polyseal filter (item 7) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 595X595X48 | mm | 0.595 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 7 | Quantity off: 12
AHU-015 |  | Polyseal filter (item 7) - PRE | Part no AHFL-3702001224 (W x H x D mm) | 290X595X48 | mm | 0.29 x 0.595 x 0.048 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 7 | Quantity off: 3
AHU-015 |  | Polyseal filter (item 7) - PRE | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Polyseal filter (item 7) - MAIN | Media | SYNTHETIC F8 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Polyseal filter (item 7) - MAIN | Efficiency | 90-95% | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Polyseal filter (item 7) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 592X592X535 | mm | 0.592 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 7 | Quantity off: 12
AHU-015 |  | Polyseal filter (item 7) - MAIN | Part no AHFL-5234200320 (W x H x D mm) | 287X592X535 | mm | 0.287 x 0.592 x 0.535 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 7 | Quantity off: 3
AHU-015 |  | Polyseal filter (item 7) - MAIN | Spare sets | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Model | 1226C6406276120W02(48+48) |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Rows | 6 | n | 6 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Fin spacing | 2 | mm | 0.002 | unit:M | mm / 1000 |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Fins | Cu | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Tubes | Cu | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Connection supply | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Connection return | 2x3" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Water flow | 15.47 | kg/s | 15.47 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Water pressure drop | 42.78 | kPa | 42780 | unit:PA | kPa x 1000 |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Total capacity | 518.09 | kW | 518.09 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Entering air (DB) | 32 | degC | 32 | unit:DEG_C |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Entering air RH | 46 | % | 46 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Leaving air (DB) | 12.1 | degC | 12.1 | unit:DEG_C |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Leaving air RH | 99.7 | % | 99.7 | unit:PERCENT_RH |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Entering water | 7 | degC | 7 | unit:DEG_C |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Leaving water | 15 | degC | 15 | unit:DEG_C |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Glycol type | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Glycol | N/A | % | N/A | unit:PERCENT |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Connection type | FLANGED DN80 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Moisture eliminator | YES | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Binder tapping points | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Drain connection | 1" | BSP |  |  | thread designation, not a quantity |  | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Drain pan | Drain Standard Sloping - Stst 304 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Casing | Galvanized | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Note | SINGLE BLOCK COIL | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Electric coil | Electrical supply | 415/240v | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Electric coil | Total capacity | 64 | kW | 64 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 7
AHU-015 |  | Electric coil | Stages | 1 | n | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Electric coil | Entering air | 16 | degC | 16 | unit:DEG_C |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Electric coil | Leaving air | 20 | degC | 20 | unit:DEG_C |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Electric coil | Note | ELEMENT SHEATHED WITH HIGH TEMPERATURE MANUAL RESET CUTOUT | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Fan model | TZAF 800 T2L |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 7 | on the fan sub-entity, not the parent unit
AHU-015 |  | Supply fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Air flow | 12.8 | m3/s | 12800 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 7
AHU-015 |  | Supply fan | External static pressure | 991 | Pa | 991 | unit:PA |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Fan static pressure | 1588 | Pa | 1588 | unit:PA |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Speed | 1256 | rpm | 1256 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Absorbed power | 25.33 | kW | 25.33 | unit:KiloW |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 90 / 91 / 95 / 91 / 88 / 81 / 78 / 71 | dB | 90 / 91 / 95 / 91 / 88 / 81 / 78 / 71 | unit:DeciB |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Rating | 37 | kW | 37 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Frame type | 225 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Full load speed | 1480 | rpm | 1480 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Supply | 400V/50Hz | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Full load current | 66.2 | A | 66.2 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 7 | Brick 1.4 entity property; no reference model uses it yet
AHU-015 |  | Supply fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Fan model | TZAF 800 T1 |  |  |  |  | rec:modelNumber | core | ahu_2.pdf | 7 | on the fan sub-entity, not the parent unit
AHU-015 |  | Return fan | Impeller type | BC | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Air flow | 12.8 | m3/s | 12800 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 7 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-015 |  | Return fan | External static pressure | 546 | Pa | 546 | unit:PA |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Fan static pressure | 932 | Pa | 932 | unit:PA |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Speed | 1087 | rpm | 1087 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 7
AHU-015 |  | Return fan | Absorbed power | 16.33 | kW | 16.33 | unit:KiloW |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 87 / 88 / 92 / 88 / 85 / 78 / 75 / 68 | dB | 87 / 88 / 92 / 88 / 85 / 78 / 75 / 68 | unit:DeciB |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Volume control | INVERTER CONTROL | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Finish | STANDARD | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Shaft guards | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Inspection door | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Inlet guards | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Stainless steel shaft | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Drain plug | YES | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | Spark minimising features | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan | AVM type | SPRING | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Rating | 22 | kW | 22 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Frame type | 200 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Efficiency class | IE2 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Full load speed | 975 | rpm | 975 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Supply | 400V/50Hz | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Full load current | 42 | A | 42 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 7 | Brick 1.4 entity property; no reference model uses it yet
AHU-015 |  | Return fan drive motor | Winding type | SINGLE | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Starting current | N/A | A | N/A | unit:A |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Starting method | INVERTER | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Thermistor fitted | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Epoxy paint finish | N/A | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Spare drive belts | 1 | set(s) | 1 | unit:UNITLESS |  |  | reference | ahu_2.pdf | 7
AHU-015 |  | Flexible connection | Material | PVC COATED POLYESTER FABRIC, CONFORMS TO DIN 24194 | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Finish | Frames | NATURAL | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Finish | Panels outer skin | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Finish | Panels inner skin | GALVANIZED | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Finish | Panels inner skin at coil section | GREY PLASTISOL | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Finish | Unit base | GALVANISED MILD STEEL | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Finish | Supply fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Finish | Extract fan base | STANDARD | [5 empty] | reference | ahu_2.pdf | 7
AHU-015 |  | Insulation | Panels | PANELS DOUBLE SKINNED 50 mm THICK - INSULATION FOAM | [5 empty] | reference | ahu_2.pdf | 7

## Closed Control Units
Closed Control Units
Emerson Network Power closed control units CC/B/01 to CC/B/09 - selection sheets issued by Qatar Site & Power.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
CC/B/01,02 | S1GOA | Identification | Manufacturer | Emerson Network Power |  |  |  |  | rec:manufacturedBy | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Identification | Model | S1GOA |  |  |  |  | rec:modelNumber | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Identification | System type | Direct expansion (DX), air-cooled | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Identification | Issued by | Qatar Site & Power | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Identification | Selection date | Monday, April 15, 2013 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Identification | Selection software release | Rel. 7.4 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Design condition | Unit inlet air temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Design condition | Unit inlet air relative humidity | 45 | % | 45 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Design condition | Unit airflow | 3700 | m3/h | 1027.78 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Design condition | ESP | 75 | Pa | 75 | unit:PA |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Design condition | Sea level | 0 | m | 0 | unit:M |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Design condition | Refrigerant | R410A |  |  |  |  | para:refrigerant | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Design condition | Unit power supply | 400 V/3 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Total cooling capacity | 14 | kW | 14 | unit:KiloW |  | brick:coolingCapacity | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Sensible cooling capacity | 13.9 | kW | 13.9 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | SHR | 0.99 |  | 0.99 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Off coil air temperature | 10.8 | degC | 10.8 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Off coil air relative humidity | 91.5 | % | 91.5 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Room SPL (@ 2 m, f.f) | 47.7 | dB(A) | 47.7 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Condensing temperature | 57.4 | degC | 57.4 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Unit power input | 5.52 | kW | 5.52 | unit:KiloW |  | brick:ratedPowerInput | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Unit EER | 2.54 |  | 2.54 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | System power input | 6.07 | kW | 6.07 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | System EER | 2.31 |  | 2.31 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Internal filter class (EN779 std) | G4 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Width | 750 | mm | 0.75 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Depth | 750 | mm | 0.75 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Height | 1950 | mm | 1.95 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Weight | 250 | kg | 250 | unit:KiloGM | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Fans | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Fans | Type | Normal | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Fans | Power supply | 400/3/50 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Fans | Power input | 1 x 0.43 | kW | 1 x 0.43 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Fans | Operating ampere | 1 x 0.70 | A | 1 x 0.70 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Fans | Full load ampere | 1 x 4.00 | A | 1 x 4.00 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Fans | Locked rotor amp. | 1 x 0.10 | A | 1 x 0.10 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Fans | Fan input voltage | 6 | V | 6 | unit:V |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Compressors | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Compressors | Power supply | 400 V/3 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Compressors | Power input | 1 x 5.09 | kW | 1 x 5.09 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Compressors | Compressors COP | 2.74 |  | 2.74 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Compressors | Operating ampere | 1 x 8.82 | A | 1 x 8.82 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Compressors | Full load ampere | 1 x 11.80 | A | 1 x 11.80 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Compressors | Locked rotor amp. | 1 x 64.00 | A | 1 x 64.00 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Condenser model | HCR33 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Version | Standard | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Air discharge | Vertical | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Power supply | 230 V/1 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Variex | No | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Heat load | 19.1 | kW | 19.1 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Outdoor air temperature | 50 | degC | 50 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Condenser airflow (@ max speed) | 7400 | m3/h | 2055.56 | unit:L-PER-SEC | m3/h / 3.6 |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Condenser actual airflow | 7400 | m3/h | 2055.56 | unit:L-PER-SEC | m3/h / 3.6 |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Condenser ESP (@ max speed) | 0 | Pa | 0 | unit:PA |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Max outdoor SPL (@ 5 m, f.f.) | 50 | dB(A) | 50 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Actual outdoor SPL (@ 5 m, f.f.) | 50 | dB(A) | 50 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Power input | 0.55 | kW | 0.55 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Full load ampere | 2.5 | A | 2.5 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Locked rotor amp. | 4.8 | A | 4.8 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Width | 1112 | mm | 1.112 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Depth | 1340 | mm | 1.34 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Height | 907 | mm | 0.907 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Condenser | Weight | 75 | kg | 75 | unit:KiloGM | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Option - electrical re-heating | Max re-heating capacity | 5.85 | kW | 5.85 | unit:KiloW |  | para:ratedReheatCapacity | core | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - electrical re-heating | FLA | 8.4 | A | 8.4 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - electrical re-heating | Inlet air temperature | 10.8 | degC | 10.8 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - electrical re-heating | Inlet air relative humidity | 91.5 | % | 91.5 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - electrical re-heating | Outlet air temperature | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - electrical re-heating | Outlet air relative humidity | 68 | % | 68 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - humidifier | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - humidifier | Max capacity steam | 1x9 | kg/h | 1x9 | unit:KiloGM-PER-HR | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - humidifier | Min capacity steam | 1x2.7 | kg/h | 1x2.7 | unit:KiloGM-PER-HR | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - humidifier | Type of humidifier | electrodes immersed | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - humidifier | Power supply | 400/3/50 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - humidifier | Nominal power input | 1x5.8 | kW | 1x5.8 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Option - humidifier | Max absorption current | 1x9 | A | 1x9 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 3
CC/B/01,02 | S1GOA | Compliance | Declared performance / directives | EN 14511:2011; 2006/42/EC, 2004/108/EC, 2006/95/EC, 97/23/EC - Module H (Notified Body Lloyd's Register of Shipping No 0038) | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 2
CC/B/03,04 | S1DOA + 1 x HCR24 | Identification | Manufacturer | Emerson Network Power |  |  |  |  | rec:manufacturedBy | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Identification | Model | S1DOA + 1 x HCR24 |  |  |  |  | rec:modelNumber | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Identification | System type | Direct expansion (DX), air-cooled | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Identification | Issued by | Qatar Site & Power | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Identification | Selection date | Monday, April 15, 2013 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Identification | Selection software release | Rel. 7.4 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Design condition | Unit inlet air temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Design condition | Unit inlet air relative humidity | 46 | % | 46 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Design condition | Unit airflow | 2412 | m3/h | 670 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Design condition | ESP | 75 | Pa | 75 | unit:PA |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Design condition | Sea level | 0 | m | 0 | unit:M |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Design condition | Refrigerant | R410A |  |  |  |  | para:refrigerant | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Design condition | Unit power supply | 400 V/3 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Total cooling capacity | 10.6 | kW | 10.6 | unit:KiloW |  | brick:coolingCapacity | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Sensible cooling capacity | 10 | kW | 10 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | SHR | 0.94 |  | 0.94 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Off coil air temperature | 9.7 | degC | 9.7 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Off coil air relative humidity | 98.1 | % | 98.1 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Room SPL (@ 2 m, f.f) | 50.7 | dB(A) | 50.7 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Condensing temperature | 57.8 | degC | 57.8 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Unit power input | 4.85 | kW | 4.85 | unit:KiloW |  | brick:ratedPowerInput | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Unit EER | 2.19 |  | 2.19 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | System power input | 5.4 | kW | 5.4 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | System EER | 1.96 |  | 1.96 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Internal filter class (EN779 std) | G4 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Width | 750 | mm | 0.75 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Depth | 500 | mm | 0.5 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Height | 1950 | mm | 1.95 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Weight | 215 | kg | 215 | unit:KiloGM | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Fans | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Fans | Type | Normal | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Fans | Power supply | 230/1/50 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Fans | Power input | 1 x 0.21 | kW | 1 x 0.21 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Fans | Operating ampere | 1 x 1.39 | A | 1 x 1.39 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Fans | Full load ampere | 1 x 2.93 | A | 1 x 2.93 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Fans | Locked rotor amp. | 1 x 0.10 | A | 1 x 0.10 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Fans | Fan input voltage | 6.5 | V | 6.5 | unit:V |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Compressors | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Compressors | Power supply | 400 V/3 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Compressors | Power input | 1 x 4.64 | kW | 1 x 4.64 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Compressors | Compressors COP | 2.27 |  | 2.27 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Compressors | Operating ampere | 1 x 7.74 | A | 1 x 7.74 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Compressors | Full load ampere | 1 x 10.30 | A | 1 x 10.30 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Compressors | Locked rotor amp. | 1 x 51.50 | A | 1 x 51.50 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Condenser model | HCR24 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Version | Standard | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Air discharge | Vertical | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Power supply | 230 V/1 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Variex | No | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Heat load | 15.2 | kW | 15.2 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Outdoor air temperature | 50 | degC | 50 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Condenser airflow (@ max speed) | 8600 | m3/h | 2388.89 | unit:L-PER-SEC | m3/h / 3.6 |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Condenser actual airflow | 8600 | m3/h | 2388.89 | unit:L-PER-SEC | m3/h / 3.6 |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Condenser ESP (@ max speed) | 0 | Pa | 0 | unit:PA |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Max outdoor SPL (@ 5 m, f.f.) | 50 | dB(A) | 50 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Actual outdoor SPL (@ 5 m, f.f.) | 50 | dB(A) | 50 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Power input | 0.55 | kW | 0.55 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Full load ampere | 2.5 | A | 2.5 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Locked rotor amp. | 4.8 | A | 4.8 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Width | 1112 | mm | 1.112 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Depth | 1340 | mm | 1.34 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Height | 907 | mm | 0.907 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Condenser | Weight | 75 | kg | 75 | unit:KiloGM | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - electrical re-heating | Max re-heating capacity | 4.5 | kW | 4.5 | unit:KiloW |  | para:ratedReheatCapacity | core | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - electrical re-heating | FLA | 6.5 | A | 6.5 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - electrical re-heating | Inlet air temperature | 9.7 | degC | 9.7 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - electrical re-heating | Inlet air relative humidity | 98.1 | % | 98.1 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - electrical re-heating | Outlet air temperature | 15.2 | degC | 15.2 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - electrical re-heating | Outlet air relative humidity | 68.5 | % | 68.5 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - humidifier | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - humidifier | Max capacity steam | 1x4.5 | kg/h | 1x4.5 | unit:KiloGM-PER-HR | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - humidifier | Min capacity steam | 1x1.3 | kg/h | 1x1.3 | unit:KiloGM-PER-HR | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - humidifier | Type of humidifier | electrodes immersed | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - humidifier | Power supply | 400/3/50 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - humidifier | Nominal power input | 1x3 | kW | 1x3 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - humidifier | Max absorption current | 1x4.6 | A | 1x4.6 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 6
CC/B/03,04 | S1DOA + 1 x HCR24 | Compliance | Declared performance / directives | EN 14511:2011; 2006/42/EC, 2004/108/EC, 2006/95/EC, 97/23/EC - Module H (Notified Body Lloyd's Register of Shipping No 0038) | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Note | Sheet note | Unit with ducted air discharge. | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 5
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Identification | Manufacturer | Emerson Network Power |  |  |  |  | rec:manufacturedBy | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Identification | Model | M5DUA + 2 x HCR59 |  |  |  |  | rec:modelNumber | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Identification | System type | Direct expansion (DX), air-cooled | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Identification | Issued by | Qatar Site & Power | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Identification | Selection date | Monday, April 15, 2013 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Identification | Selection software release | Rel. 7.4 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Design condition | Unit inlet air temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Design condition | Unit inlet air relative humidity | 47 | % | 47 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Design condition | Unit airflow | 13320 | m3/h | 3700 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Design condition | ESP | 75 | Pa | 75 | unit:PA |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Design condition | Sea level | 0 | m | 0 | unit:M |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Design condition | Refrigerant | R410A |  |  |  |  | para:refrigerant | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Design condition | Unit power supply | 400 V/3 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Total cooling capacity | 50.1 | kW | 50.1 | unit:KiloW |  | brick:coolingCapacity | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Sensible cooling capacity | 50.1 | kW | 50.1 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | SHR | 1 |  | 1 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Off coil air temperature | 10.5 | degC | 10.5 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Off coil air relative humidity | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Room SPL (@ 2 m, f.f) | 61 | dB(A) | 61 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Condensing temperature | 56.4 | degC | 56.4 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Unit power input | 20.23 | kW | 20.23 | unit:KiloW |  | brick:ratedPowerInput | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Unit EER | 2.48 |  | 2.48 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | System power input | 22.43 | kW | 22.43 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | System EER | 2.23 |  | 2.23 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Internal filter class (EN779 std) | G4 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Width | 1750 | mm | 1.75 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Depth | 850 | mm | 0.85 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Height | 1950 | mm | 1.95 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Weight | 625 | kg | 625 | unit:KiloGM | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Fans | Quantity | 2 | n | 2 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Fans | Type | Normal | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Fans | Power supply | 400/3/50 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Fans | Power input | 2 x 1.94 | kW | 2 x 1.94 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Fans | Operating ampere | 2 x 3.11 | A | 2 x 3.11 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Fans | Full load ampere | 2 x 4.00 | A | 2 x 4.00 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Fans | Locked rotor amp. | 2 x 0.10 | A | 2 x 0.10 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Fans | Fan input voltage | 9.5 | V | 9.5 | unit:V |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Compressors | Quantity | 2 | n | 2 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Compressors | Power supply | 400 V/3 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Compressors | Power input | 2 x 8.175 | kW | 2 x 8.175 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Compressors | Compressors COP | 3.05 |  | 3.05 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Compressors | Operating ampere | 2 x 14.75 | A | 2 x 14.75 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Compressors | Full load ampere | 2 x 21.00 | A | 2 x 21.00 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Compressors | Locked rotor amp. | 2 x 111.00 | A | 2 x 111.00 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Condenser model | HCR59 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Version | Standard | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Air discharge | Vertical | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Power supply | 230 V/1 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Variex | No | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Heat load | 33.2 | kW | 33.2 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Outdoor air temperature | 50 | degC | 50 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Condenser airflow (@ max speed) | 15600 | m3/h | 4333.33 | unit:L-PER-SEC | m3/h / 3.6 |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Condenser actual airflow | 15600 | m3/h | 4333.33 | unit:L-PER-SEC | m3/h / 3.6 |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Condenser ESP (@ max speed) | 0 | Pa | 0 | unit:PA |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Max outdoor SPL (@ 5 m, f.f.) | 53 | dB(A) | 53 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Actual outdoor SPL (@ 5 m, f.f.) | 53 | dB(A) | 53 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Power input | 1.1 | kW | 1.1 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Full load ampere | 5 | A | 5 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Locked rotor amp. | 9.6 | A | 9.6 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Width | 1112 | mm | 1.112 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Depth | 2340 | mm | 2.34 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Height | 907 | mm | 0.907 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Weight | 102 | kg | 102 | unit:KiloGM | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Condenser | Note | Data are per condenser; 2 condensers per unit. | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - electrical re-heating | Max re-heating capacity | 15 | kW | 15 | unit:KiloW |  | para:ratedReheatCapacity | core | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - electrical re-heating | FLA | 21.7 | A | 21.7 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - electrical re-heating | Inlet air temperature | 10.5 | degC | 10.5 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - electrical re-heating | Inlet air relative humidity | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - electrical re-heating | Outlet air temperature | 13.8 | degC | 13.8 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - electrical re-heating | Outlet air relative humidity | 80.2 | % | 80.2 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - humidifier | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - humidifier | Max capacity steam | 1x13 | kg/h | 1x13 | unit:KiloGM-PER-HR | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - humidifier | Min capacity steam | 1x2.7 | kg/h | 1x2.7 | unit:KiloGM-PER-HR | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - humidifier | Type of humidifier | electrodes immersed | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - humidifier | Power supply | 400/3/50 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - humidifier | Nominal power input | 1x9 | kW | 1x9 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - humidifier | Max absorption current | 1x13 | A | 1x13 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 9
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Compliance | Declared performance / directives | EN 14511:2011; 2006/42/EC, 2004/108/EC, 2006/95/EC, 97/23/EC - Module H (Notified Body Lloyd's Register of Shipping No 0038) | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Data quality | Source anomaly | Sheet heading reads 'M5DUA + 2 x HCR59'; the Unit row of the same sheet reads 'M5DOA + 2 x HCR59'. Heading value recorded. | [6 empty] | qnl_closed_control_units_manual.pdf | 8 | Confirm with the supplier before use
CC/B/08 | S11OC | Identification | Manufacturer | Emerson Network Power |  |  |  |  | rec:manufacturedBy | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Identification | Model | S11OC |  |  |  |  | rec:modelNumber | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Identification | System type | Chilled water (CW) | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Identification | Issued by | QSP | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Identification | Selection date | Tuesday, October 22, 2013 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Identification | Selection software release | Rel. 7.8 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Identification | Dimension drawing pages | 13-14 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 13-14
CC/B/08 | S11OC | Design condition | Unit inlet air temperature | 21 | degC | 21 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Design condition | Unit inlet air relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Design condition | Unit airflow | 2800 | m3/h | 777.778 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Design condition | ESP | 50 | Pa | 50 | unit:PA |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Design condition | Sea level | 0 | m | 0 | unit:M |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Design condition | Fluid | WATER | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Design condition | Inlet fluid temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Design condition | Outlet fluid temperature | 12 | degC | 12 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Design condition | Unit fluid flow | 0.42 | l/s | 0.42 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Design condition | Unit power supply | 400 V/3 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Total cooling capacity | 8.7 | kW | 8.7 | unit:KiloW |  | brick:coolingCapacity | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Sensible cooling capacity | 8.7 | kW | 8.7 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | SHR | 1 |  | 1 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Off coil air temperature | 11.8 | degC | 11.8 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Off coil air relative humidity | 89.6 | % | 89.6 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Room SPL (@ 2 m, f.f) | 56.2 | dB(A) | 56.2 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Unit power input | 0.35 | kW | 0.35 | unit:KiloW |  | brick:ratedPowerInput | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Unit EER | 24.9 |  | 24.9 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Internal filter class (EN779 std) | G4 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Width | 750 | mm | 0.75 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Depth | 500 | mm | 0.5 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Height | 1950 | mm | 1.95 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Weight | 165 | kg | 165 | unit:KiloGM | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | CW coil | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | CW coil | Unit fluid flow | 0.42 | l/s | 0.42 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | CW coil | Unit fluid side pressure drop | 23 | kPa | 23000 | unit:PA | kPa x 1000 |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | CW coil | Fluid pressure drop coil + connections | 18 | kPa | 18000 | unit:PA | kPa x 1000 |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | CW coil | Valve pressure drop | 6 | kPa | 6000 | unit:PA | kPa x 1000 |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Fans | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Fans | Type | Normal | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Fans | Power supply | 230/1/50 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Fans | Power input | 1 x 0.35 | kW | 1 x 0.35 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Fans | Operating ampere | 1 x 2.29 | A | 1 x 2.29 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Fans | Full load ampere | 1 x 2.93 | A | 1 x 2.93 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Fans | Locked rotor amp. | 1 x 0.10 | A | 1 x 0.10 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Fans | Fan input voltage | 8 | V | 8 | unit:V |  |  | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Option - electrical re-heating | Max re-heating capacity | 4.5 | kW | 4.5 | unit:KiloW |  | para:ratedReheatCapacity | core | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - electrical re-heating | FLA | 6.5 | A | 6.5 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - electrical re-heating | Inlet air temperature | 11.8 | degC | 11.8 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - electrical re-heating | Inlet air relative humidity | 89.6 | % | 89.6 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - electrical re-heating | Outlet air temperature | 16.5 | degC | 16.5 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - electrical re-heating | Outlet air relative humidity | 66 | % | 66 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - humidifier | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - humidifier | Max capacity steam | 1x4.5 | kg/h | 1x4.5 | unit:KiloGM-PER-HR | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - humidifier | Min capacity steam | 1x1.3 | kg/h | 1x1.3 | unit:KiloGM-PER-HR | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - humidifier | Type of humidifier | electrodes immersed | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - humidifier | Power supply | 400/3/50 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - humidifier | Nominal power input | 1x3 | kW | 1x3 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Option - humidifier | Max absorption current | 1x4.6 | A | 1x4.6 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 12
CC/B/08 | S11OC | Compliance | Declared performance / directives | EN 14511:2011 (cooling-only units); 2006/42/EC, 2004/108/EC, 2006/95/EC, 97/23/EC | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Note | Sheet note | Unit with ducted air discharge. | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 11
CC/B/09 | S1DOA + 1 x HCR33 | Identification | Manufacturer | Emerson Network Power |  |  |  |  | rec:manufacturedBy | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Identification | Model | S1DOA + 1 x HCR33 |  |  |  |  | rec:modelNumber | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Identification | System type | Direct expansion (DX), air-cooled | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Identification | Issued by | QSP | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Identification | Selection date | Tuesday, October 22, 2013 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Identification | Selection software release | Rel. 7.8 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Design condition | Unit inlet air temperature | 21 | degC | 21 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Design condition | Unit inlet air relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Design condition | Unit airflow | 2100 | m3/h | 583.333 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Design condition | ESP | 50 | Pa | 50 | unit:PA |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Design condition | Sea level | 0 | m | 0 | unit:M |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Design condition | Refrigerant | R410A |  |  |  |  | para:refrigerant | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Design condition | Unit power supply | 400 V/3 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Total cooling capacity | 10.4 | kW | 10.4 | unit:KiloW |  | brick:coolingCapacity | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Sensible cooling capacity | 8.9 | kW | 8.9 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | SHR | 0.86 |  | 0.86 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Off coil air temperature | 8.4 | degC | 8.4 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Off coil air relative humidity | 99.4 | % | 99.4 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Room SPL (@ 2 m, f.f) | 50.9 | dB(A) | 50.9 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Condensing temperature | 54.7 | degC | 54.7 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Unit power input | 4.47 | kW | 4.47 | unit:KiloW |  | brick:ratedPowerInput | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Unit EER | 2.33 |  | 2.33 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | System power input | 5.02 | kW | 5.02 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | System EER | 2.07 |  | 2.07 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Internal filter class (EN779 std) | G4 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Width | 750 | mm | 0.75 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Depth | 500 | mm | 0.5 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Height | 1950 | mm | 1.95 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Weight | 215 | kg | 215 | unit:KiloGM | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Fans | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Fans | Type | Normal | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Fans | Power supply | 230/1/50 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Fans | Power input | 1 x 0.17 | kW | 1 x 0.17 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Fans | Operating ampere | 1 x 1.14 | A | 1 x 1.14 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Fans | Full load ampere | 1 x 2.93 | A | 1 x 2.93 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Fans | Locked rotor amp. | 1 x 0.10 | A | 1 x 0.10 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Fans | Fan input voltage | 6 | V | 6 | unit:V |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Compressors | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Compressors | Power supply | 400 V/3 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Compressors | Power input | 1 x 4.3 | kW | 1 x 4.3 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Compressors | Compressors COP | 2.42 |  | 2.42 | unit:UNITLESS | dimensionless ratio |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Compressors | Operating ampere | 1 x 7.23 | A | 1 x 7.23 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Compressors | Full load ampere | 1 x 10.30 | A | 1 x 10.30 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Compressors | Locked rotor amp. | 1 x 51.50 | A | 1 x 51.50 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Condenser model | HCR33 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Version | Standard | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Air discharge | Vertical | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Power supply | 230 V/1 ph/50 Hz | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Variex | Yes | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Heat load | 14.7 | kW | 14.7 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Outdoor air temperature | 47.5 | degC | 47.5 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Condenser airflow (@ max speed) | 7400 | m3/h | 2055.56 | unit:L-PER-SEC | m3/h / 3.6 |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Condenser actual airflow | 7400 | m3/h | 2055.56 | unit:L-PER-SEC | m3/h / 3.6 |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Condenser ESP (@ max speed) | 0 | Pa | 0 | unit:PA |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Max outdoor SPL (@ 5 m, f.f.) | 50 | dB(A) | 50 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Actual outdoor SPL (@ 5 m, f.f.) | 50 | dB(A) | 50 | unit:DeciB | A-weighting kept in the property name |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Power input | 0.55 | kW | 0.55 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Full load ampere | 2.5 | A | 2.5 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Locked rotor amp. | 4.8 | A | 4.8 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Width | 1112 | mm | 1.112 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Depth | 1340 | mm | 1.34 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Height | 907 | mm | 0.907 | unit:M | mm / 1000 |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Condenser | Weight | 75 | kg | 75 | unit:KiloGM | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Option - electrical re-heating | Max re-heating capacity | 4.5 | kW | 4.5 | unit:KiloW |  | para:ratedReheatCapacity | core | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - electrical re-heating | FLA | 6.5 | A | 6.5 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - electrical re-heating | Inlet air temperature | 8.4 | degC | 8.4 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - electrical re-heating | Inlet air relative humidity | 99.4 | % | 99.4 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - electrical re-heating | Outlet air temperature | 14.7 | degC | 14.7 | unit:DEG_C |  |  | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - electrical re-heating | Outlet air relative humidity | 66.2 | % | 66.2 | unit:PERCENT_RH |  |  | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - electrical re-heating | Sheet heading | Electrical heating | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - humidifier | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - humidifier | Max capacity steam | 1x4.5 | kg/h | 1x4.5 | unit:KiloGM-PER-HR | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - humidifier | Min capacity steam | 1x1.3 | kg/h | 1x1.3 | unit:KiloGM-PER-HR | unit not used in Dar Cairo |  | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - humidifier | Type of humidifier | electrodes immersed | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - humidifier | Power supply | 400/3/50 | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - humidifier | Nominal power input | 1x3 | kW | 1x3 | unit:KiloW |  |  | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Option - humidifier | Max absorption current | 1x4.6 | A | 1x4.6 | unit:A |  |  | reference | qnl_closed_control_units_manual.pdf | 17
CC/B/09 | S1DOA + 1 x HCR33 | Compliance | Declared performance / directives | EN 14511:2011 (cooling-only units); 2006/42/EC, 2004/108/EC, 2006/95/EC, 97/23/EC | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Note | Sheet note | Unit with ducted air discharge. | [5 empty] | reference | qnl_closed_control_units_manual.pdf | 16

## Climate Control Units
Climate Control Units
Museum Climate Controls MCG-10P positive-pressure humidity control unit, VCB1000 blower option and AF4 intake air filter.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
MCG-10P | MCG-10P | Identification | Manufacturer | Museum Climate Controls |  |  |  |  | rec:manufacturedBy | core | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Identification | Model | MCG-10P |  |  |  |  | rec:modelNumber | core | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Identification | Equipment type | Positive-pressure humidity control unit for display cases / storage spaces | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Identification | Document status | Sheet watermarked 'Preliminary'; footer 'Museum Climate Controls 2012' | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Capacity | Up to 2,500 l/hr with single pump; 5,000 l/hr with optional VCB1000 blower | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Tolerance | +/- 2% at RH set point | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Operating temp | 17 to 27 (63 to 81 F) | degC | 17 to 27 (63 to 81 F) | unit:DEG_C |  |  | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Power | 110 VAC 50-60 Hz / 6 A | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Power consumption | 6 A at 50%RH / 21 C (average) | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Air hose connection | Smooth inside-surface hose, ID 25 mm | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Size | 500 mm (w) x 650 mm (d) x 650 mm (h) | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Weight | 50 | kg | 50 | unit:KiloGM | unit not used in Dar Cairo |  | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Weight | 100 | lb | 45.3592 | unit:KiloGM | lb x 0.45359237; unit not used in Dar Cairo |  | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Weight note | without water | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Intake air filter | Activated carbon filter, supplied with the unit | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Specifications | Water feed | Reverse osmosis filter, supplied with the unit | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Installation requirement | Installation requirement 1 | Display case leakage better than 0.3 air changes per day | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Installation requirement | Installation requirement 2 | Minimum clearance space 550 mm (W) x 700 mm (D) x 700 mm (H) | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Installation requirement | Installation requirement 3 | Force air ventilation at least 150 CFM / ambient temperature < 23 C | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Installation requirement | Installation requirement 4 | Water supply minimum 40 PSI | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Installation requirement | Installation requirement 5 | Ground level floor drain or drain pan | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Installation requirement | Installation requirement 6 | One or more 8 mm holes for air hose connections inside display case | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Installation requirement | Installation requirement 7 | Air supply pipeline to case from unit | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Installation requirement | Installation requirement 8 | Power outlet 220 VAC / 15 A | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | System included | System included 1 | Reverse osmosis water filter | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | System included | System included 2 | 3-way air supply diverting valve | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | System included | System included 3 | Remote RH / temperature sensor - Model MCLS-75 | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | System included | System included 4 | Activated carbon and activated alumina (Al2O3) impregnated with potassium permanganate (KMnO4) intake air filter | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | System included | System included 5 | UV light clean water system | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Feature | Feature 1 | Stackable - multiple units can stack together to condition larger volume | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Feature | Feature 2 | Unit can be placed up to 100 m away | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Feature | Feature 3 | Delivers humidity within 2% of set point | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Feature | Feature 4 | Multilevel fault tolerant protections with display | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Feature | Feature 5 | Dry contact relay connection for building management system | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Feature | Feature 6 | Remote monitoring and data logging (optional) | [5 empty] | reference | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Dimension drawing | Dwg no | MCG10P-1 / MCG10P-2 | [5 empty] | reference | climate_control_units_manual.pdf | 5-6
MCG-10P | MCG-10P | Dimension drawing | Rev | 1.0 | [5 empty] | reference | climate_control_units_manual.pdf | 5-6
MCG-10P | MCG-10P | Dimension drawing | Drawn by | KY | [5 empty] | reference | climate_control_units_manual.pdf | 5-6
MCG-10P | MCG-10P | Dimension drawing | Date | 2-10-13 | [5 empty] | reference | climate_control_units_manual.pdf | 5-6
MCG-10P | MCG-10P | Dimension drawing | Scale | 1:10 | [5 empty] | reference | climate_control_units_manual.pdf | 5-6
MCG-10P | MCG-10P | Dimension drawing | Size | A / B | [5 empty] | reference | climate_control_units_manual.pdf | 5-6
MCG-10P | MCG-10P | Dimension drawing | Front view width | 475 | mm | 0.475 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 5-6
MCG-10P | MCG-10P | Dimension drawing | Front view height | 400 | mm | 0.4 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 5-6
MCG-10P | MCG-10P | Dimension drawing | Plan view depth | 430 | mm | 0.43 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 5-6
MCG-10P | MCG-10P | Dimension drawing | Side view width | 494 | mm | 0.494 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 5-6
MCG-10P | MCG-10P | Dimension drawing | Side view height | 425 | mm | 0.425 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 5-6
MCG-10P | MCG-10P | Data quality | Source conflict | Specification sheet (page 2) states size 500 (w) x 650 (d) x 650 (h) mm, while dimension drawing MCG10P-1 (page 6) shows 475 W x 430 D x 400 H mm. Confirm with the manufacturer before using either as nameplate data. | [6 empty] | climate_control_units_manual.pdf | 2 | Confirm with the manufacturer before use
VCB1000-AB32 | VCB1000-AB32 | Identification | Manufacturer | VCBtech |  |  |  |  | rec:manufacturedBy | core | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Identification | Model | VCB1000-AB32 |  |  |  |  | rec:modelNumber | core | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Identification | Equipment type | Optional blower/pump for MCG-10P (raises capacity to 5,000 l/hr) | [5 empty] | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Electronics | integrated | [5 empty] | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Input voltage | 24 | V DC | 24 | unit:V | DC noted in the property name |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Input current | 7 | A | 7 | unit:A |  |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Speed | 9000 | rpm | 9000 | unit:RPM |  | para:ratedSpeed | core | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Motor rating | 110 | W | 0.11 | unit:KiloW | W / 1000 |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Speed control range | 700 to 9000 | rpm | 700 to 9000 | unit:RPM |  |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Permissible ambient | -10 to 40 | degC | -10 to 40 | unit:DEG_C |  |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Weight | 1.2 | kg | 1.2 | unit:KiloGM | unit not used in Dar Cairo |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Spl | 48 | dB(A) | 48 | unit:DeciB | A-weighting kept in the property name |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Total pressure difference vacuum | 100 | mbar | 10000 | unit:PA | mbar x 100 |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Total pressure difference pressure | 120 | mbar | 12000 | unit:PA | mbar x 100 |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Bearing life | 20000 | hours | 20000 | unit:HR |  |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Dimensions | Flange od | 144 | mm | 0.144 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Dimensions | Bolt circle | 133 | mm | 0.133 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Dimensions | Body od | 114 | mm | 0.114 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Dimensions | Depth | 90 | mm | 0.09 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Dimensions | Width across | 72 | mm | 0.072 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Dimensions | Height | 61 | mm | 0.061 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Dimensions | Hub | 53 | mm | 0.053 | unit:M | mm / 1000 |  | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Dimensions | Mounting | 8 x M4 x 6 | [5 empty] | reference | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Installation | Mounting | Shaft in any position; vibration within section 1 Technical Data limits | [5 empty] | reference | climate_control_units_manual.pdf | 3
VCB1000-AB32 | VCB1000-AB32 | Installation | Clearance | Minimum 15 mm each side for heat dissipation; at least 2 mm on the pump lid side | [5 empty] | reference | climate_control_units_manual.pdf | 3
VCB1000-AB32 | VCB1000-AB32 | Control wiring | Red | +Vcc, +24 V power supply | [5 empty] | reference | climate_control_units_manual.pdf | 3
VCB1000-AB32 | VCB1000-AB32 | Control wiring | Black | Gnd, -24 V power supply | [5 empty] | reference | climate_control_units_manual.pdf | 3
VCB1000-AB32 | VCB1000-AB32 | Control wiring | Green | n_des, speed reference 0-10 V DC | [5 empty] | reference | climate_control_units_manual.pdf | 3
VCB1000-AB32 | VCB1000-AB32 | Control wiring | White | A, 10 V ground (digital input) | [5 empty] | reference | climate_control_units_manual.pdf | 3
VCB1000-AB32 | VCB1000-AB32 | Control wiring | Grey | B, 24 V+ (digital input) | [5 empty] | reference | climate_control_units_manual.pdf | 3
VCB1000-AB32 | VCB1000-AB32 | Control wiring | Blue | n_act | [5 empty] | reference | climate_control_units_manual.pdf | 3
VCB1000-AB32 | VCB1000-AB32 | Control wiring | Modes | A=0/B=0 output disabled; A=0/B=1 counter-clockwise (main direction); A=1/B=0 clockwise; A=1/B=1 breaking | [5 empty] | reference | climate_control_units_manual.pdf | 3
MCG Air Filter AF4 | AF4 | Identification | Manufacturer | Museum Climate Controls |  |  |  |  | rec:manufacturedBy | core | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Identification | Model | AF4 |  |  |  |  | rec:modelNumber | core | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Identification | Equipment type | Three-stage intake air filter for MCG units | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Specifications | Gac alumina wts per sqft | 150/225 | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Specifications | Nominal thickness | secondary filter - 2" (50 mm) | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Specifications | Initial resistance | 0.11 at 100 FPM | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Specifications | Final resistance | 1.2 (in WG) | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Specifications | Average arrestance | 90-96 % at 300 FPM | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Specifications | Particulates capacity | 235 g/ft2 or 4035 g/m2 | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Specifications | Filter dimension | 4" x 4" x 2" (100 x 100 x 50 mm) | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Specifications | Filter case dimension | 11" x 4.50" x 4.5" (280 x 115 x 115 mm) | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Specifications | Hose connections | 20 mm ID for MCG4, 32 mm ID for MCG8 | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Feature | Feature 1 | Booster fan for stand-alone usage or to compensate air resistance in long-distance connection | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Feature | Feature 2 | Low air resistance | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Filtration stages | Primary | 3/4" (20 mm) polyester media - removes particulates | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Filtration stages | Secondary | Granular activated carbon + activated alumina (Al2O3) impregnated with potassium permanganate (KMnO4) - removes light gases and odors | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Filtration stages | Tertiary | 3/4" (20 mm) polyurethane foam media - removes stray particulates or carbon | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Application | Application | Light gases (ammonia NH3, formaldehyde CH2O, hydrogen sulfide H2S, sulfur dioxide SO2), particulates, gaseous pollutants, odors | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Options | Options | Alarm for filter expiration | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Warranty | Warranty | One year parts and labor | [5 empty] | reference | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Note | Note | Hose connection sizes are quoted for MCG4 and MCG8; the sheet does not state a size for MCG-10P. | [5 empty] | reference | climate_control_units_manual.pdf | 7

## FCU
FCU
Euroclima fan coil units - one selection sheet per position, offer CENTRAL LIBRARY. Positions carrying several tags on one sheet (e.g. B/06,08,17,24) were annotated by hand on the printed sheet; those tags share the selection above them. The Heating column is blank on all 28 sheets.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
FCU/B/01 | TO50-4R-2 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Identification | Offer | CENTRAL LIBRARY | [5 empty] | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Identification | Range | TO | [5 empty] | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Identification | Version | TO | [5 empty] | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Identification | Model | TO50-4R-2 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Capacity | Total capacity (cooling) | 13.21 | kW | 13.21 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Capacity | Sensible capacity (cooling) | 13.21 | kW | 13.21 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Air | Outlet DBT | 12.5 | degC | 12.5 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Air | Outlet WBT | 11.7 | degC | 11.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Air | Outlet RH | 91 | % | 91 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Air | Flow rate | 4182 | m3/h | 1161.67 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Air | Fan speed setting | 2 |  | 2 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Air | Air velocity | 1.82 | m/s | 1.82 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Air | Air pressure drop | 35.9 | Pa | 35.9 | unit:PA |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Fluid | Flow rate | 1296 | l/h | 0.36 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Fluid | Pressure drop | 3.1 | kPa | 3100 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Fluid | Outlet temperature | 15.8 | degC | 15.8 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Dimensions and weight | Max width | 1800 | mm | 1.8 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Dimensions and weight | Max height | 420 | mm | 0.42 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Dimensions and weight | Max thickness | 840 | mm | 0.84 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Dimensions and weight | Weight | 135 | kg | 135 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Other data | Power supply | V230/1/50 | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Other data | Max. absorbed power | 970 | W | 0.97 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Other data | Max. absorbed current | 4.9 | A | 4.9 | unit:A |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Other data | Sound pressure level | 50.2 | dB(A) | 50.2 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Other data | Sound power level | 70.2 | dB(A) | 70.2 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Other data | Static pressure | 71 | Pa | 71 | unit:PA |  |  | reference | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 2 | Heating column blank on the sheet; cooling-only selection.
B/02 | CR32-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Identification | Offer | CL | [5 empty] | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Identification | Version | CPI | [5 empty] | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Identification | Model | CR32-4R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Capacity | Total capacity (cooling) | 6.52 | kW | 6.52 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Capacity | Sensible capacity (cooling) | 6.52 | kW | 6.52 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Air | Outlet DBT | 11.3 | degC | 11.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Air | Outlet WBT | 11.3 | degC | 11.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Air | Outlet RH | 99 | % | 99 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Air | Flow rate | 1836 | m3/h | 510 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Air | Air velocity | 1.28 | m/s | 1.28 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Air | Air pressure drop | 21.5 | Pa | 21.5 | unit:PA |  |  | reference | FCU_Manual.pdf | 3 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/02 | CR32-4R-6 | Fluid | Flow rate | 698 | l/h | 0.19389 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Fluid | Pressure drop | 3 | kPa | 3000 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Fluid | Outlet temperature | 15 | degC | 15 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Dimensions and weight | Max width | 1980 | mm | 1.98 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Dimensions and weight | Max height | 665 | mm | 0.665 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Dimensions and weight | Max thickness | 285 | mm | 0.285 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Dimensions and weight | Weight | 24.5 | kg | 24.5 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Other data | Max. absorbed power | 570 | W | 0.57 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Other data | Max. absorbed current | 2.89 | A | 2.89 | unit:A |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Other data | Sound pressure level | 39 | dB(A) | 39 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Other data | Sound power level | 62 | dB(A) | 62 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Other data | Static pressure | 37 | Pa | 37 | unit:PA |  |  | reference | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 3 | Heating column blank on the sheet; cooling-only selection.
B/02 | CR32-4R-6 | Data quality | Sheet note | Only sheet with VERSION 'CPI'; casing dimensions (1980 x 665 x 285) also differ from the CPR sheets. | [6 empty] | FCU_Manual.pdf | 3 | Confirm with the supplier before use
B/03,04 | CR32-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Identification | Offer | CENTRAL LIBRARY REV1 | [5 empty] | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Identification | Model | CR32-3R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Capacity | Total capacity (cooling) | 6.09 | kW | 6.09 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Capacity | Sensible capacity (cooling) | 6.09 | kW | 6.09 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Air | Outlet DBT | 12 | degC | 12 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Air | Outlet WBT | 11.5 | degC | 11.5 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Air | Outlet RH | 94 | % | 94 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Air | Flow rate | 1836 | m3/h | 510 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Air | Air velocity | 1.28 | m/s | 1.28 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Air | Air pressure drop | 16.2 | Pa | 16.2 | unit:PA |  |  | reference | FCU_Manual.pdf | 4 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/03,04 | CR32-3R-6 | Fluid | Flow rate | 720 | l/h | 0.2 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Fluid | Pressure drop | 3.3 | kPa | 3300 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Fluid | Outlet temperature | 14.3 | degC | 14.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Dimensions and weight | Max thickness | 1900 | mm | 1.9 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Dimensions and weight | Weight | 65 | kg | 65 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Other data | Max. absorbed power | 570 | W | 0.57 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Other data | Max. absorbed current | 2.89 | A | 2.89 | unit:A |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Other data | Sound pressure level | 39 | dB(A) | 39 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Other data | Sound power level | 62 | dB(A) | 62 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Other data | Static pressure | 37 | Pa | 37 | unit:PA |  |  | reference | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 4 | Heating column blank on the sheet; cooling-only selection.
B5 | CR23-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Identification | Offer | CL | [5 empty] | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Identification | Model | CR23-3R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Capacity | Total capacity (cooling) | 3.52 | kW | 3.52 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Capacity | Sensible capacity (cooling) | 3.52 | kW | 3.52 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Air | Inlet DBT | 21 | degC | 21 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Air | Inlet WBT | 14.6 | degC | 14.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Air | Outlet DBT | 13.3 | degC | 13.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Air | Outlet WBT | 11.6 | degC | 11.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Air | Outlet RH | 82 | % | 82 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Air | Flow rate | 1365 | m3/h | 379.167 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Air | Air velocity | 1.26 | m/s | 1.26 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Air | Air pressure drop | 16 | Pa | 16 | unit:PA |  |  | reference | FCU_Manual.pdf | 5 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B5 | CR23-3R-6 | Fluid | Flow rate | 360 | l/h | 0.1 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Fluid | Pressure drop | 2 | kPa | 2000 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Fluid | Outlet temperature | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Dimensions and weight | Max thickness | 1500 | mm | 1.5 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Dimensions and weight | Weight | 55 | kg | 55 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Other data | Max. absorbed power | 420 | W | 0.42 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Other data | Max. absorbed current | 2.11 | A | 2.11 | unit:A |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Other data | Sound pressure level | 42 | dB(A) | 42 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Other data | Sound power level | 63 | dB(A) | 63 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Other data | Static pressure | 40 | Pa | 40 | unit:PA |  |  | reference | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 5 | Heating column blank on the sheet; cooling-only selection.
B/06,08,17,24 | FH090-3R-7 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Identification | Offer | CL | [5 empty] | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Identification | Range | FH | [5 empty] | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Identification | Version | FOH | [5 empty] | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Identification | Model | FH090-3R-7 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Capacity | Total capacity (cooling) | 3.8 | kW | 3.8 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Capacity | Sensible capacity (cooling) | 3.8 | kW | 3.8 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Air | Inlet DBT | 27 | degC | 27 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Air | Inlet WBT | 16.7 | degC | 16.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Air | Inlet RH | 35 | % | 35 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Air | Outlet DBT | 10.9 | degC | 10.9 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Air | Outlet WBT | 10.6 | degC | 10.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Air | Outlet RH | 96 | % | 96 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Air | Flow rate | 720 | m3/h | 200 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Air | Fan speed setting | 7 |  | 7 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Air | Air velocity | 0.57 | m/s | 0.57 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Air | Air pressure drop | 5.7 | Pa | 5.7 | unit:PA |  |  | reference | FCU_Manual.pdf | 6 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/06,08,17,24 | FH090-3R-7 | Fluid | Flow rate | 360 | l/h | 0.1 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Fluid | Pressure drop | 2.3 | kPa | 2300 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Fluid | Outlet temperature | 16.1 | degC | 16.1 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Dimensions and weight | Max width | 495 | mm | 0.495 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Dimensions and weight | Max height | 220 | mm | 0.22 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Dimensions and weight | Max thickness | 1700 | mm | 1.7 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Dimensions and weight | Weight | 44.5 | kg | 44.5 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Other data | Max. absorbed power | 285 | W | 0.285 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Other data | Max. absorbed current | 1.27 | A | 1.27 | unit:A |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Other data | Sound pressure level | 31 | dB(A) | 31 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Other data | Sound power level | 54 | dB(A) | 54 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Other data | Static pressure | 44 | Pa | 44 | unit:PA |  |  | reference | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 6 | Heating column blank on the sheet; cooling-only selection.
B/07 | TO30-3R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Identification | Offer | CENTRAL LIBRARY REV1 | [5 empty] | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Identification | Range | TO | [5 empty] | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Identification | Version | TO | [5 empty] | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Identification | Model | TO30-3R-3 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Capacity | Total capacity (cooling) | 12 | kW | 12 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Capacity | Sensible capacity (cooling) | 12 | kW | 12 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Air | Inlet DBT | 27 | degC | 27 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Air | Inlet WBT | 16.7 | degC | 16.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Air | Inlet RH | 35 | % | 35 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Air | Outlet DBT | 12.8 | degC | 12.8 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Air | Outlet WBT | 11.4 | degC | 11.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Air | Outlet RH | 84 | % | 84 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Air | Flow rate | 2576 | m3/h | 715.556 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Air | Fan speed setting | 3 |  | 3 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Air | Air velocity | 1.49 | m/s | 1.49 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Air | Air pressure drop | 20.3 | Pa | 20.3 | unit:PA |  |  | reference | FCU_Manual.pdf | 7 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/07 | TO30-3R-3 | Fluid | Flow rate | 1296 | l/h | 0.36 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Fluid | Pressure drop | 8.6 | kPa | 8600 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Fluid | Outlet temperature | 15 | degC | 15 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Dimensions and weight | Max width | 920 | mm | 0.92 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Dimensions and weight | Max height | 420 | mm | 0.42 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Dimensions and weight | Max thickness | 1400 | mm | 1.4 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Dimensions and weight | Weight | 96 | kg | 96 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Other data | Max. absorbed power | 770 | W | 0.77 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Other data | Max. absorbed current | 4.06 | A | 4.06 | unit:A |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Other data | Sound pressure level | 46 | dB(A) | 46 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Other data | Sound power level | 66 | dB(A) | 66 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Other data | Static pressure | 55 | Pa | 55 | unit:PA |  |  | reference | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 7 | Heating column blank on the sheet; cooling-only selection.
B/09 | CR32-3R-6-5NC | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Identification | Offer | CENTRAL LIBRARY REV1 | [5 empty] | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Identification | Model | CR32-3R-6-5NC |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Capacity | Total capacity (cooling) | 9.03 | kW | 9.03 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Capacity | Sensible capacity (cooling) | 9.03 | kW | 9.03 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Air | Inlet DBT | 27 | degC | 27 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Air | Inlet WBT | 16.9 | degC | 16.9 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Air | Inlet RH | 36 | % | 36 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Air | Outlet DBT | 11.8 | degC | 11.8 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Air | Outlet WBT | 11.2 | degC | 11.2 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Air | Outlet RH | 93 | % | 93 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Air | Flow rate | 1820 | m3/h | 505.556 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Air | Air velocity | 1.26 | m/s | 1.26 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Air | Air pressure drop | 16 | Pa | 16 | unit:PA |  |  | reference | FCU_Manual.pdf | 8 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/09 | CR32-3R-6-5NC | Fluid | Flow rate | 972 | l/h | 0.27 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Fluid | Pressure drop | 14.8 | kPa | 14800 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Fluid | Outlet temperature | 15 | degC | 15 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Dimensions and weight | Max thickness | 1900 | mm | 1.9 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Dimensions and weight | Weight | 65 | kg | 65 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Other data | Max. absorbed power | 570 | W | 0.57 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Other data | Max. absorbed current | 2.89 | A | 2.89 | unit:A |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Other data | Sound pressure level | 39 | dB(A) | 39 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Other data | Sound power level | 62 | dB(A) | 62 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Other data | Static pressure | 39 | Pa | 39 | unit:PA |  |  | reference | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 8 | Heating column blank on the sheet; cooling-only selection.
B/10 | CR23-4R-7 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Identification | Offer | CL | [5 empty] | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Identification | Model | CR23-4R-7 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Capacity | Total capacity (cooling) | 3.67 | kW | 3.67 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Capacity | Sensible capacity (cooling) | 3.67 | kW | 3.67 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Air | Outlet DBT | 12 | degC | 12 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Air | Outlet WBT | 11.5 | degC | 11.5 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Air | Outlet RH | 94 | % | 94 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Air | Flow rate | 1106 | m3/h | 307.222 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Air | Fan speed setting | 7 |  | 7 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Air | Air velocity | 1.02 | m/s | 1.02 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Air | Air pressure drop | 15.9 | Pa | 15.9 | unit:PA |  |  | reference | FCU_Manual.pdf | 9 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/10 | CR23-4R-7 | Fluid | Flow rate | 360 | l/h | 0.1 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Fluid | Pressure drop | 1.5 | kPa | 1500 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Fluid | Outlet temperature | 15.7 | degC | 15.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Dimensions and weight | Max thickness | 1500 | mm | 1.5 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Dimensions and weight | Weight | 55 | kg | 55 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Other data | Max. absorbed power | 420 | W | 0.42 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Other data | Max. absorbed current | 2.11 | A | 2.11 | unit:A |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Other data | Sound pressure level | 37.5 | dB(A) | 37.5 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Other data | Sound power level | 58.5 | dB(A) | 58.5 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Other data | Static pressure | 40 | Pa | 40 | unit:PA |  |  | reference | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 9 | Heating column blank on the sheet; cooling-only selection.
B/11-12 (OPT-1) | CR23-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Identification | Offer | CENTRAL LIBRARY REV1 | [5 empty] | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Identification | Model | CR23-4R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Capacity | Total capacity (cooling) | 7.38 | kW | 7.38 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Capacity | Sensible capacity (cooling) | 7.38 | kW | 7.38 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Air | Inlet DBT | 27 | degC | 27 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Air | Inlet WBT | 16.7 | degC | 16.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Air | Inlet RH | 35 | % | 35 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Air | Outlet DBT | 11 | degC | 11 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Air | Outlet WBT | 10.6 | degC | 10.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Air | Outlet RH | 95 | % | 95 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Air | Flow rate | 1404 | m3/h | 390 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Air | Air velocity | 1.3 | m/s | 1.3 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Air | Air pressure drop | 22.1 | Pa | 22.1 | unit:PA |  |  | reference | FCU_Manual.pdf | 10 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/11-12 (OPT-1) | CR23-4R-6 | Fluid | Flow rate | 756 | l/h | 0.21 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Fluid | Pressure drop | 5.4 | kPa | 5400 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Fluid | Outlet temperature | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Dimensions and weight | Max thickness | 1500 | mm | 1.5 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Dimensions and weight | Weight | 55 | kg | 55 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Other data | Max. absorbed power | 420 | W | 0.42 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Other data | Max. absorbed current | 2.11 | A | 2.11 | unit:A |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Other data | Sound pressure level | 42 | dB(A) | 42 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Other data | Sound power level | 63 | dB(A) | 63 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Other data | Static pressure | 34 | Pa | 34 | unit:PA |  |  | reference | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 10 | Heating column blank on the sheet; cooling-only selection.
B/13-14 | CR23-4R-7 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Identification | Offer | CENTRAL LIBRARY REV1 | [5 empty] | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Identification | Model | CR23-4R-7 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Capacity | Total capacity (cooling) | 5.8 | kW | 5.8 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Capacity | Sensible capacity (cooling) | 5.8 | kW | 5.8 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Air | Inlet DBT | 27 | degC | 27 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Air | Inlet WBT | 16.7 | degC | 16.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Air | Inlet RH | 35 | % | 35 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Air | Outlet DBT | 10.6 | degC | 10.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Air | Outlet WBT | 10.5 | degC | 10.5 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Air | Outlet RH | 98 | % | 98 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Air | Flow rate | 1080 | m3/h | 300 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Air | Fan speed setting | 7 |  | 7 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Air | Air velocity | 1 | m/s | 1 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Air | Air pressure drop | 15.4 | Pa | 15.4 | unit:PA |  |  | reference | FCU_Manual.pdf | 11 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/13-14 | CR23-4R-7 | Fluid | Flow rate | 576 | l/h | 0.16 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Fluid | Pressure drop | 3.4 | kPa | 3400 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Fluid | Outlet temperature | 15.6 | degC | 15.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Dimensions and weight | Max thickness | 1500 | mm | 1.5 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Dimensions and weight | Weight | 55 | kg | 55 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Other data | Max. absorbed power | 420 | W | 0.42 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Other data | Max. absorbed current | 2.11 | A | 2.11 | unit:A |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Other data | Sound pressure level | 37.5 | dB(A) | 37.5 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Other data | Sound power level | 58.5 | dB(A) | 58.5 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Other data | Static pressure | 50 | Pa | 50 | unit:PA |  |  | reference | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 11 | Heating column blank on the sheet; cooling-only selection.
B/15-16 | CR26-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Identification | Offer | CENTRAL LIBRARY REV1 | [5 empty] | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Identification | Model | CR26-4R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Capacity | Total capacity (cooling) | 8.35 | kW | 8.35 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Capacity | Sensible capacity (cooling) | 8.35 | kW | 8.35 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Air | Inlet DBT | 27 | degC | 27 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Air | Inlet WBT | 16.7 | degC | 16.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Air | Inlet RH | 35 | % | 35 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Air | Outlet DBT | 10.9 | degC | 10.9 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Air | Outlet WBT | 10.6 | degC | 10.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Air | Outlet RH | 96 | % | 96 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Air | Flow rate | 1584 | m3/h | 440 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Air | Air velocity | 1.26 | m/s | 1.26 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Air | Air pressure drop | 21.1 | Pa | 21.1 | unit:PA |  |  | reference | FCU_Manual.pdf | 12 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/15-16 | CR26-4R-6 | Fluid | Flow rate | 864 | l/h | 0.24 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Fluid | Pressure drop | 5 | kPa | 5000 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Fluid | Outlet temperature | 15.3 | degC | 15.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Dimensions and weight | Max thickness | 1700 | mm | 1.7 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Dimensions and weight | Weight | 60 | kg | 60 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Other data | Max. absorbed power | 535 | W | 0.535 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Other data | Max. absorbed current | 2.48 | A | 2.48 | unit:A |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Other data | Sound pressure level | 35.6 | dB(A) | 35.6 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Other data | Sound power level | 58.6 | dB(A) | 58.6 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Other data | Static pressure | 46 | Pa | 46 | unit:PA |  |  | reference | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 12 | Heating column blank on the sheet; cooling-only selection.
B/18-21 | CR23-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Identification | Offer | CENTRAL LIBRARY REV1 | [5 empty] | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Identification | Model | CR23-4R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Capacity | Total capacity (cooling) | 7.31 | kW | 7.31 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Capacity | Sensible capacity (cooling) | 7.31 | kW | 7.31 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Air | Inlet DBT | 27 | degC | 27 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Air | Inlet WBT | 16.7 | degC | 16.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Air | Inlet RH | 35 | % | 35 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Air | Outlet DBT | 10.9 | degC | 10.9 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Air | Outlet WBT | 10.6 | degC | 10.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Air | Outlet RH | 96 | % | 96 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Air | Flow rate | 1386 | m3/h | 385 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Air | Air velocity | 1.28 | m/s | 1.28 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Air | Air pressure drop | 21.7 | Pa | 21.7 | unit:PA |  |  | reference | FCU_Manual.pdf | 13 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/18-21 | CR23-4R-6 | Fluid | Flow rate | 756 | l/h | 0.21 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Fluid | Pressure drop | 5.4 | kPa | 5400 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Fluid | Outlet temperature | 15.3 | degC | 15.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Dimensions and weight | Max thickness | 1500 | mm | 1.5 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Dimensions and weight | Weight | 55 | kg | 55 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Other data | Max. absorbed power | 420 | W | 0.42 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Other data | Max. absorbed current | 2.11 | A | 2.11 | unit:A |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Other data | Sound pressure level | 42 | dB(A) | 42 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Other data | Sound power level | 63 | dB(A) | 63 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Other data | Static pressure | 37 | Pa | 37 | unit:PA |  |  | reference | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 13 | Heating column blank on the sheet; cooling-only selection.
B/22-23 | FH105-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Identification | Offer | CENTRAL LIBRARY REV1 | [5 empty] | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Identification | Range | FH | [5 empty] | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Identification | Version | FOH | [5 empty] | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Identification | Model | FH105-3R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Capacity | Total capacity (cooling) | 5.32 | kW | 5.32 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Capacity | Sensible capacity (cooling) | 5.32 | kW | 5.32 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Air | Inlet DBT | 27 | degC | 27 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Air | Inlet WBT | 16.7 | degC | 16.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Air | Inlet RH | 35 | % | 35 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Air | Outlet DBT | 10.9 | degC | 10.9 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Air | Outlet WBT | 10.6 | degC | 10.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Air | Outlet RH | 96 | % | 96 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Air | Flow rate | 1008 | m3/h | 280 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Air | Air velocity | 0.7 | m/s | 0.7 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Air | Air pressure drop | 7.3 | Pa | 7.3 | unit:PA |  |  | reference | FCU_Manual.pdf | 14 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/22-23 | FH105-3R-6 | Fluid | Flow rate | 540 | l/h | 0.15 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Fluid | Pressure drop | 3.2 | kPa | 3200 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Fluid | Outlet temperature | 15.5 | degC | 15.5 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Dimensions and weight | Max width | 495 | mm | 0.495 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Dimensions and weight | Max height | 220 | mm | 0.22 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Dimensions and weight | Max thickness | 1900 | mm | 1.9 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Dimensions and weight | Weight | 56.5 | kg | 56.5 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Other data | Max. absorbed power | 300 | W | 0.3 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Other data | Max. absorbed current | 1.33 | A | 1.33 | unit:A |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Other data | Sound pressure level | 31.3 | dB(A) | 31.3 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Other data | Sound power level | 54.3 | dB(A) | 54.3 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Other data | Static pressure | 37 | Pa | 37 | unit:PA |  |  | reference | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 14 | Heating column blank on the sheet; cooling-only selection.
B/25-26 | TO50-4R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Identification | Offer | CENTRAL LIBRARY REV1 | [5 empty] | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Identification | Range | TO | [5 empty] | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Identification | Version | TO | [5 empty] | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Identification | Model | TO50-4R-3 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Capacity | Total capacity (cooling) | 19.16 | kW | 19.16 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Capacity | Sensible capacity (cooling) | 19.16 | kW | 19.16 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Air | Inlet DBT | 27 | degC | 27 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Air | Inlet WBT | 16.7 | degC | 16.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Air | Inlet RH | 35 | % | 35 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Air | Outlet DBT | 11.5 | degC | 11.5 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Air | Outlet WBT | 10.9 | degC | 10.9 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Air | Outlet RH | 92 | % | 92 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Air | Flow rate | 3780 | m3/h | 1050 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Air | Fan speed setting | 3 |  | 3 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Air | Air velocity | 1.64 | m/s | 1.64 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Air | Air pressure drop | 30.9 | Pa | 30.9 | unit:PA |  |  | reference | FCU_Manual.pdf | 15 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/25-26 | TO50-4R-3 | Fluid | Flow rate | 1980 | l/h | 0.55 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Fluid | Pressure drop | 6.7 | kPa | 6700 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Fluid | Outlet temperature | 15.3 | degC | 15.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Dimensions and weight | Max width | 920 | mm | 0.92 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Dimensions and weight | Max height | 420 | mm | 0.42 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Dimensions and weight | Max thickness | 1800 | mm | 1.8 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Dimensions and weight | Weight | 135 | kg | 135 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Other data | Max. absorbed power | 970 | W | 0.97 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Other data | Max. absorbed current | 4.9 | A | 4.9 | unit:A |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Other data | Sound pressure level | 47.1 | dB(A) | 47.1 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Other data | Sound power level | 67.1 | dB(A) | 67.1 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Other data | Static pressure | 69 | Pa | 69 | unit:PA |  |  | reference | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 15 | Heating column blank on the sheet; cooling-only selection.
B/27-28 | FH070-2R-7 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Identification | Offer | CL | [5 empty] | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Identification | Range | FH | [5 empty] | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Identification | Version | FOH | [5 empty] | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Identification | Model | FH070-2R-7 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Capacity | Total capacity (cooling) | 2.34 | kW | 2.34 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Capacity | Sensible capacity (cooling) | 2.34 | kW | 2.34 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Coil | Rows | 2 | n | 2 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Air | Outlet DBT | 12.8 | degC | 12.8 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Air | Outlet WBT | 11.8 | degC | 11.8 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Air | Outlet RH | 89 | % | 89 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Air | Flow rate | 770 | m3/h | 213.889 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Air | Fan speed setting | 7 |  | 7 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Air | Air velocity | 0.71 | m/s | 0.71 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Air | Air pressure drop | 5 | Pa | 5 | unit:PA |  |  | reference | FCU_Manual.pdf | 16 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/27-28 | FH070-2R-7 | Fluid | Flow rate | 251 | l/h | 0.069722 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Fluid | Pressure drop | 2.6 | kPa | 2600 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Fluid | Outlet temperature | 15 | degC | 15 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Dimensions and weight | Max width | 495 | mm | 0.495 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Dimensions and weight | Max height | 220 | mm | 0.22 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Dimensions and weight | Max thickness | 1500 | mm | 1.5 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Dimensions and weight | Weight | 32.5 | kg | 32.5 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Other data | Max. absorbed power | 281 | W | 0.281 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Other data | Max. absorbed current | 1.25 | A | 1.25 | unit:A |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Other data | Sound pressure level | 33.8 | dB(A) | 33.8 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Other data | Sound power level | 54.8 | dB(A) | 54.8 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Other data | Static pressure | 40 | Pa | 40 | unit:PA |  |  | reference | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 16 | Heating column blank on the sheet; cooling-only selection.
B/29 | CR32-4R-6-4NC | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Identification | Offer | CL | [5 empty] | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Identification | Model | CR32-4R-6-4NC |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Capacity | Total capacity (cooling) | 8.03 | kW | 8.03 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Capacity | Sensible capacity (cooling) | 6.9 | kW | 6.9 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Capacity | Condensed water | 1.51 | g/h | 0.00151 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Air | Outlet DBT | 10.4 | degC | 10.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Air | Outlet WBT | 10.1 | degC | 10.1 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Air | Outlet RH | 96 | % | 96 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Air | Flow rate | 1813 | m3/h | 503.611 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Air | Air velocity | 1.26 | m/s | 1.26 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Air | Air pressure drop | 24.3 | Pa | 24.3 | unit:PA |  |  | reference | FCU_Manual.pdf | 17 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/29 | CR32-4R-6-4NC | Fluid | Flow rate | 862 | l/h | 0.23944 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Fluid | Pressure drop | 28.4 | kPa | 28400 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Fluid | Outlet temperature | 15 | degC | 15 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Dimensions and weight | Max thickness | 1900 | mm | 1.9 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Dimensions and weight | Weight | 65 | kg | 65 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Other data | Max. absorbed power | 570 | W | 0.57 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Other data | Max. absorbed current | 2.89 | A | 2.89 | unit:A |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Other data | Sound pressure level | 39 | dB(A) | 39 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Other data | Sound power level | 62 | dB(A) | 62 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Other data | Static pressure | 40 | Pa | 40 | unit:PA |  |  | reference | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 17 | Heating column blank on the sheet; cooling-only selection.
B/30 | TO50-4R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Identification | Offer | CENTRAL LIBRARY REV1 | [5 empty] | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Identification | Range | TO | [5 empty] | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Identification | Version | TO | [5 empty] | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Identification | Model | TO50-4R-3 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Capacity | Total capacity (cooling) | 17.59 | kW | 17.59 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Capacity | Sensible capacity (cooling) | 17.59 | kW | 17.59 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Air | Inlet DBT | 27 | degC | 27 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Air | Inlet WBT | 16.7 | degC | 16.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Air | Inlet RH | 35 | % | 35 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Air | Outlet DBT | 11.3 | degC | 11.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Air | Outlet WBT | 10.7 | degC | 10.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Air | Outlet RH | 93 | % | 93 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Air | Flow rate | 3420 | m3/h | 950 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Air | Fan speed setting | 3 |  | 3 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Air | Air velocity | 1.48 | m/s | 1.48 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Air | Air pressure drop | 26.7 | Pa | 26.7 | unit:PA |  |  | reference | FCU_Manual.pdf | 18 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
B/30 | TO50-4R-3 | Fluid | Flow rate | 1800 | l/h | 0.5 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Fluid | Pressure drop | 5.6 | kPa | 5600 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Fluid | Outlet temperature | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Dimensions and weight | Max width | 920 | mm | 0.92 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Dimensions and weight | Max height | 420 | mm | 0.42 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Dimensions and weight | Max thickness | 1800 | mm | 1.8 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Dimensions and weight | Weight | 135 | kg | 135 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Other data | Max. absorbed power | 970 | W | 0.97 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Other data | Max. absorbed current | 4.9 | A | 4.9 | unit:A |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Other data | Sound pressure level | 47.1 | dB(A) | 47.1 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Other data | Sound power level | 67.1 | dB(A) | 67.1 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Other data | Static pressure | 85 | Pa | 85 | unit:PA |  |  | reference | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 18 | Heating column blank on the sheet; cooling-only selection.
FCU/B/31 | CR32-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Identification | Offer | CENTRAL LIBRARY REV1 | [5 empty] | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Identification | Model | CR32-3R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Capacity | Total capacity (cooling) | 6.09 | kW | 6.09 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Capacity | Sensible capacity (cooling) | 6.09 | kW | 6.09 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Air | Outlet DBT | 12 | degC | 12 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Air | Outlet WBT | 11.5 | degC | 11.5 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Air | Outlet RH | 94 | % | 94 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Air | Flow rate | 1836 | m3/h | 510 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Air | Air velocity | 1.28 | m/s | 1.28 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Air | Air pressure drop | 16.2 | Pa | 16.2 | unit:PA |  |  | reference | FCU_Manual.pdf | 19 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
FCU/B/31 | CR32-3R-6 | Fluid | Flow rate | 720 | l/h | 0.2 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Fluid | Pressure drop | 3.3 | kPa | 3300 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Fluid | Outlet temperature | 14.3 | degC | 14.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Dimensions and weight | Max thickness | 1900 | mm | 1.9 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Dimensions and weight | Weight | 65 | kg | 65 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Other data | Max. absorbed power | 570 | W | 0.57 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Other data | Max. absorbed current | 2.89 | A | 2.89 | unit:A |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Other data | Sound pressure level | 39 | dB(A) | 39 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Other data | Sound power level | 62 | dB(A) | 62 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Other data | Static pressure | 37 | Pa | 37 | unit:PA |  |  | reference | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 19 | Heating column blank on the sheet; cooling-only selection.
FCU/1F/01 | CR26-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Identification | Offer | CENTRAL LIBRARY | [5 empty] | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Identification | Version | CMO-CMOG | [5 empty] | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Identification | Model | CR26-3R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Capacity | Total capacity (cooling) | 6.12 | kW | 6.12 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Capacity | Sensible capacity (cooling) | 6.12 | kW | 6.12 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Air | Outlet DBT | 12.4 | degC | 12.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Air | Outlet WBT | 11.7 | degC | 11.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Air | Outlet RH | 92 | % | 92 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Air | Flow rate | 1925 | m3/h | 534.722 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Air | Air velocity | 1.53 | m/s | 1.53 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Air | Air pressure drop | 21 | Pa | 21 | unit:PA |  |  | reference | FCU_Manual.pdf | 20 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
FCU/1F/01 | CR26-3R-6 | Fluid | Flow rate | 720 | l/h | 0.2 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Fluid | Pressure drop | 4.8 | kPa | 4800 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Fluid | Outlet temperature | 14.3 | degC | 14.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Dimensions and weight | Max width | 1580 | mm | 1.58 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Dimensions and weight | Max height | 285 | mm | 0.285 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Dimensions and weight | Max thickness | 840 | mm | 0.84 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Dimensions and weight | Weight | 46 | kg | 46 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Other data | Max. absorbed power | 535 | W | 0.535 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Other data | Max. absorbed current | 2.48 | A | 2.48 | unit:A |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Other data | Sound pressure level | 47.6 | dB(A) | 47.6 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Other data | Sound power level | 58.6 | dB(A) | 58.6 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Other data | Static pressure | 10 | Pa | 10 | unit:PA |  |  | reference | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 20 | Heating column blank on the sheet; cooling-only selection.
1F/02-03 | TO30-4R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Identification | Offer | CENTRAL LIBRARY | [5 empty] | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Identification | Range | TO | [5 empty] | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Identification | Version | TO | [5 empty] | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Identification | Model | TO30-4R-3 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Capacity | Total capacity (cooling) | 9.09 | kW | 9.09 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Capacity | Sensible capacity (cooling) | 9.09 | kW | 9.09 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Air | Outlet DBT | 11.7 | degC | 11.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Air | Outlet WBT | 11.4 | degC | 11.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Air | Outlet RH | 96 | % | 96 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Air | Flow rate | 2648 | m3/h | 735.556 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Air | Fan speed setting | 3 |  | 3 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Air | Air velocity | 1.53 | m/s | 1.53 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Air | Air pressure drop | 28 | Pa | 28 | unit:PA |  |  | reference | FCU_Manual.pdf | 21 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
1F/02-03 | TO30-4R-3 | Fluid | Flow rate | 972 | l/h | 0.27 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Fluid | Pressure drop | 3.4 | kPa | 3400 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Fluid | Outlet temperature | 15 | degC | 15 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Dimensions and weight | Max width | 920 | mm | 0.92 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Dimensions and weight | Max height | 420 | mm | 0.42 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Dimensions and weight | Max thickness | 1400 | mm | 1.4 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Dimensions and weight | Weight | 96 | kg | 96 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Other data | Max. absorbed power | 770 | W | 0.77 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Other data | Max. absorbed current | 4.06 | A | 4.06 | unit:A |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Other data | Sound pressure level | 46 | dB(A) | 46 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Other data | Sound power level | 66 | dB(A) | 66 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Other data | Static pressure | 40 | Pa | 40 | unit:PA |  |  | reference | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 21 | Heating column blank on the sheet; cooling-only selection.
1F/04-54 | CR17-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Identification | Offer | CENTRAL LIBRARY | [5 empty] | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Identification | Model | CR17-4R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Capacity | Total capacity (cooling) | 3.73 | kW | 3.73 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Capacity | Sensible capacity (cooling) | 3.26 | kW | 3.26 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Capacity | Condensed water | 0.61 | g/h | 0.00061 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Air | Inlet DBT | 24 | degC | 24 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Air | Inlet WBT | 17 | degC | 17 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Air | Outlet DBT | 11.9 | degC | 11.9 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Air | Outlet WBT | 11.9 | degC | 11.9 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Air | Outlet RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Air | Flow rate | 825 | m3/h | 229.167 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Air | Air velocity | 1.15 | m/s | 1.15 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Air | Air pressure drop | 21 | Pa | 21 | unit:PA |  |  | reference | FCU_Manual.pdf | 22 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
1F/04-54 | CR17-4R-6 | Fluid | Flow rate | 396 | l/h | 0.11 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Fluid | Pressure drop | 2.3 | kPa | 2300 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Fluid | Outlet temperature | 15.1 | degC | 15.1 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Dimensions and weight | Max thickness | 1100 | mm | 1.1 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Dimensions and weight | Weight | 36 | kg | 36 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Other data | Max. absorbed power | 253 | W | 0.253 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Other data | Max. absorbed current | 1.16 | A | 1.16 | unit:A |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Other data | Sound pressure level | 33.9 | dB(A) | 33.9 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Other data | Sound power level | 54.9 | dB(A) | 54.9 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Other data | Static pressure | 40 | Pa | 40 | unit:PA |  |  | reference | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 22 | Heating column blank on the sheet; cooling-only selection.
1F/55 | TO50-4R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Identification | Offer | CENTRAL LIBRARY | [5 empty] | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Identification | Range | TO | [5 empty] | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Identification | Version | TI | [5 empty] | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Identification | Model | TO50-4R-3 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Capacity | Total capacity (cooling) | 14.14 | kW | 14.14 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Capacity | Sensible capacity (cooling) | 14.14 | kW | 14.14 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Air | Outlet DBT | 11.9 | degC | 11.9 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Air | Outlet WBT | 11.5 | degC | 11.5 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Air | Outlet RH | 95 | % | 95 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Air | Flow rate | 4189 | m3/h | 1163.61 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Air | Fan speed setting | 3 |  | 3 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Air | Air velocity | 1.82 | m/s | 1.82 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Air | Air pressure drop | 36 | Pa | 36 | unit:PA |  |  | reference | FCU_Manual.pdf | 23 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
1F/55 | TO50-4R-3 | Fluid | Flow rate | 1512 | l/h | 0.42 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Fluid | Pressure drop | 4.1 | kPa | 4100 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Fluid | Outlet temperature | 15 | degC | 15 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Dimensions and weight | Max width | 1800 | mm | 1.8 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Dimensions and weight | Max height | 920 | mm | 0.92 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Dimensions and weight | Max thickness | 420 | mm | 0.42 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Dimensions and weight | Weight | 132 | kg | 132 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Other data | Max. absorbed power | 970 | W | 0.97 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Other data | Max. absorbed current | 4.9 | A | 4.9 | unit:A |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Other data | Sound pressure level | 47.1 | dB(A) | 47.1 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Other data | Sound power level | 67.1 | dB(A) | 67.1 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Other data | Static pressure | 40 | Pa | 40 | unit:PA |  |  | reference | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 23 | Heating column blank on the sheet; cooling-only selection.
1F/55 | TO50-4R-3 | Data quality | Sheet note | Dimensions row order differs on this sheet: Max Width 1800, Max Height 920, Max Thickness 420. Compare with the other TO50 sheets (920 / 420 / 1800) before use. | [6 empty] | FCU_Manual.pdf | 23 | Confirm with the supplier before use
1F/56 | CR09-3R-7 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Identification | Offer | CENTRAL LIBRARY | [5 empty] | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Identification | Version | CMO-CMOG | [5 empty] | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Identification | Model | CR09-3R-7 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Capacity | Total capacity (cooling) | 3.08 | kW | 3.08 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Capacity | Sensible capacity (cooling) | 2.03 | kW | 2.03 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Capacity | Condensed water | 1.42 | g/h | 0.00142 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Air | Inlet DBT | 28 | degC | 28 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Air | Inlet WBT | 20.3 | degC | 20.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Air | Outlet DBT | 14.6 | degC | 14.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Air | Outlet WBT | 13.6 | degC | 13.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Air | Outlet RH | 89 | % | 89 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Air | Flow rate | 473 | m3/h | 131.389 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Air | Fan speed setting | 7 |  | 7 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Air | Air velocity | 1.31 | m/s | 1.31 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Air | Air pressure drop | 25.2 | Pa | 25.2 | unit:PA |  |  | reference | FCU_Manual.pdf | 24 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
1F/56 | CR09-3R-7 | Fluid | Flow rate | 331 | l/h | 0.091944 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Fluid | Pressure drop | 9.8 | kPa | 9800 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Fluid | Outlet temperature | 15 | degC | 15 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Dimensions and weight | Max width | 580 | mm | 0.58 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Dimensions and weight | Max height | 285 | mm | 0.285 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Dimensions and weight | Max thickness | 840 | mm | 0.84 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Dimensions and weight | Weight | 73.5 | kg | 73.5 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Other data | Max. absorbed power | 178 | W | 0.178 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Other data | Max. absorbed current | 1 | A | 1 | unit:A |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Other data | Sound pressure level | 47.7 | dB(A) | 47.7 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Other data | Sound power level | 56.7 | dB(A) | 56.7 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Other data | Static pressure | 40 | Pa | 40 | unit:PA |  |  | reference | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 24 | Heating column blank on the sheet; cooling-only selection.
1F/57-58 | CR17-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Identification | Offer | CENTRAL LIBRARY | [5 empty] | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Identification | Model | CR17-4R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Capacity | Total capacity (cooling) | 3.73 | kW | 3.73 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Capacity | Sensible capacity (cooling) | 3.26 | kW | 3.26 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Capacity | Condensed water | 0.61 | g/h | 0.00061 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Air | Inlet DBT | 24 | degC | 24 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Air | Inlet WBT | 17 | degC | 17 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Air | Outlet DBT | 11.9 | degC | 11.9 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Air | Outlet WBT | 11.9 | degC | 11.9 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Air | Outlet RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Air | Flow rate | 825 | m3/h | 229.167 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Air | Air velocity | 1.15 | m/s | 1.15 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Air | Air pressure drop | 21 | Pa | 21 | unit:PA |  |  | reference | FCU_Manual.pdf | 25 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
1F/57-58 | CR17-4R-6 | Fluid | Flow rate | 396 | l/h | 0.11 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Fluid | Pressure drop | 2.3 | kPa | 2300 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Fluid | Outlet temperature | 15.1 | degC | 15.1 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Dimensions and weight | Max thickness | 1100 | mm | 1.1 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Dimensions and weight | Weight | 36 | kg | 36 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Other data | Max. absorbed power | 253 | W | 0.253 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Other data | Max. absorbed current | 1.16 | A | 1.16 | unit:A |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Other data | Sound pressure level | 33.9 | dB(A) | 33.9 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Other data | Sound power level | 54.9 | dB(A) | 54.9 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Other data | Static pressure | 40 | Pa | 40 | unit:PA |  |  | reference | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 25 | Heating column blank on the sheet; cooling-only selection.
FCU/2F/01-04 | CR26-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Identification | Offer | CENTRAL LIBRARY | [5 empty] | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Identification | Version | CMO-CMOG | [5 empty] | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Identification | Model | CR26-3R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Capacity | Total capacity (cooling) | 6.12 | kW | 6.12 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Capacity | Sensible capacity (cooling) | 6.12 | kW | 6.12 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Air | Outlet DBT | 12.4 | degC | 12.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Air | Outlet WBT | 11.7 | degC | 11.7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Air | Outlet RH | 92 | % | 92 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Air | Flow rate | 1925 | m3/h | 534.722 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Air | Air velocity | 1.53 | m/s | 1.53 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Air | Air pressure drop | 21 | Pa | 21 | unit:PA |  |  | reference | FCU_Manual.pdf | 26 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
FCU/2F/01-04 | CR26-3R-6 | Fluid | Flow rate | 720 | l/h | 0.2 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Fluid | Pressure drop | 4.8 | kPa | 4800 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Fluid | Outlet temperature | 14.3 | degC | 14.3 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Dimensions and weight | Max width | 1580 | mm | 1.58 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Dimensions and weight | Max height | 285 | mm | 0.285 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Dimensions and weight | Max thickness | 840 | mm | 0.84 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Dimensions and weight | Weight | 46 | kg | 46 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Other data | Max. absorbed power | 535 | W | 0.535 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Other data | Max. absorbed current | 2.48 | A | 2.48 | unit:A |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Other data | Sound pressure level | 47.6 | dB(A) | 47.6 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Other data | Sound power level | 58.6 | dB(A) | 58.6 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Other data | Static pressure | 10 | Pa | 10 | unit:PA |  |  | reference | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 26 | Heating column blank on the sheet; cooling-only selection.
2F/05 | TO30-4R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Identification | Offer | CENTRAL LIBRARY | [5 empty] | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Identification | Range | TO | [5 empty] | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Identification | Version | TO | [5 empty] | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Identification | Model | TO30-4R-3 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Capacity | Total capacity (cooling) | 9.07 | kW | 9.07 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Capacity | Sensible capacity (cooling) | 9.07 | kW | 9.07 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Coil | Rows | 4 | n | 4 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Air | Outlet DBT | 11.6 | degC | 11.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Air | Outlet WBT | 11.4 | degC | 11.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Air | Outlet RH | 97 | % | 97 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Air | Flow rate | 2646 | m3/h | 735 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Air | Fan speed setting | 3 |  | 3 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Air | Air velocity | 1.53 | m/s | 1.53 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Air | Air pressure drop | 27.9 | Pa | 27.9 | unit:PA |  |  | reference | FCU_Manual.pdf | 27 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
2F/05 | TO30-4R-3 | Fluid | Flow rate | 972 | l/h | 0.27 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Fluid | Pressure drop | 3.4 | kPa | 3400 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Fluid | Outlet temperature | 15 | degC | 15 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Dimensions and weight | Max width | 920 | mm | 0.92 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Dimensions and weight | Max height | 420 | mm | 0.42 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Dimensions and weight | Max thickness | 1400 | mm | 1.4 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Dimensions and weight | Weight | 96 | kg | 96 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Other data | Max. absorbed power | 770 | W | 0.77 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Other data | Max. absorbed current | 4.06 | A | 4.06 | unit:A |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Other data | Sound pressure level | 46 | dB(A) | 46 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Other data | Sound power level | 66 | dB(A) | 66 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Other data | Static pressure | 40 | Pa | 40 | unit:PA |  |  | reference | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 27 | Heating column blank on the sheet; cooling-only selection.
2F/06-29 | CR26-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Identification | Offer | CENTRAL LIBRARY | [5 empty] | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Identification | Model | CR26-3R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Capacity | Total capacity (cooling) | 4.45 | kW | 4.45 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Capacity | Sensible capacity (cooling) | 4.17 | kW | 4.17 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Capacity | Condensed water | 0.3 | g/h | 0.0003 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Air | Inlet DBT | 24 | degC | 24 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Air | Inlet WBT | 18.6 | degC | 18.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Air | Inlet RH | 60 | % | 60 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Air | Outlet DBT | 15.5 | degC | 15.5 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Air | Outlet WBT | 15.5 | degC | 15.5 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Air | Outlet RH | 100 | % | 100 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Air | Flow rate | 1512 | m3/h | 420 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Air | Air velocity | 1.2 | m/s | 1.2 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Air | Air pressure drop | 15.7 | Pa | 15.7 | unit:PA |  |  | reference | FCU_Manual.pdf | 28 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
2F/06-29 | CR26-3R-6 | Fluid | Flow rate | 360 | l/h | 0.1 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Fluid | Pressure drop | 1.4 | kPa | 1400 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Fluid | Outlet temperature | 17.6 | degC | 17.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Dimensions and weight | Max thickness | 1700 | mm | 1.7 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Dimensions and weight | Weight | 60 | kg | 60 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Other data | Max. absorbed power | 535 | W | 0.535 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Other data | Max. absorbed current | 2.48 | A | 2.48 | unit:A |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Other data | Sound pressure level | 35.6 | dB(A) | 35.6 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Other data | Sound power level | 58.6 | dB(A) | 58.6 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Other data | Static pressure | 54 | Pa | 54 | unit:PA |  |  | reference | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 28 | Heating column blank on the sheet; cooling-only selection.
2F/30-33 | CR20-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  |  |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Identification | Offer | CENTRAL LIBRARY | [5 empty] | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Identification | Range | CR | [5 empty] | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Identification | Version | CPR | [5 empty] | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Identification | Model | CR20-3R-6 |  |  |  |  | rec:modelNumber | core | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Capacity | Total capacity (cooling) | 2.95 | kW | 2.95 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Capacity | Sensible capacity (cooling) | 2.95 | kW | 2.95 | unit:KiloW |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Capacity | Condensed water | 0 | g/h | 0 | unit:KiloGM-PER-HR | g/h / 1000; unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Coil | Rows | 3 | n | 3 | unit:UNITLESS |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Air | Inlet DBT | 22 | degC | 22 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Air | Inlet WBT | 15.4 | degC | 15.4 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Air | Inlet RH | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Air | Outlet DBT | 12.1 | degC | 12.1 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Air | Outlet WBT | 11.6 | degC | 11.6 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Air | Outlet RH | 94 | % | 94 | unit:PERCENT_RH |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Air | Flow rate | 902 | m3/h | 250.556 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Air | Fan speed setting | 6 |  | 6 | unit:UNITLESS | dimensionless ratio |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Air | Air velocity | 1 | m/s | 1 | unit:M-PER-SEC | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Air | Air pressure drop | 11.6 | Pa | 11.6 | unit:PA |  |  | reference | FCU_Manual.pdf | 29 | Row printed as 'Perdita di carico aria [degC]' on this sheet - untranslated label with the wrong unit; the value is Pa.
2F/30-33 | CR20-3R-6 | Fluid | Flow rate | 317 | l/h | 0.088056 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Fluid | Pressure drop | 2.4 | kPa | 2400 | unit:PA | kPa x 1000 |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Fluid | Inlet temperature | 7 | degC | 7 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Fluid | Outlet temperature | 15 | degC | 15 | unit:DEG_C |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Fluid | Fluid | Water | [5 empty] | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Dimensions and weight | Max width | 575 | mm | 0.575 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Dimensions and weight | Max height | 275 | mm | 0.275 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Dimensions and weight | Max thickness | 1300 | mm | 1.3 | unit:M | mm / 1000 |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Dimensions and weight | Weight | 42 | kg | 42 | unit:KiloGM | unit not used in Dar Cairo |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Other data | Power supply | V230/1/50-60Hz | V-ph-Hz |  |  | composite nameplate string, not a quantity |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Other data | Max. absorbed power | 294 | W | 0.294 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Other data | Max. absorbed current | 1.44 | A | 1.44 | unit:A |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Other data | Sound pressure level | 36.7 | dB(A) | 36.7 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Other data | Sound power level | 57.7 | dB(A) | 57.7 | unit:DeciB | A-weighting kept in the property name |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Other data | Static pressure | 40 | Pa | 40 | unit:PA |  |  | reference | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Capacity | Heating capacity | - | kW | - | unit:KiloW |  |  | reference | FCU_Manual.pdf | 29 | Heating column blank on the sheet; cooling-only selection.

## Heat Exchangers
Heat Exchangers
Plate heat exchangers PHX/B/01 to PHX/B/04 - SCHEDULE OF HEAT EXCHANGER. The supplied image crops the title block, so the drawing number and sheet are not recorded.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
PHX/B/01 |  | Identification | Make | ALFA LAVAL |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/01 |  | Identification | Type | COUNTER CURRENT | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/01 |  | Identification | Location | PLANT ROOM-4 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/01 |  | Identification | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/01 |  | Dimensions and weight | Unit dimension (L x W x H) | 2735x780x2165 | mm | 2.735 x 0.78 x 2.165 | unit:M | mm / 1000 |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/01 |  | Dimensions and weight | Operating weight | 4430 | kg | 4430 | unit:KiloGM | unit not used in Dar Cairo |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/01 |  | CHW flow rate | Cold side | 62.8 | l/s | 62.8 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/01 |  | CHW flow rate | Hot side | 62.2 | l/s | 62.2 | unit:L-PER-SEC |  | para:ratedWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER | Brick 1.4 has no water-flowrate entity property at all; Dar Cairo's generic para: term is the next rung of the ladder and already exists
PHX/B/02 |  | Identification | Make | ALFA LAVAL |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/02 |  | Identification | Type | COUNTER CURRENT | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/02 |  | Identification | Location | PLANT ROOM-4 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/02 |  | Identification | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/02 |  | Dimensions and weight | Unit dimension (L x W x H) | 2735x780x2165 | mm | 2.735 x 0.78 x 2.165 | unit:M | mm / 1000 |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/02 |  | Dimensions and weight | Operating weight | 4430 | kg | 4430 | unit:KiloGM | unit not used in Dar Cairo |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/02 |  | CHW flow rate | Cold side | 62.8 | l/s | 62.8 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/02 |  | CHW flow rate | Hot side | 62.2 | l/s | 62.2 | unit:L-PER-SEC |  | para:ratedWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER | Brick 1.4 has no water-flowrate entity property at all; Dar Cairo's generic para: term is the next rung of the ladder and already exists
PHX/B/03 |  | Identification | Make | ALFA LAVAL |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/03 |  | Identification | Type | COUNTER CURRENT | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/03 |  | Identification | Location | PLANT ROOM-4 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/03 |  | Identification | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/03 |  | Dimensions and weight | Unit dimension (L x W x H) | 2735x780x2165 | mm | 2.735 x 0.78 x 2.165 | unit:M | mm / 1000 |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/03 |  | Dimensions and weight | Operating weight | 4430 | kg | 4430 | unit:KiloGM | unit not used in Dar Cairo |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/03 |  | CHW flow rate | Cold side | 62.8 | l/s | 62.8 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/03 |  | CHW flow rate | Hot side | 62.2 | l/s | 62.2 | unit:L-PER-SEC |  | para:ratedWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER | Brick 1.4 has no water-flowrate entity property at all; Dar Cairo's generic para: term is the next rung of the ladder and already exists
PHX/B/04 |  | Identification | Make | ALFA LAVAL |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/04 |  | Identification | Type | COUNTER CURRENT | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/04 |  | Identification | Location | PLANT ROOM-4 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/04 |  | Identification | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/04 |  | Dimensions and weight | Unit dimension (L x W x H) | 2735x780x2165 | mm | 2.735 x 0.78 x 2.165 | unit:M | mm / 1000 |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/04 |  | Dimensions and weight | Operating weight | 4430 | kg | 4430 | unit:KiloGM | unit not used in Dar Cairo |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/04 |  | CHW flow rate | Cold side | 62.8 | l/s | 62.8 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/04 |  | CHW flow rate | Hot side | 62.2 | l/s | 62.2 | unit:L-PER-SEC |  | para:ratedWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER | Brick 1.4 has no water-flowrate entity property at all; Dar Cairo's generic para: term is the next rung of the ladder and already exists
PHX/B/01 | T20-BFG | Identification | Duty or standby | Duty HEX | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/01 | T20-BFG | Identification | Model | T20-BFG |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/01 | T20-BFG | Design condition | Hot side temperature | 15.5 degC in, 6.5 degC out | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule | SYSTEM DETAILS states one figure across all five rows
PHX/B/01 | T20-BFG | Design condition | Cold side temperature | 5.5 degC in, 14.4 degC out | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule | SYSTEM DETAILS states one figure across all five rows
PHX/B/01 | T20-BFG | Project | Project | QF Central Library | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/01 | T20-BFG | Project | Contractor | Mercury Engineering Qatar | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/01 | T20-BFG | Project | Consultant | ASTAD Project Management | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/01 | T20-BFG | Construction | Item reference | PHX/B/01-04-2350 KW | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/01 | T20-BFG | Construction | Duty | 2350 | kW | 2350 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger Brick 1.4 has no heat-exchanger duty property; coolingCapacity is the Brick term and these exchangers deliver cooling to the secondary loop
PHX/B/01 | T20-BFG | Construction | Number of plates | 423 | n | 423 | unit:UNITLESS |  |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/01 | T20-BFG | Construction | Plate material | Stainless Steel 316 | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/01 | T20-BFG | Construction | Plate thickness | 0.6 | mm | 0.0006 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/01 | T20-BFG | Construction | Effective heat transfer area | 380.7 | m2 | 380.7 | unit:M2 |  |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/01 | T20-BFG | Construction | Overall heat transfer coefficient | 5890 / 6478 (dirty / clean) | W/m2 K | 5890 / 6478 (dirty / clean) | unit:W-PER-M2-K | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/01 | T20-BFG | Construction | Packed dimensions per PHE (L x W x H) | 3000 x 890 x 2500 | mm | 3 x 0.89 x 2.5 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/01 | T20-BFG | Construction | Packed weight per PHE | 3810 | kg | 3810 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/01 | T20-BFG | Construction | Overall dimensions per PHE (L x W x H) | 2735 x 780 x 2165 | mm | 2.735 x 0.78 x 2.165 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/01 | T20-BFG | Construction | Net weight, empty | 3640 | kg | 3640 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/01 | T20-BFG | Construction | Net weight, operating | 4430 | kg | 4430 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/02 | T20-BFG | Identification | Duty or standby | Duty HEX | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/02 | T20-BFG | Identification | Model | T20-BFG |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/02 | T20-BFG | Design condition | Hot side temperature | 15.5 degC in, 6.5 degC out | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule | SYSTEM DETAILS states one figure across all five rows
PHX/B/02 | T20-BFG | Design condition | Cold side temperature | 5.5 degC in, 14.4 degC out | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule | SYSTEM DETAILS states one figure across all five rows
PHX/B/02 | T20-BFG | Project | Project | QF Central Library | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/02 | T20-BFG | Project | Contractor | Mercury Engineering Qatar | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/02 | T20-BFG | Project | Consultant | ASTAD Project Management | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/02 | T20-BFG | Construction | Item reference | PHX/B/01-04-2350 KW | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/02 | T20-BFG | Construction | Duty | 2350 | kW | 2350 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger Brick 1.4 has no heat-exchanger duty property; coolingCapacity is the Brick term and these exchangers deliver cooling to the secondary loop
PHX/B/02 | T20-BFG | Construction | Number of plates | 423 | n | 423 | unit:UNITLESS |  |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/02 | T20-BFG | Construction | Plate material | Stainless Steel 316 | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/02 | T20-BFG | Construction | Plate thickness | 0.6 | mm | 0.0006 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/02 | T20-BFG | Construction | Effective heat transfer area | 380.7 | m2 | 380.7 | unit:M2 |  |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/02 | T20-BFG | Construction | Overall heat transfer coefficient | 5890 / 6478 (dirty / clean) | W/m2 K | 5890 / 6478 (dirty / clean) | unit:W-PER-M2-K | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/02 | T20-BFG | Construction | Packed dimensions per PHE (L x W x H) | 3000 x 890 x 2500 | mm | 3 x 0.89 x 2.5 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/02 | T20-BFG | Construction | Packed weight per PHE | 3810 | kg | 3810 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/02 | T20-BFG | Construction | Overall dimensions per PHE (L x W x H) | 2735 x 780 x 2165 | mm | 2.735 x 0.78 x 2.165 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/02 | T20-BFG | Construction | Net weight, empty | 3640 | kg | 3640 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/02 | T20-BFG | Construction | Net weight, operating | 4430 | kg | 4430 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/03 | T20-BFG | Identification | Duty or standby | Duty HEX | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/03 | T20-BFG | Identification | Model | T20-BFG |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/03 | T20-BFG | Design condition | Hot side temperature | 15.5 degC in, 6.5 degC out | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule | SYSTEM DETAILS states one figure across all five rows
PHX/B/03 | T20-BFG | Design condition | Cold side temperature | 5.5 degC in, 14.4 degC out | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule | SYSTEM DETAILS states one figure across all five rows
PHX/B/03 | T20-BFG | Project | Project | QF Central Library | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/03 | T20-BFG | Project | Contractor | Mercury Engineering Qatar | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/03 | T20-BFG | Project | Consultant | ASTAD Project Management | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/03 | T20-BFG | Construction | Item reference | PHX/B/01-04-2350 KW | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/03 | T20-BFG | Construction | Duty | 2350 | kW | 2350 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger Brick 1.4 has no heat-exchanger duty property; coolingCapacity is the Brick term and these exchangers deliver cooling to the secondary loop
PHX/B/03 | T20-BFG | Construction | Number of plates | 423 | n | 423 | unit:UNITLESS |  |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/03 | T20-BFG | Construction | Plate material | Stainless Steel 316 | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/03 | T20-BFG | Construction | Plate thickness | 0.6 | mm | 0.0006 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/03 | T20-BFG | Construction | Effective heat transfer area | 380.7 | m2 | 380.7 | unit:M2 |  |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/03 | T20-BFG | Construction | Overall heat transfer coefficient | 5890 / 6478 (dirty / clean) | W/m2 K | 5890 / 6478 (dirty / clean) | unit:W-PER-M2-K | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/03 | T20-BFG | Construction | Packed dimensions per PHE (L x W x H) | 3000 x 890 x 2500 | mm | 3 x 0.89 x 2.5 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/03 | T20-BFG | Construction | Packed weight per PHE | 3810 | kg | 3810 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/03 | T20-BFG | Construction | Overall dimensions per PHE (L x W x H) | 2735 x 780 x 2165 | mm | 2.735 x 0.78 x 2.165 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/03 | T20-BFG | Construction | Net weight, empty | 3640 | kg | 3640 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/03 | T20-BFG | Construction | Net weight, operating | 4430 | kg | 4430 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/04 | T20-BFG | Identification | Duty or standby | Standby HEX | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/04 | T20-BFG | Identification | Model | T20-BFG |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/04 | T20-BFG | Design condition | Hot side temperature | 15.5 degC in, 6.5 degC out | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule | SYSTEM DETAILS states one figure across all five rows
PHX/B/04 | T20-BFG | Design condition | Cold side temperature | 5.5 degC in, 14.4 degC out | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule | SYSTEM DETAILS states one figure across all five rows
PHX/B/04 | T20-BFG | Project | Project | QF Central Library | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/04 | T20-BFG | Project | Contractor | Mercury Engineering Qatar | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/04 | T20-BFG | Project | Consultant | ASTAD Project Management | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/04 | T20-BFG | Construction | Item reference | PHX/B/01-04-2350 KW | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/04 | T20-BFG | Construction | Duty | 2350 | kW | 2350 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger Brick 1.4 has no heat-exchanger duty property; coolingCapacity is the Brick term and these exchangers deliver cooling to the secondary loop
PHX/B/04 | T20-BFG | Construction | Number of plates | 423 | n | 423 | unit:UNITLESS |  |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/04 | T20-BFG | Construction | Plate material | Stainless Steel 316 | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/04 | T20-BFG | Construction | Plate thickness | 0.6 | mm | 0.0006 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/04 | T20-BFG | Construction | Effective heat transfer area | 380.7 | m2 | 380.7 | unit:M2 |  |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/04 | T20-BFG | Construction | Overall heat transfer coefficient | 5890 / 6478 (dirty / clean) | W/m2 K | 5890 / 6478 (dirty / clean) | unit:W-PER-M2-K | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/04 | T20-BFG | Construction | Packed dimensions per PHE (L x W x H) | 3000 x 890 x 2500 | mm | 3 x 0.89 x 2.5 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/04 | T20-BFG | Construction | Packed weight per PHE | 3810 | kg | 3810 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/04 | T20-BFG | Construction | Overall dimensions per PHE (L x W x H) | 2735 x 780 x 2165 | mm | 2.735 x 0.78 x 2.165 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/04 | T20-BFG | Construction | Net weight, empty | 3640 | kg | 3640 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/04 | T20-BFG | Construction | Net weight, operating | 4430 | kg | 4430 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Identification | Duty or standby | Main HEX | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/05 | M10-MFM | Identification | Model | M10-MFM |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/05 | M10-MFM | Design condition | Hot side temperature | 15.5 degC in, 6.5 degC out | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule | SYSTEM DETAILS states one figure across all five rows
PHX/B/05 | M10-MFM | Design condition | Cold side temperature | 5.5 degC in, 14.4 degC out | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule | SYSTEM DETAILS states one figure across all five rows
PHX/B/05 | M10-MFM | Project | Project | QF Central Library | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/05 | M10-MFM | Project | Contractor | Mercury Engineering Qatar | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/05 | M10-MFM | Project | Consultant | ASTAD Project Management | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/05 | M10-MFM | Construction | Item reference | PHX/B/05-300 KW | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Construction | Duty | 300 | kW | 300 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger Brick 1.4 has no heat-exchanger duty property; coolingCapacity is the Brick term and these exchangers deliver cooling to the secondary loop
PHX/B/05 | M10-MFM | Construction | Number of plates | 19 | n | 19 | unit:UNITLESS |  |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Construction | Plate material | Stainless Steel 316 | [5 empty] | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Construction | Plate thickness | 0.6 | mm | 0.0006 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Construction | Effective heat transfer area | 4.18 | m2 | 4.18 | unit:M2 |  |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Construction | Overall heat transfer coefficient | 3408 / 3613 (dirty / clean) | W/m2 K | 3408 / 3613 (dirty / clean) | unit:W-PER-M2-K | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Construction | Packed dimensions per PHE (L x W x H) | 1145 x 600 x 930 | mm | 1.145 x 0.6 x 0.93 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Construction | Packed weight per PHE | 327 | kg | 327 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Construction | Overall dimensions per PHE (L x W x H) | 720 x 470 x 1084 | mm | 0.72 x 0.47 x 1.084 | unit:M | mm / 1000 |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Construction | Net weight, empty | 297 | kg | 297 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Construction | Net weight, operating | 315 | kg | 315 | unit:KiloGM | unit not used in Dar Cairo |  | reference | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger
PHX/B/05 | M10-MFM | Thermal specification | Customer | Mercury Qatar | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification | Project | AEDUBMY-1304(c)/J-20111017-Mercury-Ctrl Library BP#7A | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification | Item | PHX/B/05-300 KW A | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification | Specification date | 5/21/2012 | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification | Heat exchanged | 300 | kW | 300 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012 | same Brick term as the duty above
PHX/B/05 | M10-MFM | Thermal specification | L.M.T.D. | 23.5 | K | 23.5 | unit:K | temperature difference, not a temperature; unit not used in Dar Cairo |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification | Relative directions of fluids | Countercurrent | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification | Plate material / thickness | ALLOY 316 / 0.60 mm | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification | Pressure vessel code | PED | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification | Flange rating | DIN PN10 | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification | Overall length x width x height | 720 x 470 x 1084 | mm | 0.72 x 0.47 x 1.084 | unit:M | mm / 1000 |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Fluid | Water | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Fluid | Water | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Density | 993.8 | kg/m3 | 993.8 | unit:KiloGM-PER-M3 | unit not used in Dar Cairo |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Density | 1000 | kg/m3 | 1000 | unit:KiloGM-PER-M3 | unit not used in Dar Cairo |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Specific heat capacity | 4.18 | kJ/(kg*K) | 4.18 | unit:KiloJ-PER-KiloGM-K | unit not used in Dar Cairo |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Specific heat capacity | 4.21 | kJ/(kg*K) | 4.21 | unit:KiloJ-PER-KiloGM-K | unit not used in Dar Cairo |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Thermal conductivity | 0.62 | W/(m*K) | 0.62 | unit:W-PER-M-K | unit not used in Dar Cairo |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Thermal conductivity | 0.585 | W/(m*K) | 0.585 | unit:W-PER-M-K | unit not used in Dar Cairo |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Viscosity inlet | 0.546 | cP | 0.546 | unit:CentiP | unit not used in Dar Cairo |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Viscosity inlet | 1.5 | cP | 1.5 | unit:CentiP | unit not used in Dar Cairo |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Viscosity outlet | 1.01 | cP | 1.01 | unit:CentiP | unit not used in Dar Cairo |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Viscosity outlet | 1.16 | cP | 1.16 | unit:CentiP | unit not used in Dar Cairo |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Volume flow rate | 2.4 | l/s | 2.4 | unit:L-PER-SEC |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Volume flow rate | 8 | l/s | 8 | unit:L-PER-SEC |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Inlet temperature | 50 | degC | 50 | unit:DEG_C |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Inlet temperature | 5.5 | degC | 5.5 | unit:DEG_C |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Outlet temperature | 20 | degC | 20 | unit:DEG_C |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Outlet temperature | 14.4 | degC | 14.4 | unit:DEG_C |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Pressure drop | 4.44 | kPa | 4440 | unit:PA | kPa x 1000 |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Pressure drop | 46.9 | kPa | 46900 | unit:PA | kPa x 1000 |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Number of passes | 1 | n | 1 | unit:UNITLESS |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Number of passes | 1 | n | 1 | unit:UNITLESS |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Sealing material | NBRP CLIP-ON | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Sealing material | NBRP CLIP-ON | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Connection diameter | DN100 | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Connection diameter | DN100 | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Nozzle orientation | S1 -> S2 | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Nozzle orientation | S4 <- S3 | [5 empty] | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Design pressure | 10 | bar | 10 | unit:BAR |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Design pressure | 10 | bar | 10 | unit:BAR |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Test pressure | 13 | bar | 13 | unit:BAR |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Test pressure | 13 | bar | 13 | unit:BAR |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - hot side | Design temperature | 120 | degC | 120 | unit:DEG_C |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/05 | M10-MFM | Thermal specification - cold side | Design temperature | 120 | degC | 120 | unit:DEG_C |  |  | reference | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012
PHX/B/01 |  | Data quality | Source reference | The supplied image crops the drawing title block, so the drawing number, sheet number and revision are not recorded. Ask for the sheet reference before handover. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER | Applies to every unit on this schedule
PHX/B/01 |  | Data quality | Schedule scope | The schedule gives dimensions, operating weight and CHW flow rate only. It states no duty, no plate count, no design pressure and no connection sizes - those were not inferred. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER | Applies to every unit on this schedule
PHX/B/01 |  | Data quality | A fifth exchanger | The drawing schedule carries PHX/B/01 to PHX/B/04 only. The Alfa Laval data and the SYSTEM DETAILS schedule both add PHX/B/05, a 300 kW M10-MFM described as the 'Main HEX'. It is included here on that basis. | [6 empty] | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Applies to the heat exchanger set
PHX/B/01 |  | Data quality | Duty split | SYSTEM DETAILS names PHX/B/01 to 03 as duty, PHX/B/04 as standby and PHX/B/05 as the main HEX. The drawing schedule states no duty split. | [6 empty] | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Applies to the heat exchanger set
PHX/B/01 |  | Data quality | Temperature conflict on PHX/B/05 | SYSTEM DETAILS gives one hot-side figure across all five rows - 15.5 degC in, 6.5 degC out. The Alfa Laval specification for the M10-MFM gives 50.0 degC in, 20.0 degC out on the hot side. The cold side agrees at 5.5 in / 14.4 out. Both are recorded against their own source; the conflict is unresolved. | [6 empty] | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Applies to the heat exchanger set
PHX/B/01 |  | Data quality | Weights cross-check | The Alfa Laval net operating weight for the T20-BFG, 4430 kg, and its overall dimensions, 2735 x 780 x 2165 mm, both match the drawing schedule exactly. | [6 empty] | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Applies to the heat exchanger set
PHX/B/01 |  | Data quality | Flow rate is per unit | The drawing schedule's 62.8 / 62.2 l/s is per exchanger. The Alfa Laval sheet gives 2350 kW per T20-BFG. | [6 empty] | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Applies to the heat exchanger set

## Pumps
Pumps
Chilled water pumps CHWP/B/01 to CHWP/B/04 - SCHEDULE OF PUMPS, same drawing as the heat exchanger schedule. The supplied image crops the title block.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Identification | Make | ARMSTRONG |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Identification | Type | HORIZONTAL SPLIT CASE | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Identification | Location | PLANT ROOM-4 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Identification | Model | 4600-STARFLO-125-380H-55KW |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS | Designation ends in 55KW; the schedule states no motor rating of its own
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Identification | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensions and weight | Unit dimension (L x W x H) | 1727x760x760 | mm | 1.727 x 0.76 x 0.76 | unit:M | mm / 1000 |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensions and weight | Weight | 843 | kg | 843 | unit:KiloGM | unit not used in Dar Cairo |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Performance | CHW flow rate | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Identification | Make | ARMSTRONG |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Identification | Type | HORIZONTAL SPLIT CASE | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Identification | Location | PLANT ROOM-4 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Identification | Model | 4600-STARFLO-125-380H-55KW |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS | Designation ends in 55KW; the schedule states no motor rating of its own
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Identification | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensions and weight | Unit dimension (L x W x H) | 1727x760x760 | mm | 1.727 x 0.76 x 0.76 | unit:M | mm / 1000 |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensions and weight | Weight | 843 | kg | 843 | unit:KiloGM | unit not used in Dar Cairo |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Performance | CHW flow rate | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Identification | Make | ARMSTRONG |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Identification | Type | HORIZONTAL SPLIT CASE | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Identification | Location | PLANT ROOM-4 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Identification | Model | 4600-STARFLO-125-380H-55KW |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS | Designation ends in 55KW; the schedule states no motor rating of its own
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Identification | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensions and weight | Unit dimension (L x W x H) | 1727x760x760 | mm | 1.727 x 0.76 x 0.76 | unit:M | mm / 1000 |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensions and weight | Weight | 843 | kg | 843 | unit:KiloGM | unit not used in Dar Cairo |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Performance | CHW flow rate | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Identification | Make | ARMSTRONG |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Identification | Type | HORIZONTAL SPLIT CASE | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Identification | Location | PLANT ROOM-4 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Identification | Model | 4600-STARFLO-125-380H-55KW |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS | Designation ends in 55KW; the schedule states no motor rating of its own
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Identification | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensions and weight | Unit dimension (L x W x H) | 1727x760x760 | mm | 1.727 x 0.76 x 0.76 | unit:M | mm / 1000 |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensions and weight | Weight | 843 | kg | 843 | unit:KiloGM | unit not used in Dar Cairo |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Performance | CHW flow rate | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Identification | Duty or standby | Duty Pump | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.1 - Chilled Water Pumps Equipment Schedule
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Identification | Alternate reference | CHWP-B-01 | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.1 - Chilled Water Pumps Equipment Schedule | Dash form used by SYSTEM DETAILS; the drawing schedule writes slashes
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Submittal | Project number | 301358.1.3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Submittal | Project name | Central Library - Qatar | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Submittal | Reference | TENDER301358.1.3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Submittal | Project location | DOHA | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Submittal | Representative | PETROFAC QATAR W.L.L. | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Submittal | Submitted by | M Aashik | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dated 8/8/2012
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Submittal | Type | HORZ | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Horizontal
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Tag num | BP#7A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | The project/package reference, not a pump tag
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Service | Chilled Water Pump | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Quantity | 4 | n | 4 | unit:UNITLESS |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Submittal covers all four pumps
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Duty flow | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Duty head | 460 | kPa | 460000 | unit:PA | kPa x 1000 | para:ratedHead | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dar Cairo writes ratedHead in metres; this value is kPa
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Pipe orientation | Parallel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Pump run quantity | 3 | n | 3 | unit:UNITLESS |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Three of the four run; the fourth is standby
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Suction pressure | 0 | psig | 0 | unit:PA | psi x 6894.757; the submittal states it as gauge pressure |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Fluid | Water | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Operating temperature | 15.55 | degC | 15.55 | unit:DEG_C |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Viscosity | 31 SSU | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Saybolt Universal Seconds - no QUDT unit
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Specific gravity | 1 |  | 1 | unit:UNITLESS | dimensionless ratio |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Suction | 6 | in | 0.1524 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Discharge | 5 | in | 0.127 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor supplier | WEG | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | the motor maker; rec:manufacturedBy on the motor sub-entity would need that entity first
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor size | 55 | kW | 55 | unit:KiloW |  | brick:ratedPowerInput | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor frame number | 250M | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor enclosure | TEFC | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Totally enclosed fan cooled
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Drive motor | Power supply | 400/3/50 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor efficiency class | IE3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Drive motor | Insulation class | Class F Insulation | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Drive motor | Inverter motor type | [none] | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Stated as none on the submittal
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor speed | 1500 | rpm | 1500 | unit:RPM |  | para:ratedSpeed | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Manufacturer | Armstrong | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | the seal maker, not the pump's manufacturer
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Seal type | Inside Unbalanced | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Manufacturer code | 21A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Rotating face | Resin Bonded Carbon | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Stationary seat | Silicon Carbide | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Secondary seal | EPDM | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Springs | Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Rotating hardware | Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Fluid type | Non-Potable Fluid | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Seal | A5: Armstrong 21A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Construction | CI/GM | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Cast iron / gunmetal
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Rating | PN-16 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Impeller | Gunmetal Bronze (BS1400 LG2C) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Shaft sleeve | SS (BS970 304) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Flexible couplings | Standard | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump shaft | SS (BS970 416) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Flush line | Braided Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Casing gasket | Velotherm (Non-Asbestos fiber) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Bearings | Anti-Friction Grease Lubricated | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump casing | Cast Iron | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump suction | Right-hand when viewed from Drive End | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Suction/discharge flange | BS EN 1092-2:1997 PN16/PN16 Cast Iron | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Size | 125-380H | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Materials of construction | Hydrostatic test | Pump casings are hydrostatically tested to 150% of maximum pump working pressure | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | Configuration code | 4600125-380HPN16250MTEFC | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | D | 15 | in | 0.381 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout; the submittal does not name the feature
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | HA | 19 | in | 0.4826 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | HB | 64 | in | 1.6256 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | HC | 68.06 | in | 1.7287 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | HD | 16 | in | 0.4064 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | HE | 8.5 | in | 0.2159 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | HF | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | HG | 6 | in | 0.1524 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | HL | 13.5 | in | 0.3429 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | HM | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | HO | 30.03 | in | 0.76276 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | HP | 2 | in | 0.0508 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | S | 15 | in | 0.381 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | SD | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Dimensional data | Weight | 1874 | lb | 850.032 | unit:KiloGM | lb x 0.45359237; unit not used in Dar Cairo |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Identification | Duty or standby | Duty Pump | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.1 - Chilled Water Pumps Equipment Schedule
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Identification | Alternate reference | CHWP-B-02 | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.1 - Chilled Water Pumps Equipment Schedule | Dash form used by SYSTEM DETAILS; the drawing schedule writes slashes
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Submittal | Project number | 301358.1.3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Submittal | Project name | Central Library - Qatar | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Submittal | Reference | TENDER301358.1.3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Submittal | Project location | DOHA | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Submittal | Representative | PETROFAC QATAR W.L.L. | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Submittal | Submitted by | M Aashik | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dated 8/8/2012
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Submittal | Type | HORZ | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Horizontal
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Tag num | BP#7A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | The project/package reference, not a pump tag
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Service | Chilled Water Pump | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Quantity | 4 | n | 4 | unit:UNITLESS |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Submittal covers all four pumps
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Duty flow | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Duty head | 460 | kPa | 460000 | unit:PA | kPa x 1000 | para:ratedHead | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dar Cairo writes ratedHead in metres; this value is kPa
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Pipe orientation | Parallel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Pump run quantity | 3 | n | 3 | unit:UNITLESS |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Three of the four run; the fourth is standby
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Suction pressure | 0 | psig | 0 | unit:PA | psi x 6894.757; the submittal states it as gauge pressure |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Fluid | Water | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Operating temperature | 15.55 | degC | 15.55 | unit:DEG_C |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Viscosity | 31 SSU | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Saybolt Universal Seconds - no QUDT unit
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Specific gravity | 1 |  | 1 | unit:UNITLESS | dimensionless ratio |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Suction | 6 | in | 0.1524 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Discharge | 5 | in | 0.127 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor supplier | WEG | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | the motor maker; rec:manufacturedBy on the motor sub-entity would need that entity first
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor size | 55 | kW | 55 | unit:KiloW |  | brick:ratedPowerInput | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor frame number | 250M | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor enclosure | TEFC | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Totally enclosed fan cooled
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Drive motor | Power supply | 400/3/50 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor efficiency class | IE3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Drive motor | Insulation class | Class F Insulation | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Drive motor | Inverter motor type | [none] | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Stated as none on the submittal
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor speed | 1500 | rpm | 1500 | unit:RPM |  | para:ratedSpeed | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Manufacturer | Armstrong | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | the seal maker, not the pump's manufacturer
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Seal type | Inside Unbalanced | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Manufacturer code | 21A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Rotating face | Resin Bonded Carbon | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Stationary seat | Silicon Carbide | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Secondary seal | EPDM | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Springs | Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Rotating hardware | Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Fluid type | Non-Potable Fluid | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Seal | A5: Armstrong 21A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Construction | CI/GM | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Cast iron / gunmetal
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Rating | PN-16 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Impeller | Gunmetal Bronze (BS1400 LG2C) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Shaft sleeve | SS (BS970 304) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Flexible couplings | Standard | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump shaft | SS (BS970 416) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Flush line | Braided Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Casing gasket | Velotherm (Non-Asbestos fiber) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Bearings | Anti-Friction Grease Lubricated | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump casing | Cast Iron | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump suction | Right-hand when viewed from Drive End | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Suction/discharge flange | BS EN 1092-2:1997 PN16/PN16 Cast Iron | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Size | 125-380H | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Materials of construction | Hydrostatic test | Pump casings are hydrostatically tested to 150% of maximum pump working pressure | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | Configuration code | 4600125-380HPN16250MTEFC | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | D | 15 | in | 0.381 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout; the submittal does not name the feature
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | HA | 19 | in | 0.4826 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | HB | 64 | in | 1.6256 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | HC | 68.06 | in | 1.7287 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | HD | 16 | in | 0.4064 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | HE | 8.5 | in | 0.2159 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | HF | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | HG | 6 | in | 0.1524 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | HL | 13.5 | in | 0.3429 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | HM | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | HO | 30.03 | in | 0.76276 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | HP | 2 | in | 0.0508 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | S | 15 | in | 0.381 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | SD | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Dimensional data | Weight | 1874 | lb | 850.032 | unit:KiloGM | lb x 0.45359237; unit not used in Dar Cairo |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Identification | Duty or standby | Duty Pump | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.1 - Chilled Water Pumps Equipment Schedule
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Identification | Alternate reference | CHWP-B-03 | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.1 - Chilled Water Pumps Equipment Schedule | Dash form used by SYSTEM DETAILS; the drawing schedule writes slashes
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Submittal | Project number | 301358.1.3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Submittal | Project name | Central Library - Qatar | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Submittal | Reference | TENDER301358.1.3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Submittal | Project location | DOHA | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Submittal | Representative | PETROFAC QATAR W.L.L. | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Submittal | Submitted by | M Aashik | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dated 8/8/2012
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Submittal | Type | HORZ | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Horizontal
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Tag num | BP#7A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | The project/package reference, not a pump tag
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Service | Chilled Water Pump | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Quantity | 4 | n | 4 | unit:UNITLESS |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Submittal covers all four pumps
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Duty flow | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Duty head | 460 | kPa | 460000 | unit:PA | kPa x 1000 | para:ratedHead | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dar Cairo writes ratedHead in metres; this value is kPa
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Pipe orientation | Parallel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Pump run quantity | 3 | n | 3 | unit:UNITLESS |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Three of the four run; the fourth is standby
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Suction pressure | 0 | psig | 0 | unit:PA | psi x 6894.757; the submittal states it as gauge pressure |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Fluid | Water | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Operating temperature | 15.55 | degC | 15.55 | unit:DEG_C |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Viscosity | 31 SSU | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Saybolt Universal Seconds - no QUDT unit
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Specific gravity | 1 |  | 1 | unit:UNITLESS | dimensionless ratio |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Suction | 6 | in | 0.1524 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Discharge | 5 | in | 0.127 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor supplier | WEG | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | the motor maker; rec:manufacturedBy on the motor sub-entity would need that entity first
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor size | 55 | kW | 55 | unit:KiloW |  | brick:ratedPowerInput | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor frame number | 250M | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor enclosure | TEFC | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Totally enclosed fan cooled
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Drive motor | Power supply | 400/3/50 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor efficiency class | IE3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Drive motor | Insulation class | Class F Insulation | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Drive motor | Inverter motor type | [none] | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Stated as none on the submittal
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor speed | 1500 | rpm | 1500 | unit:RPM |  | para:ratedSpeed | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Manufacturer | Armstrong | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | the seal maker, not the pump's manufacturer
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Seal type | Inside Unbalanced | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Manufacturer code | 21A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Rotating face | Resin Bonded Carbon | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Stationary seat | Silicon Carbide | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Secondary seal | EPDM | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Springs | Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Rotating hardware | Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Fluid type | Non-Potable Fluid | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Seal | A5: Armstrong 21A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Construction | CI/GM | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Cast iron / gunmetal
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Rating | PN-16 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Impeller | Gunmetal Bronze (BS1400 LG2C) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Shaft sleeve | SS (BS970 304) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Flexible couplings | Standard | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump shaft | SS (BS970 416) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Flush line | Braided Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Casing gasket | Velotherm (Non-Asbestos fiber) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Bearings | Anti-Friction Grease Lubricated | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump casing | Cast Iron | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump suction | Right-hand when viewed from Drive End | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Suction/discharge flange | BS EN 1092-2:1997 PN16/PN16 Cast Iron | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Size | 125-380H | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Materials of construction | Hydrostatic test | Pump casings are hydrostatically tested to 150% of maximum pump working pressure | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | Configuration code | 4600125-380HPN16250MTEFC | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | D | 15 | in | 0.381 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout; the submittal does not name the feature
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | HA | 19 | in | 0.4826 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | HB | 64 | in | 1.6256 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | HC | 68.06 | in | 1.7287 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | HD | 16 | in | 0.4064 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | HE | 8.5 | in | 0.2159 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | HF | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | HG | 6 | in | 0.1524 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | HL | 13.5 | in | 0.3429 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | HM | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | HO | 30.03 | in | 0.76276 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | HP | 2 | in | 0.0508 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | S | 15 | in | 0.381 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | SD | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Dimensional data | Weight | 1874 | lb | 850.032 | unit:KiloGM | lb x 0.45359237; unit not used in Dar Cairo |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Identification | Duty or standby | Standby Pump | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.1 - Chilled Water Pumps Equipment Schedule
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Identification | Alternate reference | CHWP-B-04 | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.1 - Chilled Water Pumps Equipment Schedule | Dash form used by SYSTEM DETAILS; the drawing schedule writes slashes
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Submittal | Project number | 301358.1.3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Submittal | Project name | Central Library - Qatar | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Submittal | Reference | TENDER301358.1.3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Submittal | Project location | DOHA | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Submittal | Representative | PETROFAC QATAR W.L.L. | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Submittal | Submitted by | M Aashik | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dated 8/8/2012
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Submittal | Type | HORZ | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Horizontal
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Tag num | BP#7A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | The project/package reference, not a pump tag
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Service | Chilled Water Pump | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Quantity | 4 | n | 4 | unit:UNITLESS |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Submittal covers all four pumps
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Duty flow | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Duty head | 460 | kPa | 460000 | unit:PA | kPa x 1000 | para:ratedHead | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dar Cairo writes ratedHead in metres; this value is kPa
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Pipe orientation | Parallel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Pump run quantity | 3 | n | 3 | unit:UNITLESS |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Three of the four run; the fourth is standby
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Suction pressure | 0 | psig | 0 | unit:PA | psi x 6894.757; the submittal states it as gauge pressure |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Fluid | Water | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Operating temperature | 15.55 | degC | 15.55 | unit:DEG_C |  |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Viscosity | 31 SSU | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Saybolt Universal Seconds - no QUDT unit
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Specific gravity | 1 |  | 1 | unit:UNITLESS | dimensionless ratio |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Suction | 6 | in | 0.1524 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Discharge | 5 | in | 0.127 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor supplier | WEG | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | the motor maker; rec:manufacturedBy on the motor sub-entity would need that entity first
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor size | 55 | kW | 55 | unit:KiloW |  | brick:ratedPowerInput | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor frame number | 250M | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor enclosure | TEFC | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Totally enclosed fan cooled
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Drive motor | Power supply | 400/3/50 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor efficiency class | IE3 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Drive motor | Insulation class | Class F Insulation | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Drive motor | Inverter motor type | [none] | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Stated as none on the submittal
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor speed | 1500 | rpm | 1500 | unit:RPM |  | para:ratedSpeed | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Manufacturer | Armstrong | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | the seal maker, not the pump's manufacturer
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Seal type | Inside Unbalanced | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Manufacturer code | 21A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Rotating face | Resin Bonded Carbon | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Stationary seat | Silicon Carbide | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Secondary seal | EPDM | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Springs | Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Rotating hardware | Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Fluid type | Non-Potable Fluid | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Mechanical seal | Seal | A5: Armstrong 21A | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Construction | CI/GM | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Cast iron / gunmetal
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Rating | PN-16 | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Impeller | Gunmetal Bronze (BS1400 LG2C) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Shaft sleeve | SS (BS970 304) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Flexible couplings | Standard | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump shaft | SS (BS970 416) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Flush line | Braided Stainless Steel | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Casing gasket | Velotherm (Non-Asbestos fiber) | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Bearings | Anti-Friction Grease Lubricated | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump casing | Cast Iron | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Pump suction | Right-hand when viewed from Drive End | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Suction/discharge flange | BS EN 1092-2:1997 PN16/PN16 Cast Iron | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Size | 125-380H | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Materials of construction | Hydrostatic test | Pump casings are hydrostatically tested to 150% of maximum pump working pressure | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | Configuration code | 4600125-380HPN16250MTEFC | [5 empty] | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | D | 15 | in | 0.381 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout; the submittal does not name the feature
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | HA | 19 | in | 0.4826 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | HB | 64 | in | 1.6256 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | HC | 68.06 | in | 1.7287 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | HD | 16 | in | 0.4064 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | HE | 8.5 | in | 0.2159 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | HF | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | HG | 6 | in | 0.1524 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | HL | 13.5 | in | 0.3429 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | HM | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | HO | 30.03 | in | 0.76276 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | HP | 2 | in | 0.0508 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | S | 15 | in | 0.381 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | SD | 30 | in | 0.762 | unit:M | in x 0.0254 |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Drawing callout
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Dimensional data | Weight | 1874 | lb | 850.032 | unit:KiloGM | lb x 0.45359237; unit not used in Dar Cairo |  | reference | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 |  | Data quality | Source reference | The supplied image crops the drawing title block, so the drawing number, sheet number and revision are not recorded. Ask for the sheet reference before handover. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS | Applies to every unit on this schedule
CHWP/B/01 |  | Data quality | Motor rating | The model designation ends in '55KW', which reads as a 55 kW motor. The schedule states no motor rating of its own, so no rated-power property was created from it. Confirm against the pump submittal before writing brick:ratedPowerInput. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS | Applies to every unit on this schedule
CHWP/B/01 |  | Data quality | Schedule scope | The schedule gives no head, no speed, no efficiency and no electrical data - those were not inferred. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS | Applies to every unit on this schedule
CHWP/B/01 |  | Data quality | Submittal dimensions are imperial | The dimensional block is headed '(in, lb) NOT for CONSTRUCTION'. Values are inches and pounds and are converted on that basis. The block is marked not for construction, so do not build to it. | [6 empty] | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Applies to every unit on this submittal
CHWP/B/01 |  | Data quality | Weight disagreement | The submittal gives 1874 lb, which is 850 kg. The drawing schedule gives 843 kg. A 7 kg difference - probably a different scope of supply (baseplate, coupling guard) rather than an error, but neither document says. | [6 empty] | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Applies to every unit on this submittal
CHWP/B/01 |  | Data quality | Dimension callouts are unlabelled | D, HA, HB, HC and the rest are letters keyed to the outline drawing. The submittal does not say which feature each measures, so they are recorded as callouts rather than named dimensions. | [6 empty] | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Applies to every unit on this submittal
CHWP/B/01 |  | Data quality | Duty and standby | The SYSTEM DETAILS schedule names CHWP-B-01 to 03 as duty pumps and CHWP-B-04 as the standby. That matches the submittal's 'Pump Run Qty 3' against 'Qty 4'. | [6 empty] | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Applies to every unit on this submittal
CHWP/B/01 |  | Data quality | Alternate tag shape | The SYSTEM DETAILS schedule writes the tags with dashes (CHWP-B-01) where the drawing schedule writes slashes (CHWP/B/01). The slash form is used as the tag here because it matches every other reference in this workbook; the dash form is recorded against each pump as an alternate reference. Confirm which the BMS uses. | [6 empty] | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Applies to every unit on this submittal
CHWP/B/01 |  | Data quality | Tag Num on the submittal | The submittal's 'Tag Num' field reads BP#7A, which is the Education City building package reference, not a pump tag. It does not identify an individual pump. | [6 empty] | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Applies to every unit on this submittal

## Exhaust Fans
Exhaust Fans
39 exhaust fans from the supplied schedule spreadsheet. The sheet carries model, manufacturer and air flow only - no location, motor rating or static pressure. Two identifier shapes are in use; both were kept as written.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
EF/2/01 | S6-315 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r2
EF/2/01 | S6-315 | Identification | Model | S6-315 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r2
EF/2/01 | S6-315 | Air | Air flow | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r2 | source writes '200 l/s' these are exhaust fans
KEF_B020 |  | Data quality | Model and manufacturer | not stated in the source sheet | [6 empty] | Book1.xlsx | Sheet1 r3 | Left out rather than filled with a typical value
KEF_B020 |  | Air | Air flow | 300 | l/s | 300 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r3 | these are exhaust fans
TEF_B01A | AXT80P-413A | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r4
TEF_B01A | AXT80P-413A | Identification | Model | AXT80P-413A |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r4
TEF_B01A | AXT80P-413A | Air | Air flow | 1538 | l/s | 1538 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r4 | these are exhaust fans
TEF_B01B | AXT80P-413A | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r5
TEF_B01B | AXT80P-413A | Identification | Model | AXT80P-413A |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r5
TEF_B01B | AXT80P-413A | Air | Air flow | 1538 | l/s | 1538 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r5 | these are exhaust fans
TEF_B02A | AXT71P-413A | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r6
TEF_B02A | AXT71P-413A | Identification | Model | AXT71P-413A |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r6
TEF_B02A | AXT71P-413A | Air | Air flow | 970 | l/s | 970 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r6 | these are exhaust fans
TEF_B02B | AXT71P-413A | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r7
TEF_B02B | AXT71P-413A | Identification | Model | AXT71P-413A |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r7
TEF_B02B | AXT71P-413A | Air | Air flow | 970 | l/s | 970 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r7 | these are exhaust fans
TEF_B03A | AXT35M-211A | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r8
TEF_B03A | AXT35M-211A | Identification | Model | AXT35M-211A |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r8
TEF_B03A | AXT35M-211A | Air | Air flow | 400 | l/s | 400 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r8 | these are exhaust fans
TEF_B03B | AXT35M-211A | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r9
TEF_B03B | AXT35M-211A | Identification | Model | AXT35M-211A |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r9
TEF_B03B | AXT35M-211A | Air | Air flow | 400 | l/s | 400 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r9 | these are exhaust fans
EF/RP/1 | AX71P-453A1 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r10
EF/RP/1 | AX71P-453A1 | Identification | Model | AX71P-453A1 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r10
EF/RP/1 | AX71P-453A1 | Air | Air flow | 5000 | l/s | 5000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r10 | these are exhaust fans
EF/RP/2 | AX71P-453A1 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r11
EF/RP/2 | AX71P-453A1 | Identification | Model | AX71P-453A1 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r11
EF/RP/2 | AX71P-453A1 | Air | Air flow | 5000 | l/s | 5000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r11 | these are exhaust fans
EF/RP/3 | AX71P-453A1 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r12
EF/RP/3 | AX71P-453A1 | Identification | Model | AX71P-453A1 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r12
EF/RP/3 | AX71P-453A1 | Air | Air flow | 5000 | l/s | 5000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r12 | these are exhaust fans
TEF_101C | S - Squrbo | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r13
TEF_101C | S - Squrbo | Identification | Model | S - Squrbo |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r13
TEF_101C | S - Squrbo | Data quality | Air flow | not stated in the source sheet | [6 empty] | Book1.xlsx | Sheet1 r13 | Left out rather than filled with a typical value
TEF_102C | S - Squrbo | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r14
TEF_102C | S - Squrbo | Identification | Model | S - Squrbo |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r14
TEF_102C | S - Squrbo | Data quality | Air flow | not stated in the source sheet | [6 empty] | Book1.xlsx | Sheet1 r14 | Left out rather than filled with a typical value
EF/BV/01 | AX719-41AKZ+0WE | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r15
EF/BV/01 | AX719-41AKZ+0WE | Identification | Model | AX719-41AKZ+0WE |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r15
EF/BV/01 | AX719-41AKZ+0WE | Air | Air flow | 330 | l/s | 330 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r15 | source writes '330L/S' these are exhaust fans
EF/BV/02 | AX719-41AKZ+0WE | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r16
EF/BV/02 | AX719-41AKZ+0WE | Identification | Model | AX719-41AKZ+0WE |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r16
EF/BV/02 | AX719-41AKZ+0WE | Air | Air flow | 330 | l/s | 330 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r16 | source writes '330L/S' these are exhaust fans
KEF_B019 |  | Data quality | Model and manufacturer | not stated in the source sheet | [6 empty] | Book1.xlsx | Sheet1 r17 | Left out rather than filled with a typical value
KEF_B019 |  | Air | Air flow | 1800 | l/s | 1800 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r17 | these are exhaust fans
KEF_101 |  | Data quality | Model and manufacturer | not stated in the source sheet | [6 empty] | Book1.xlsx | Sheet1 r18 | Left out rather than filled with a typical value
KEF_101 |  | Air | Air flow | 1500 | l/s | 1500 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r18 | these are exhaust fans
EF/RP/4 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r19
EF/RP/4 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r19
EF/RP/4 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r19 | these are exhaust fans
EF/RP/5 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r20
EF/RP/5 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r20
EF/RP/5 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r20 | these are exhaust fans
EF/RP/6 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r21
EF/RP/6 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r21
EF/RP/6 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r21 | these are exhaust fans
EF/RP/7 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r22
EF/RP/7 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r22
EF/RP/7 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r22 | these are exhaust fans
EF/RP/8 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r23
EF/RP/8 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r23
EF/RP/8 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r23 | these are exhaust fans
EF/RP/9 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r24
EF/RP/9 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r24
EF/RP/9 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r24 | these are exhaust fans
EF/RP/10 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r25
EF/RP/10 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r25
EF/RP/10 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r25 | these are exhaust fans
EF/RP/11 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r26
EF/RP/11 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r26
EF/RP/11 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r26 | these are exhaust fans
EF/RP/12 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r27
EF/RP/12 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r27
EF/RP/12 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r27 | these are exhaust fans
EF/B/4 | SQFA41-1 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r28
EF/B/4 | SQFA41-1 | Identification | Model | SQFA41-1 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r28
EF/B/4 | SQFA41-1 | Air | Air flow | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r28 | these are exhaust fans
EF/B/5 | NALAF-150 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r29
EF/B/5 | NALAF-150 | Identification | Model | NALAF-150 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r29
EF/B/5 | NALAF-150 | Air | Air flow | 70 | l/s | 70 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r29 | these are exhaust fans
EF/B/6 | AX63F-413AFG1 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r30
EF/B/6 | AX63F-413AFG1 | Identification | Model | AX63F-413AFG1 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r30
EF/B/6 | AX63F-413AFG1 | Air | Air flow | 250 | l/s | 250 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r30 | these are exhaust fans
EF/B/7 | AX100CX-4H3A7I | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r31
EF/B/7 | AX100CX-4H3A7I | Identification | Model | AX100CX-4H3A7I |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r31
EF/B/7 | AX100CX-4H3A7I | Air | Air flow | 11000 | l/s | 11000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r31 | these are exhaust fans
EF/B/8 | AX100CX-4H3A7I | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r32
EF/B/8 | AX100CX-4H3A7I | Identification | Model | AX100CX-4H3A7I |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r32
EF/B/8 | AX100CX-4H3A7I | Air | Air flow | 11000 | l/s | 11000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r32 | these are exhaust fans
EF/B/9 | AX80P-423A | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r33
EF/B/9 | AX80P-423A | Identification | Model | AX80P-423A |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r33
EF/B/9 | AX80P-423A | Air | Air flow | 2800 | l/s | 2800 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r33 | these are exhaust fans
EF/B/10 | AX40I-411A | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r34
EF/B/10 | AX40I-411A | Identification | Model | AX40I-411A |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r34
EF/B/10 | AX40I-411A | Air | Air flow | 475 | l/s | 475 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r34 | these are exhaust fans
EF/B/11 | EZPLATES 315-41 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r35
EF/B/11 | EZPLATES 315-41 | Identification | Model | EZPLATES 315-41 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r35
EF/B/11 | EZPLATES 315-41 | Air | Air flow | 90 | l/s | 90 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r35 | these are exhaust fans
EF/B/12 | S6-315 | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r36
EF/B/12 | S6-315 | Identification | Model | S6-315 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r36
EF/B/12 | S6-315 | Air | Air flow | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r36 | these are exhaust fans
EF/B/13 | AX63F-411A | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r37
EF/B/13 | AX63F-411A | Identification | Model | AX63F-411A |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r37
EF/B/13 | AX63F-411A | Air | Air flow | 810 | l/s | 810 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r37 | source writes '810L/S' these are exhaust fans
EF/B/14 | AX63D-411A | Identification | Manufacturer | NUAIRE |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r38
EF/B/14 | AX63D-411A | Identification | Model | AX63D-411A |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r38
EF/B/14 | AX63D-411A | Air | Air flow | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r38 | these are exhaust fans
EF/B/15 | Cmveco 315/315 | Identification | Manufacturer | COLASIT |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r39
EF/B/15 | Cmveco 315/315 | Identification | Model | Cmveco 315/315 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r39
EF/B/15 | Cmveco 315/315 | Data quality | Air flow | not stated in the source sheet | [6 empty] | Book1.xlsx | Sheet1 r39 | Left out rather than filled with a typical value
EF/B/16 | Cmveco 125/125 | Identification | Manufacturer | COLASIT |  |  |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r40
EF/B/16 | Cmveco 125/125 | Identification | Model | Cmveco 125/125 |  |  |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r40
EF/B/16 | Cmveco 125/125 | Data quality | Air flow | not stated in the source sheet | [6 empty] | Book1.xlsx | Sheet1 r40 | Left out rather than filled with a typical value
EF/2/01 |  | Data quality | Identifier shapes | Two families are in use and neither is a typo: 28 tags are slash separated (EF/B/nn, EF/RP/n, EF/BV/nn, EF/2/01) and 11 are underscore separated (TEF_B01A, KEF_B020, TEF_101C, KEF_101). Tags are the BMS join key, so both were kept exactly as written. Confirm which shape the BMS actually uses before the ontology is built. | [6 empty] | Book1.xlsx | Sheet1 | Applies to the whole schedule
EF/2/01 |  | Data quality | Whitespace | 'EF/2/01 ' carries a trailing space in the source. Stripped, per the rule that whitespace is the only thing changed on a supplied identifier. | [6 empty] | Book1.xlsx | Sheet1 | Applies to the whole schedule
EF/2/01 |  | Data quality | Numbering gap | EF/B numbering runs 4 to 16; there is no EF/B/1, EF/B/2 or EF/B/3 in the sheet. Either they are scheduled elsewhere or the list is partial - worth confirming. | [6 empty] | Book1.xlsx | Sheet1 | Applies to the whole schedule
EF/2/01 |  | Data quality | Air flow spelling | The source writes the unit as both 'l/s' and 'L/S', and sometimes with no space ('330L/S'). All are litres per second; the value was parsed and the unit normalised. | [6 empty] | Book1.xlsx | Sheet1 | Applies to the whole schedule
EF/2/01 |  | Data quality | Missing data | KEF_B020, KEF_B019 and KEF_101 have no model and no manufacturer. TEF_101C, TEF_102C, EF/B/15 and EF/B/16 have no air flow. Those properties are left out rather than filled with a typical value. | [6 empty] | Book1.xlsx | Sheet1 | Applies to the whole schedule

## Generators
Generators
One standby diesel generator from the GENERATOR ASSET LIST, a multi-equipment asset register. The row cropped off below it belongs to different equipment, so this is the complete record for this machine.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
GENERATOR SET | 4012-46TAG3A | Asset register | Location info | QNL | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Asset register | Main category | STANDBY GENERATOR | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Asset register | Sub category | DIESEL GENERATOR | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Identification | Manufacturer | CTM |  |  |  |  | rec:manufacturedBy | core | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Identification | Model number | 4012-46TAG3A |  |  |  |  | rec:modelNumber | core | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Identification | Serial number | 11 211 038571-16 | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Asset register | Equipment name | GENERATOR SET | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Location | Building name | QATAR NATIONAL LIBRARY | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Location | Floor | LOWER LEVEL | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Location | Room no. | B080 | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Maintenance | Date installed | Jun-12 |  |  |  |  | rec:installationDate | core | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Asset register | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Maintenance | PM procedure description | REFER O&M | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Maintenance | Procedure document | REFER O&M | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Warranty | Warranty | YES | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Warranty | Warranty expires | 12 MONTHS FROM COC | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Warranty | Warranty notes | 12 MONTHS FROM DATE OF COMMISSIONING | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Maintenance | Recommended spare parts | REFER O&M | [5 empty] | reference | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET |  | Data quality | One generator, not a truncated list | The image cuts off partway through the row below, but the user has confirmed that row belongs to a different piece of equipment. The asset list is a multi-equipment register rather than a generator inventory, so the single row transcribed here is the complete record for this generator. | [6 empty] | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET |  | Data quality | Asset tag is not unique | The ASSET TAG NUMBER column holds the words 'GENERATOR SET', the same text as the EQUIPMENT NAME column. It does not identify one machine, so it cannot serve as the join key to the BMS the way every other tag in this workbook does. Ask for the real asset tag. | [6 empty] | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET |  | Data quality | Serial number | The serial number 11 211 038571-16 is specific to one machine, so this row does describe a single generator even though its tag does not name one. | [6 empty] | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET |  | Data quality | Model | CTM 4012-46TAG3A is a Perkins 4012-46TAG3A engine badged by CTM. The list states the manufacturer as CTM; the engine builder was not inferred into the data. | [6 empty] | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET |  | Data quality | Date installed | Given as 'Jun-12' - month and year, no day. | [6 empty] | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET |  | Data quality | Deferred fields | PM procedure, procedure document and recommended spare parts all read 'REFER O&M'. The O&M manual is where those live; nothing was invented for them. | [6 empty] | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST

## Pressurization Unit
Pressurization Unit
PU/B/01 - SCHEDULE OF PRESSURIZATION UNIT, same drawing as the heat exchanger and pump schedules. The supplied image crops the title block.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
PU/B/01 | 3750 2 EM-S | Identification | Make | ARMSTRONG |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PRESSURIZATION UNIT
PU/B/01 | 3750 2 EM-S | Identification | Model | 3750 2 EM-S |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PRESSURIZATION UNIT
PU/B/01 | 3750 2 EM-S | Identification | Location | PLANT ROOM-4 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PRESSURIZATION UNIT
PU/B/01 | 3750 2 EM-S | Identification | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PRESSURIZATION UNIT
PU/B/01 | 3750 2 EM-S | Performance | System volume (as printed) | WITH 10BAR PRESSURE & 1000L TANK | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PRESSURIZATION UNIT | Column is headed SYSTEM VOLUME but holds a pressure and a tank size
PU/B/01 |  | Identification | Alternate reference | PRO1 | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule | Tag used by SYSTEM DETAILS; the drawing schedule writes PU/B/01
PU/B/01 |  | Expansion tank | Make | Armstrong |  |  |  |  | rec:manufacturedBy | core | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 |  | Expansion tank | Model | Reflex DE10 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 |  | Expansion tank | Capacity | 1000 | litre | 1000 | unit:L | unit not used in Dar Cairo | para:Rated_Tank_Level | core | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule | chosen by the user. Note brick:volume exists in Brick 1.4 and by the ladder would outrank a para: term for a tank volume - reversible in one line if the team prefers it
PU/B/01 |  | Expansion tank | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 |  | Pressurisation unit | Make | Armstrong |  |  |  |  | rec:manufacturedBy | core | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 |  | Pressurisation unit | Model | 3750 2 EM-S |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 |  | Pressurisation unit | Capacity | 10 | bar | 10 | unit:BAR |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 |  | Pressurisation unit | Quantity | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 |  | Data quality | Source reference | The supplied image crops the drawing title block, so the drawing number, sheet number and revision are not recorded. Ask for the sheet reference before handover. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PRESSURIZATION UNIT
PU/B/01 |  | Data quality | Column mismatch | The column is headed SYSTEM VOLUME but holds the text 'WITH 10BAR PRESSURE & 1000L TANK' - a pressure and a tank size, not a system volume. Recorded verbatim; the system volume the header asks for is not stated anywhere on the schedule. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PRESSURIZATION UNIT
PU/B/01 |  | Data quality | Column mismatch resolved | The drawing schedule's SYSTEM VOLUME cell reads 'WITH 10BAR PRESSURE & 1000L TANK'. SYSTEM DETAILS Table 3.2 explains it: the assembly is an Armstrong 3750 2 EM-S pressurisation unit rated 10 bar plus a Reflex DE10 expansion tank of 1000 litre. Those are now recorded as two components. The system volume the column header asks for is still not stated on either document. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 |  | Data quality | Alternate tag | SYSTEM DETAILS tags the assembly PRO1 where the drawing schedule tags it PU/B/01. The drawing form is used here because it matches the rest of the workbook; PRO1 is recorded as an alternate reference. Confirm which the BMS uses. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule

## CAV Units
CAV Units
Constant air volume boxes across six schedules on level 1F and the basement. Air flow is stated per box. A range reference is expanded into its individual boxes only when the box count matches the stated quantity.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
CAV/1F/S11/001 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/001 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/001 | NBOQOB250 | Air | Air flow (per box) | 300 | l/s | 300 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/002 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/002 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/002 | NBOQOB200 | Air | Air flow (per box) | 175 | l/s | 175 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/004 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/004 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/004 | NBOQOB200 | Air | Air flow (per box) | 190 | l/s | 190 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/006 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/006 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/006 | NBOQOB160 | Air | Air flow (per box) | 165 | l/s | 165 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/006 | NBOQOB160 | Provenance | Scheduled as | CAV/1F/S11/006 TO 007 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11) | One schedule line of QTY 2, split to one row per box
CAV/1F/S11/007 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/007 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/007 | NBOQOB160 | Air | Air flow (per box) | 165 | l/s | 165 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/007 | NBOQOB160 | Provenance | Scheduled as | CAV/1F/S11/006 TO 007 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11) | One schedule line of QTY 2, split to one row per box
CAV/1F/S11/008 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/008 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/008 | NBOQOB200 | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/008 | NBOQOB200 | Provenance | Scheduled as | CAV/1F/S11/008 TO 009 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11) | One schedule line of QTY 2, split to one row per box
CAV/1F/S11/009 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/009 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/009 | NBOQOB200 | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/009 | NBOQOB200 | Provenance | Scheduled as | CAV/1F/S11/008 TO 009 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11) | One schedule line of QTY 2, split to one row per box
CAV/1F/S15/002 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/002 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/002 | NBOQOB160 | Air | Air flow (per box) | 151 | l/s | 151 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/004 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/004 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/004 | NBOQOB160 | Air | Air flow (per box) | 225 | l/s | 225 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/005 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/005 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/005 | NBOQOB200 | Air | Air flow (per box) | 185 | l/s | 185 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/006 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/006 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/006 | NBOQOB200 | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/007 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/007 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/007 | NBOQOB200 | Air | Air flow (per box) | 315 | l/s | 315 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S11/005 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S11/005 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S11/005 | NBOQOB200 | Air | Air flow (per box) | 190 | l/s | 190 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S11/005 | NBOQOB200 | Data quality | Row note | Box 005 is absent from the other 1F schedule, which jumps 004 to 006. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/B/S14/03 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/03 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/03 | NBOQOB250 | Air | Air flow (per box) | 305 | l/s | 305 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/04 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/04 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/04 | NBOQOB250 | Air | Air flow (per box) | 305 | l/s | 305 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/05 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/05 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/05 | NBOQOB250 | Air | Air flow (per box) | 305 | l/s | 305 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S13/004 |  | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S13/005 |  | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S14/001 |  | Air | Air flow (per box) | 125 | l/s | 125 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S14/002 |  | Air | Air flow (per box) | 250 | l/s | 250 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S15/001 |  | Air | Air flow (per box) | 125 | l/s | 125 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S15/002 |  | Air | Air flow (per box) | 125 | l/s | 125 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S15/003 |  | Air | Air flow (per box) | 125 | l/s | 125 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S12/001 |  | Air | Air flow (per box) | 105 | l/s | 105 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/001 |  | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/001 |  | Provenance | Scheduled as | CAV/B/S13/001 TO 003 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13) | One schedule line of QTY 3, split to one row per box
CAV/B/S13/002 |  | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/002 |  | Provenance | Scheduled as | CAV/B/S13/001 TO 003 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13) | One schedule line of QTY 3, split to one row per box
CAV/B/S13/003 |  | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/003 |  | Provenance | Scheduled as | CAV/B/S13/001 TO 003 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13) | One schedule line of QTY 3, split to one row per box
CAV/B/S13/006 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/006 |  | Provenance | Scheduled as | CAV/B/S13/006 TO 008 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13) | One schedule line of QTY 3, split to one row per box
CAV/B/S13/007 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/007 |  | Provenance | Scheduled as | CAV/B/S13/006 TO 008 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13) | One schedule line of QTY 3, split to one row per box
CAV/B/S13/008 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/008 |  | Provenance | Scheduled as | CAV/B/S13/006 TO 008 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13) | One schedule line of QTY 3, split to one row per box
CAV/B/S13/012 |  | Air | Air flow (per box) | 50 | l/s | 50 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/013 |  | Air | Air flow (per box) | 50 | l/s | 50 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/014 |  | Air | Air flow (per box) | 70 | l/s | 70 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/015 |  | Air | Air flow (per box) | 150 | l/s | 150 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/016 |  | Air | Air flow (per box) | 285 | l/s | 285 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/017 |  | Air | Air flow (per box) | 145 | l/s | 145 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/018 |  | Air | Air flow (per box) | 145 | l/s | 145 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/019 |  | Air | Air flow (per box) | 190 | l/s | 190 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/020 |  | Air | Air flow (per box) | 150 | l/s | 150 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/021 |  | Air | Air flow (per box) | 85 | l/s | 85 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S12/002 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)
CAV/B/S12/002 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)
CAV/B/S12/002 | NBOQOB250 | Air | Air flow (per box) | 292 | l/s | 292 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)
CAV/B/S12/003 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)
CAV/B/S12/003 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)
CAV/B/S12/003 | NBOQOB250 | Air | Air flow (per box) | 292 | l/s | 292 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)
CAV/1F/S11/001 |  | Data quality | Source reference | All six CAV schedules were supplied as drawing images with the title block cropped out, so no drawing number, sheet or revision is recorded against any row. | [6 empty] | MEP schedule drawing (image supplied in chat) | all CAV schedules | Applies to the whole CAV set
CAV/1F/S11/001 |  | Data quality | Reference format | The header reads CAV/FLOOR/AHU NO/BOX NO, so CAV/1F/S11/001 is floor 1F, AHU S11, box 001. Air flow is stated per box. | [6 empty] | MEP schedule drawing (image supplied in chat) | all CAV schedules | Applies to the whole CAV set
CAV/1F/S11/001 |  | Data quality | Box number width | Most schedules use three-digit box numbers (001); the CAV/B/S14 schedule uses two digits (03, 04, 05). Both kept as written - the tag is the BMS join key. | [6 empty] | MEP schedule drawing (image supplied in chat) | all CAV schedules | Applies to the whole CAV set
CAV/1F/S11/001 |  | Data quality | Numbering gaps | CAV/1F/S11 runs 001, 002, 004, 005, 006-007, 008-009 once both 1F drawings are read together - box 003 is on neither. CAV/B/S13 runs 001-008 then 012-021, so boxes 009, 010 and 011 are absent. | [6 empty] | MEP schedule drawing (image supplied in chat) | all CAV schedules | Applies to the whole CAV set
CAV/1F/S11/001 |  | Data quality | Schedule scope | The basement S13-S15 and S12/S13 schedules state no model and no make; those columns do not exist on them. Nothing was carried across from the schedules that do. | [6 empty] | MEP schedule drawing (image supplied in chat) | all CAV schedules | Applies to the whole CAV set

## VAV Units
VAV Units
Variable air volume boxes across six schedules on level 1F and the basement. Two drawings overlap on the basement S10/S15 boxes and disagree on one air flow; both are recorded. Five out-of-range rows were excluded on instruction.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
VAV/1F/S15/005 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/005 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/005 | NBOQOB250 | Air | Air flow (per box) | 290 | l/s | 290 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/005 | NBOQOB250 | Provenance | Scheduled as | VAV/1F/S15/005 TO 009 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 5, split to one row per box
VAV/1F/S15/006 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/006 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/006 | NBOQOB250 | Air | Air flow (per box) | 290 | l/s | 290 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/006 | NBOQOB250 | Provenance | Scheduled as | VAV/1F/S15/005 TO 009 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 5, split to one row per box
VAV/1F/S15/007 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/007 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/007 | NBOQOB250 | Air | Air flow (per box) | 290 | l/s | 290 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/007 | NBOQOB250 | Provenance | Scheduled as | VAV/1F/S15/005 TO 009 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 5, split to one row per box
VAV/1F/S15/008 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/008 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/008 | NBOQOB250 | Air | Air flow (per box) | 290 | l/s | 290 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/008 | NBOQOB250 | Provenance | Scheduled as | VAV/1F/S15/005 TO 009 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 5, split to one row per box
VAV/1F/S15/009 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/009 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/009 | NBOQOB250 | Air | Air flow (per box) | 290 | l/s | 290 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/009 | NBOQOB250 | Provenance | Scheduled as | VAV/1F/S15/005 TO 009 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 5, split to one row per box
VAV/1F/S11/001 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/001 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/001 | NBOQOB200 | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/001 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S11/001 TO 003 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 3, split to one row per box
VAV/1F/S11/002 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/002 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/002 | NBOQOB200 | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/002 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S11/001 TO 003 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 3, split to one row per box
VAV/1F/S11/003 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/003 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/003 | NBOQOB200 | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/003 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S11/001 TO 003 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 3, split to one row per box
VAV/1F/S11/004 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/004 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/004 | NBOQOB250 | Air | Air flow (per box) | 243 | l/s | 243 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/004 | NBOQOB250 | Provenance | Scheduled as | VAV/1F/S11/004 TO 005 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 2, split to one row per box
VAV/1F/S11/005 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/005 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/005 | NBOQOB250 | Air | Air flow (per box) | 243 | l/s | 243 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/005 | NBOQOB250 | Provenance | Scheduled as | VAV/1F/S11/004 TO 005 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 2, split to one row per box
VAV/1F/S11/022 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/022 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/022 | NBOQOB200 | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/022 | NBOQOB200 | Data quality | Row note | Governs box 022. Confirmed by the user against the overlapping VAV/1F/S11/022 TO 24 row on the same schedule. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/006 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/006 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/006 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/006 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S11/006 TO 013 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/007 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/007 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/007 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/007 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S11/006 TO 013 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/008 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/008 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/008 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/008 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S11/006 TO 013 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/009 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/009 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/009 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/009 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S11/006 TO 013 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/010 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/010 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/010 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/010 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S11/006 TO 013 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/011 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/011 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/011 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/011 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S11/006 TO 013 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/012 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/012 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/012 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/012 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S11/006 TO 013 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/013 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/013 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/013 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/013 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S11/006 TO 013 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/014 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/014 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/014 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/014 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S11/014 TO 021 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/015 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/015 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/015 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/015 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S11/014 TO 021 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/016 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/016 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/016 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/016 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S11/014 TO 021 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/017 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/017 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/017 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/017 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S11/014 TO 021 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/018 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/018 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/018 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/018 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S11/014 TO 021 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/019 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/019 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/019 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/019 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S11/014 TO 021 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/020 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/020 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/020 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/020 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S11/014 TO 021 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S11/021 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/021 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/021 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/021 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S11/014 TO 021 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 8, split to one row per box
VAV/1F/S15/012 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/012 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/012 | NBOQOB200 | Air | Air flow (per box) | 120 | l/s | 120 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/012 | NBOQOB200 | Data quality | Reference and quantity disagree | single reference but QTY is 2 - the schedule does not name the other boxes | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | Not split into individual boxes - confirm before modelling
VAV/1F/S11/023 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/023 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/023 | NBOQOB160 | Air | Air flow (per box) | 147 | l/s | 147 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/023 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S11/022 TO 24 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 3, split to one row per box
VAV/1F/S11/024 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/024 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/024 | NBOQOB160 | Air | Air flow (per box) | 147 | l/s | 147 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/024 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S11/022 TO 24 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15) | One schedule line of QTY 3, split to one row per box
VAV/1F/S11/023 | NBOQOB160 | Data quality | Row note | Covers boxes 023 and 024 only. Box 022 is governed by the standalone VAV/1F/S11/022 row on the same schedule, per the user's decision. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/001 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/001 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/001 | NBOQOB200 | Air | Air flow (per box) | 257 | l/s | 257 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/001 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/001 TO 002 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 2, split to one row per box
VAV/1F/S15/002 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/002 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/002 | NBOQOB200 | Air | Air flow (per box) | 257 | l/s | 257 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/002 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/001 TO 002 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 2, split to one row per box
VAV/1F/S15/003 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/003 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/003 | NBOQOB200 | Air | Air flow (per box) | 257 | l/s | 257 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/003 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/003 TO 004 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 2, split to one row per box
VAV/1F/S15/004 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/004 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/004 | NBOQOB200 | Air | Air flow (per box) | 257 | l/s | 257 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/004 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/003 TO 004 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 2, split to one row per box
VAV/1F/S15/006 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/006 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/006 |  | Provenance | Scheduled as | VAV/1F/S15/006 TO 011 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 6, split to one row per box
VAV/1F/S15/007 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/007 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/007 |  | Provenance | Scheduled as | VAV/1F/S15/006 TO 011 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 6, split to one row per box
VAV/1F/S15/008 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/008 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/008 |  | Provenance | Scheduled as | VAV/1F/S15/006 TO 011 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 6, split to one row per box
VAV/1F/S15/009 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/009 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/009 |  | Provenance | Scheduled as | VAV/1F/S15/006 TO 011 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 6, split to one row per box
VAV/1F/S15/010 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/010 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/010 |  | Provenance | Scheduled as | VAV/1F/S15/006 TO 011 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 6, split to one row per box
VAV/1F/S15/011 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/011 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/011 |  | Provenance | Scheduled as | VAV/1F/S15/006 TO 011 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 6, split to one row per box
VAV/1F/S15/012 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/012 |  | Air | Air flow (per box) | 120 | l/s | 120 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/013 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/013 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/013 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/013 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/013 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 8, split to one row per box
VAV/1F/S15/014 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/013 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 8, split to one row per box
VAV/1F/S15/015 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/013 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 8, split to one row per box
VAV/1F/S15/016 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/016 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/016 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/016 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/013 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 8, split to one row per box
VAV/1F/S15/017 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/017 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/017 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/017 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/013 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 8, split to one row per box
VAV/1F/S15/018 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/018 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/018 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/018 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/013 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 8, split to one row per box
VAV/1F/S15/019 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/019 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/019 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/019 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/013 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 8, split to one row per box
VAV/1F/S15/020 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/020 | NBOQOB200 | Identification | Model | NBOQOB200 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/020 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/020 | NBOQOB200 | Provenance | Scheduled as | VAV/1F/S15/013 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 8, split to one row per box
VAV/1F/S15/021 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/021 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/021 |  | Provenance | Scheduled as | VAV/1F/S15/021 TO 024 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 4, split to one row per box
VAV/1F/S15/022 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/022 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/022 |  | Provenance | Scheduled as | VAV/1F/S15/021 TO 024 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 4, split to one row per box
VAV/1F/S15/023 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/023 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/023 |  | Provenance | Scheduled as | VAV/1F/S15/021 TO 024 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 4, split to one row per box
VAV/1F/S15/024 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/024 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/024 |  | Provenance | Scheduled as | VAV/1F/S15/021 TO 024 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 4, split to one row per box
VAV/1F/S15/025 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/025 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/025 | NBOQOB160 | Air | Air flow (per box) | 60 | l/s | 60 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/026 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/026 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/026 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/026 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/027 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/027 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/027 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/027 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/028 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/028 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/028 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/028 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/029 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/029 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/029 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/029 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/030 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/030 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/030 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/030 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/031 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/031 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/031 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/031 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/032 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/032 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/032 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/032 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/033 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/033 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/033 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/033 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/034 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/034 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/034 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/034 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/035 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/035 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/035 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/035 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/036 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/036 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/036 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/036 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/037 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/037 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/037 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/037 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/026 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 12, split to one row per box
VAV/1F/S15/039 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/039 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/039 | NBOQOB160 | Air | Air flow (per box) | 160 | l/s | 160 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/039 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/039 TO 040 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 2, split to one row per box
VAV/1F/S15/040 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/040 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/040 | NBOQOB160 | Air | Air flow (per box) | 160 | l/s | 160 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/040 | NBOQOB160 | Provenance | Scheduled as | VAV/1F/S15/039 TO 040 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 2, split to one row per box
VAV/1F/S15/014 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB250 | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB250 | Provenance | Scheduled as | VAV/1F/S15/014 TO 015 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 2, split to one row per box
VAV/1F/S15/015 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB250 | Identification | Model | NBOQOB250 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB250 | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB250 | Provenance | Scheduled as | VAV/1F/S15/014 TO 015 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing) | One schedule line of QTY 2, split to one row per box
VAV/1F/S15/014 | NBOQOB250 | Data quality | Row note | Overlaps VAV/1F/S15/013 TO 020 on the same schedule, which gives these boxes 174 l/s on NBOQOB200. Unresolved. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/038 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/038 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/038 | NBOQOB160 | Air | Air flow (per box) | 60 | l/s | 60 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S11/025 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S11/025 | NBOQOB160 | Identification | Model | NBOQOB160 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S11/025 | NBOQOB160 | Air | Air flow (per box) | 147 | l/s | 147 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/B/S10/020 |  | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/020 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/020 |  | Provenance | Scheduled as | VAV/B/S10/020 TO 023 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 4, split to one row per box
VAV/B/S10/021 |  | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/021 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/021 |  | Provenance | Scheduled as | VAV/B/S10/020 TO 023 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 4, split to one row per box
VAV/B/S10/022 |  | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/022 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/022 |  | Provenance | Scheduled as | VAV/B/S10/020 TO 023 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 4, split to one row per box
VAV/B/S10/023 |  | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/023 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/023 |  | Provenance | Scheduled as | VAV/B/S10/020 TO 023 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 4, split to one row per box
VAV/B/S15/001 |  | Air | Air flow (per box) | 261 | l/s | 261 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/001 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/001 |  | Provenance | Scheduled as | VAV/B/S15/001 TO 004 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 4, split to one row per box
VAV/B/S15/002 |  | Air | Air flow (per box) | 261 | l/s | 261 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/002 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/002 |  | Provenance | Scheduled as | VAV/B/S15/001 TO 004 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 4, split to one row per box
VAV/B/S15/003 |  | Air | Air flow (per box) | 261 | l/s | 261 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/003 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/003 |  | Provenance | Scheduled as | VAV/B/S15/001 TO 004 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 4, split to one row per box
VAV/B/S15/004 |  | Air | Air flow (per box) | 261 | l/s | 261 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/004 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/004 |  | Provenance | Scheduled as | VAV/B/S15/001 TO 004 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 4, split to one row per box
VAV/B/S15/001 |  | Data quality | Row note | The model-and-make drawing of the same schedule gives 251 l/s for these boxes. Unresolved. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/005 |  | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/005 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/005 |  | Provenance | Scheduled as | VAV/B/S15/005 & 006 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 2, split to one row per box
VAV/B/S15/006 |  | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/006 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/006 |  | Provenance | Scheduled as | VAV/B/S15/005 & 006 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 2, split to one row per box
VAV/B/S15/007 |  | Air | Air flow (per box) | 78 | l/s | 78 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/007 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/008 |  | Air | Air flow (per box) | 227 | l/s | 227 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/008 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/009 |  | Air | Air flow (per box) | 143 | l/s | 143 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/009 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/010 |  | Air | Air flow (per box) | 179 | l/s | 179 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/010 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/011 |  | Air | Air flow (per box) | 262 | l/s | 262 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/011 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/011 |  | Provenance | Scheduled as | VAV/B/S15/011 TO 012 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 2, split to one row per box
VAV/B/S15/012 |  | Air | Air flow (per box) | 262 | l/s | 262 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/012 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/012 |  | Provenance | Scheduled as | VAV/B/S15/011 TO 012 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity) | One schedule line of QTY 2, split to one row per box
VAV/B/S10/020 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/020 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/020 | NBOQE03 | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/020 | NBOQE03 | Provenance | Scheduled as | VAV/B/S10/020 TO 023 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 4, split to one row per box
VAV/B/S10/021 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/021 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/021 | NBOQE03 | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/021 | NBOQE03 | Provenance | Scheduled as | VAV/B/S10/020 TO 023 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 4, split to one row per box
VAV/B/S10/022 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/022 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/022 | NBOQE03 | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/022 | NBOQE03 | Provenance | Scheduled as | VAV/B/S10/020 TO 023 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 4, split to one row per box
VAV/B/S10/023 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/023 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/023 | NBOQE03 | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/023 | NBOQE03 | Provenance | Scheduled as | VAV/B/S10/020 TO 023 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 4, split to one row per box
VAV/B/S15/001 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/001 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/001 | NBOQE03 | Air | Air flow (per box) | 251 | l/s | 251 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/001 | NBOQE03 | Provenance | Scheduled as | VAV/B/S15/001 TO 004 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 4, split to one row per box
VAV/B/S15/002 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/002 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/002 | NBOQE03 | Air | Air flow (per box) | 251 | l/s | 251 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/002 | NBOQE03 | Provenance | Scheduled as | VAV/B/S15/001 TO 004 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 4, split to one row per box
VAV/B/S15/003 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/003 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/003 | NBOQE03 | Air | Air flow (per box) | 251 | l/s | 251 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/003 | NBOQE03 | Provenance | Scheduled as | VAV/B/S15/001 TO 004 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 4, split to one row per box
VAV/B/S15/004 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/004 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/004 | NBOQE03 | Air | Air flow (per box) | 251 | l/s | 251 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/004 | NBOQE03 | Provenance | Scheduled as | VAV/B/S15/001 TO 004 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 4, split to one row per box
VAV/B/S15/001 | NBOQE03 | Data quality | Row note | The heating-capacity drawing of the same schedule gives 261 l/s for these boxes. Unresolved. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/005 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/005 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/005 | NBOQE03 | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/005 | NBOQE03 | Provenance | Scheduled as | VAV/B/S15/005 TO 006 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 2, split to one row per box
VAV/B/S15/006 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/006 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/006 | NBOQE03 | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/006 | NBOQE03 | Provenance | Scheduled as | VAV/B/S15/005 TO 006 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 2, split to one row per box
VAV/B/S15/007 |  | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/007 |  | Air | Air flow (per box) | 78 | l/s | 78 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/007 |  | Data quality | Row note | Model cell is blank on this schedule; every other row on it reads NBOQE03. | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/008 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/008 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/008 | NBOQE03 | Air | Air flow (per box) | 227 | l/s | 227 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/009 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/009 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/009 | NBOQE03 | Air | Air flow (per box) | 143 | l/s | 143 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/010 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/010 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/010 | NBOQE03 | Air | Air flow (per box) | 179 | l/s | 179 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/011 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/011 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/011 | NBOQE03 | Air | Air flow (per box) | 262 | l/s | 262 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/011 | NBOQE03 | Provenance | Scheduled as | VAV/B/S15/011 TO 012 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 2, split to one row per box
VAV/B/S15/012 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/012 | NBOQE03 | Identification | Model | NBOQE03 |  |  |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/012 | NBOQE03 | Air | Air flow (per box) | 262 | l/s | 262 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/012 | NBOQE03 | Provenance | Scheduled as | VAV/B/S15/011 TO 012 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make) | One schedule line of QTY 2, split to one row per box
VAV/B/S14/001 |  | Air | Air flow (per box) | 230 | l/s | 230 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/001 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/001 |  | Provenance | Scheduled as | VAV/B/S14/001 TO 003 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S14/002 |  | Air | Air flow (per box) | 230 | l/s | 230 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/002 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/002 |  | Provenance | Scheduled as | VAV/B/S14/001 TO 003 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S14/003 |  | Air | Air flow (per box) | 230 | l/s | 230 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/003 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/003 |  | Provenance | Scheduled as | VAV/B/S14/001 TO 003 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S14/004 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/004 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/004 |  | Provenance | Scheduled as | VAV/B/S14/004 TO 006 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S14/005 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/005 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/005 |  | Provenance | Scheduled as | VAV/B/S14/004 TO 006 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S14/006 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/006 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/006 |  | Provenance | Scheduled as | VAV/B/S14/004 TO 006 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S14/007 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/007 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/007 |  | Provenance | Scheduled as | VAV/B/S14/007 & 008 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 2, split to one row per box
VAV/B/S14/008 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/008 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/008 |  | Provenance | Scheduled as | VAV/B/S14/007 & 008 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 2, split to one row per box
VAV/B/S14/009 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/009 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/010 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/010 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/011 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/011 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/012 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/012 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/009 TO 012 |  | Data quality | Reference and quantity disagree | reference spans 4 boxes but QTY is 2 | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | Not split into individual boxes - confirm before modelling
VAV/B/S14/013 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/013 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/013 |  | Provenance | Scheduled as | VAV/B/S14/013 TO 016 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S14/014 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/014 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/014 |  | Provenance | Scheduled as | VAV/B/S14/013 TO 016 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S14/015 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/015 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/015 |  | Provenance | Scheduled as | VAV/B/S14/013 TO 016 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S14/016 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/016 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/016 |  | Provenance | Scheduled as | VAV/B/S14/013 TO 016 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S14/017 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/017 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/017 |  | Provenance | Scheduled as | VAV/B/S14/017 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S14/018 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/018 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/018 |  | Provenance | Scheduled as | VAV/B/S14/017 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S14/019 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/019 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/019 |  | Provenance | Scheduled as | VAV/B/S14/017 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S14/020 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/020 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/020 |  | Provenance | Scheduled as | VAV/B/S14/017 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S21 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S21 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/025 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/025 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/025 |  | Provenance | Scheduled as | VAV/B/S14/025 TO 028 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S14/026 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/026 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/026 |  | Provenance | Scheduled as | VAV/B/S14/025 TO 028 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S14/027 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/027 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/027 |  | Provenance | Scheduled as | VAV/B/S14/025 TO 028 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S14/028 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/028 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/028 |  | Provenance | Scheduled as | VAV/B/S14/025 TO 028 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 4, split to one row per box
VAV/B/S14/029 |  | Air | Air flow (per box) | 160 | l/s | 160 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/029 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/022 |  | Air | Air flow (per box) | 136 | l/s | 136 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/022 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/022 |  | Provenance | Scheduled as | VAV/B/S14/022 TO 024 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S14/023 |  | Air | Air flow (per box) | 136 | l/s | 136 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/023 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/023 |  | Provenance | Scheduled as | VAV/B/S14/022 TO 024 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S14/024 |  | Air | Air flow (per box) | 136 | l/s | 136 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/024 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/024 |  | Provenance | Scheduled as | VAV/B/S14/022 TO 024 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S14/030 |  | Air | Air flow (per box) | 136 | l/s | 136 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/030 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/030 |  | Provenance | Scheduled as | VAV/B/S14/030 & 031 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 2, split to one row per box
VAV/B/S14/031 |  | Air | Air flow (per box) | 136 | l/s | 136 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/031 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/031 |  | Provenance | Scheduled as | VAV/B/S14/030 & 031 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 2, split to one row per box
VAV/B/S13/003 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/003 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/003 |  | Provenance | Scheduled as | VAV/B/S13/003 TO 005 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S13/004 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/004 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/004 |  | Provenance | Scheduled as | VAV/B/S13/003 TO 005 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S13/005 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/005 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/005 |  | Provenance | Scheduled as | VAV/B/S13/003 TO 005 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S13/007 |  | Air | Air flow (per box) | 99 | l/s | 99 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/007 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/008 |  | Air | Air flow (per box) | 95 | l/s | 95 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/008 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/001 |  | Air | Air flow (per box) | 246 | l/s | 246 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/001 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/008 |  | Air | Air flow (per box) | 246 | l/s | 246 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/008 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/001 & 008 |  | Data quality | Reference and quantity disagree | reference spans 2 boxes but QTY is 8 | [6 empty] | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | Not split into individual boxes - confirm before modelling
VAV/B/S10/009 |  | Air | Air flow (per box) | 262 | l/s | 262 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/009 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/010 |  | Air | Air flow (per box) | 254 | l/s | 254 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/010 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/010 |  | Provenance | Scheduled as | VAV/B/S10/010 & 011 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 2, split to one row per box
VAV/B/S10/011 |  | Air | Air flow (per box) | 254 | l/s | 254 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/011 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/011 |  | Provenance | Scheduled as | VAV/B/S10/010 & 011 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 2, split to one row per box
VAV/B/S10/012 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/012 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/012 |  | Provenance | Scheduled as | VAV/B/S10/012 TO 014 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S10/013 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/013 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/013 |  | Provenance | Scheduled as | VAV/B/S10/012 TO 014 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S10/014 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/014 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/014 |  | Provenance | Scheduled as | VAV/B/S10/012 TO 014 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S10/015 |  | Air | Air flow (per box) | 300 | l/s | 300 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/015 |  | Heating | Heating capacity | 1 | kW | 1 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/016 |  | Air | Air flow (per box) | 212 | l/s | 212 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/016 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/016 |  | Provenance | Scheduled as | VAV/B/S10/016 TO 018 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S10/017 |  | Air | Air flow (per box) | 212 | l/s | 212 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/017 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/017 |  | Provenance | Scheduled as | VAV/B/S10/016 TO 018 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S10/018 |  | Air | Air flow (per box) | 212 | l/s | 212 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/018 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/018 |  | Provenance | Scheduled as | VAV/B/S10/016 TO 018 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14) | One schedule line of QTY 3, split to one row per box
VAV/B/S10/019 |  | Air | Air flow (per box) | 215 | l/s | 215 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/019 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S11/001 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/001 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/001 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/001 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/002 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/002 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/002 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/002 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/003 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/003 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/003 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/003 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/004 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/004 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/004 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/004 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/005 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/005 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/005 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/005 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/006 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/006 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/006 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/006 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/007 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/007 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/007 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/007 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/008 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/008 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/008 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/008 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/009 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/009 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/009 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/009 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/010 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/010 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/010 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/010 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/011 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/011 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/011 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/011 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/012 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/012 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/012 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/012 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/013 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/013 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/013 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/013 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/014 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/014 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/014 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/014 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/015 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/015 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/015 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/015 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/016 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/016 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/016 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/016 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/017 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/017 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/017 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/017 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/018 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/018 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/018 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/018 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/019 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/019 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/019 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/019 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/020 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/020 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/020 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/020 |  | Provenance | Scheduled as | VAV/B/S11/001 TO 020 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 20, split to one row per box
VAV/B/S11/021 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/021 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/021 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/021 |  | Provenance | Scheduled as | VAV/B/S11/021 TO 023 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 3, split to one row per box
VAV/B/S11/022 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/022 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/022 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/022 |  | Provenance | Scheduled as | VAV/B/S11/021 TO 023 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 3, split to one row per box
VAV/B/S11/023 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/023 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/023 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/023 |  | Provenance | Scheduled as | VAV/B/S11/021 TO 023 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 3, split to one row per box
VAV/B/S11/024 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/024 |  | Air | Air flow (per box) | 86 | l/s | 86 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/024 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/024 |  | Provenance | Scheduled as | VAV/B/S11/024 TO 025 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 2, split to one row per box
VAV/B/S11/025 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/025 |  | Air | Air flow (per box) | 86 | l/s | 86 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/025 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/025 |  | Provenance | Scheduled as | VAV/B/S11/024 TO 025 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 2, split to one row per box
VAV/B/S11/026 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/026 |  | Air | Air flow (per box) | 100 | l/s | 100 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/026 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/026 |  | Provenance | Scheduled as | VAV/B/S11/026 TO 027 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 2, split to one row per box
VAV/B/S11/027 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/027 |  | Air | Air flow (per box) | 100 | l/s | 100 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/027 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/027 |  | Provenance | Scheduled as | VAV/B/S11/026 TO 027 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 2, split to one row per box
VAV/B/S11/028 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/028 |  | Air | Air flow (per box) | 90 | l/s | 90 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/028 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/028 |  | Provenance | Scheduled as | VAV/B/S11/028 TO 031 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 4, split to one row per box
VAV/B/S11/029 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/029 |  | Air | Air flow (per box) | 90 | l/s | 90 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/029 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/029 |  | Provenance | Scheduled as | VAV/B/S11/028 TO 031 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 4, split to one row per box
VAV/B/S11/030 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/030 |  | Air | Air flow (per box) | 90 | l/s | 90 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/030 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/030 |  | Provenance | Scheduled as | VAV/B/S11/028 TO 031 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 4, split to one row per box
VAV/B/S11/031 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/031 |  | Air | Air flow (per box) | 90 | l/s | 90 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/031 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/031 |  | Provenance | Scheduled as | VAV/B/S11/028 TO 031 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 4, split to one row per box
VAV/B/S11/032 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/032 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/032 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/032 |  | Provenance | Scheduled as | VAV/B/S11/032 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 6, split to one row per box
VAV/B/S11/033 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/033 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/033 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/033 |  | Provenance | Scheduled as | VAV/B/S11/032 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 6, split to one row per box
VAV/B/S11/034 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/034 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/034 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/034 |  | Provenance | Scheduled as | VAV/B/S11/032 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 6, split to one row per box
VAV/B/S11/035 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/035 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/035 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/035 |  | Provenance | Scheduled as | VAV/B/S11/032 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 6, split to one row per box
VAV/B/S11/036 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/036 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/036 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/036 |  | Provenance | Scheduled as | VAV/B/S11/032 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 6, split to one row per box
VAV/B/S11/037 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/037 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/037 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/037 |  | Provenance | Scheduled as | VAV/B/S11/032 TO 037 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 6, split to one row per box
VAV/B/S11/038 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/038 |  | Air | Air flow (per box) | 120 | l/s | 120 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/038 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/039 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/039 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/039 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/039 |  | Provenance | Scheduled as | VAV/B/S11/039 TO 041 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 3, split to one row per box
VAV/B/S11/040 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/040 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/040 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/040 |  | Provenance | Scheduled as | VAV/B/S11/039 TO 041 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 3, split to one row per box
VAV/B/S11/041 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/041 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/041 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/041 |  | Provenance | Scheduled as | VAV/B/S11/039 TO 041 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 3, split to one row per box
VAV/B/S11/042 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/042 |  | Air | Air flow (per box) | 120 | l/s | 120 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/042 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/043 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/043 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/043 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/043 |  | Provenance | Scheduled as | VAV/B/S11/043 TO 046 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 4, split to one row per box
VAV/B/S11/044 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/044 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/044 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/044 |  | Provenance | Scheduled as | VAV/B/S11/043 TO 046 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 4, split to one row per box
VAV/B/S11/045 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/045 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/045 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/045 |  | Provenance | Scheduled as | VAV/B/S11/043 TO 046 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 4, split to one row per box
VAV/B/S11/046 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/046 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/046 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/046 |  | Provenance | Scheduled as | VAV/B/S11/043 TO 046 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 4, split to one row per box
VAV/B/S13/001 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/001 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/001 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/001 |  | Provenance | Scheduled as | VAV/B/S13/001 TO 002 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 2, split to one row per box
VAV/B/S13/002 |  | Identification | Make | TITUS USA |  |  |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/002 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/002 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/002 |  | Provenance | Scheduled as | VAV/B/S13/001 TO 002 | [5 empty] | reference | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS) | One schedule line of QTY 2, split to one row per box
VAV/1F/S15/005 |  | Data quality | Source reference | All six VAV schedules were supplied as drawing images with the title block cropped out, so no drawing number, sheet or revision is recorded against any row. | [6 empty] | MEP schedule drawing (image supplied in chat) | all VAV schedules | Applies to the whole VAV set
VAV/1F/S15/005 |  | Data quality | Reference format | The header reads VAV/FLOOR/AHU NO/BOX NO. Air flow is stated per VAV box, so a range row carries that flow on each of its boxes, not across them. | [6 empty] | MEP schedule drawing (image supplied in chat) | all VAV schedules | Applies to the whole VAV set
VAV/1F/S15/005 |  | Data quality | Duplicate box 022 - resolved | VAV/1F/S11/022 appears twice on the 1F schedule. The user confirmed the standalone row governs: 220 l/s on NBOQOB200. The overlapping 'VAV/1F/S11/022 TO 24' row is therefore read as covering boxes 023 and 024 only. | [6 empty] | MEP schedule drawing (image supplied in chat) | all VAV schedules | Applies to the whole VAV set
VAV/1F/S15/005 |  | Data quality | Rows excluded on instruction | Five rows carrying box numbers far outside the range their schedule otherwise uses were dropped at the user's direction: VAV/1F/S15/395, VAV/1F/S11/088 and VAV/1F/S11/096-098 from the first 1F schedule, and VAV/1F/S11/088 TO 087 and VAV/1F/S15/096 TO 098 from the second. | [6 empty] | MEP schedule drawing (image supplied in chat) | all VAV schedules | Applies to the whole VAV set
VAV/1F/S15/005 |  | Data quality | Overlapping drawings - S10/S15 | Two drawings schedule the same basement boxes. One carries heating capacity, the other model and make, and they disagree on VAV/B/S15/001 TO 004 (261 l/s against 251 l/s). Both are recorded against their own drawing; neither was picked. | [6 empty] | MEP schedule drawing (image supplied in chat) | all VAV schedules | Applies to the whole VAV set
VAV/1F/S15/005 |  | Data quality | Overlapping rows - 1F/S15 | On the second 1F schedule, VAV/1F/S15/014 TO 015 (240 l/s, NBOQOB250) falls inside VAV/1F/S15/013 TO 020 (174 l/s, NBOQOB200). Both are recorded. | [6 empty] | MEP schedule drawing (image supplied in chat) | all VAV schedules | Applies to the whole VAV set
VAV/1F/S15/005 |  | Data quality | Box 012 disagreement | VAV/1F/S15/012 is scheduled at 120 l/s on both 1F drawings, but the first states QTY 02 and the second QTY 01 for a single-box reference. | [6 empty] | MEP schedule drawing (image supplied in chat) | all VAV schedules | Applies to the whole VAV set
VAV/1F/S15/005 |  | Data quality | Missing boxes | VAV/B/S14 runs 001-020 then 022-031, so box 021 is absent. On the second 1F schedule VAV/1F/S15 runs 001-004 then 006-011, so box 005 is absent there - though the first 1F schedule does carry VAV/1F/S15/005 TO 009. | [6 empty] | MEP schedule drawing (image supplied in chat) | all VAV schedules | Applies to the whole VAV set
VAV/1F/S15/005 |  | Data quality | Reference shape | VAV/B/S21 has no floor or box segment, unlike every other reference on its schedule. Kept as written - the tag is the BMS join key. | [6 empty] | MEP schedule drawing (image supplied in chat) | all VAV schedules | Applies to the whole VAV set
VAV/1F/S15/005 |  | Data quality | Schedule scope | No single schedule carries every column. The 1F drawings give model and make but no heating capacity; the basement S10/S13/S14 and S11/S13 drawings give heating capacity but no model. Nothing was carried across between drawings. | [6 empty] | MEP schedule drawing (image supplied in chat) | all VAV schedules | Applies to the whole VAV set

## DX Units
DX Units
21 DX split systems from the schematic riser, with indoor and outdoor models from SYSTEM DETAILS Table 3.6 for DX/B/01 to DX/B/16. The cooling figure is the load printed on each room box, not a per-unit capacity. Five units take an X2 outdoor model - two condensers each - so the schematic's matching-number pairing does not describe them.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
DX/B/01 | PEAD-RP35 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/01 | PEAD-RP35 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/01 | PEAD-RP35 | Served space | Room served | MV ROOM | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/01 | PEAD-RP35 | Served space | Room design temperature | 35 | degC | 35 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/01 | PEAD-RP35 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/01 | PEAD-RP35 | Served space | Room cooling load | 2.3 | kW | 2.3 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/01 | PEAD-RP35 | Refrigeration | Matched condensing unit | DX/OD/01 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/B/01 | PEAD-RP35 | Identification | Location (equipment schedule) | MV Room, HV Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/01 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/01 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/01 | PEAD-RP35 | Refrigeration | Outdoor units required | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | No multiplier on the outdoor model
DX/B/01 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/02 | PEAD-RP35 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/02 | PEAD-RP35 | Identification | Duty or standby | STANDBY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/02 | PEAD-RP35 | Served space | Room served | MV ROOM | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/02 | PEAD-RP35 | Served space | Room design temperature | 35 | degC | 35 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/02 | PEAD-RP35 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/02 | PEAD-RP35 | Served space | Room cooling load | 2.3 | kW | 2.3 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/02 | PEAD-RP35 | Refrigeration | Matched condensing unit | DX/OD/02 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing - this condenser is marked (ST.BY)
DX/B/02 | PEAD-RP35 | Identification | Location (equipment schedule) | MV Room, HV Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/02 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/02 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/02 | PEAD-RP35 | Refrigeration | Outdoor units required | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | No multiplier on the outdoor model
DX/B/02 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/05 | PEAD-RP35 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/05 | PEAD-RP35 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/05 | PEAD-RP35 | Served space | Room served | HV ROOM | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/05 | PEAD-RP35 | Served space | Room design temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/05 | PEAD-RP35 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/05 | PEAD-RP35 | Served space | Room cooling load | 2.3 | kW | 2.3 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/05 | PEAD-RP35 | Refrigeration | Matched condensing unit | DX/OD/05 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing - this condenser is marked (ST.BY)
DX/B/05 | PEAD-RP35 | Identification | Location (equipment schedule) | MV Room, HV Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/05 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/05 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/05 | PEAD-RP35 | Refrigeration | Outdoor units required | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | No multiplier on the outdoor model
DX/B/05 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/06 | PEAD-RP35 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/06 | PEAD-RP35 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/06 | PEAD-RP35 | Served space | Room served | HV ROOM | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/06 | PEAD-RP35 | Served space | Room design temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/06 | PEAD-RP35 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/06 | PEAD-RP35 | Served space | Room cooling load | 2.3 | kW | 2.3 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/06 | PEAD-RP35 | Refrigeration | Matched condensing unit | DX/OD/06 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/B/06 | PEAD-RP35 | Identification | Location (equipment schedule) | MV Room, HV Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/06 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/06 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/06 | PEAD-RP35 | Refrigeration | Outdoor units required | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | No multiplier on the outdoor model
DX/B/06 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/03 | PEAD-RP400 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/03 | PEAD-RP400 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/03 | PEAD-RP400 | Served space | Room served | TRANSFORMER ROOM | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/03 | PEAD-RP400 | Served space | Room design temperature | 35 | degC | 35 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/03 | PEAD-RP400 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/03 | PEAD-RP400 | Served space | Room cooling load | 35 | kW | 35 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/03 | PEAD-RP400 | Refrigeration | Matched condensing unit | DX/OD/03 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | The equipment schedule gives this unit an X2 outdoor model, so it takes TWO condensers. The single matching number is not the whole pairing - the pipework layout plan is needed.
DX/B/03 | PEAD-RP400 | Identification | Location (equipment schedule) | Transformer Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/03 | PEAD-RP400 | Identification | Indoor unit model | PEAD-RP400 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/03 | PEAD-RP400 | Refrigeration | Outdoor unit model | PUHZ-RP200X2 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | X2 suffix - two condensers per indoor unit goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/03 | PEAD-RP400 | Refrigeration | Outdoor units required | 2 | n | 2 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Read from the X2 suffix on the outdoor model
DX/B/03 | PEAD-RP400 | Air | Number of speeds | 2 | n | 2 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/04 | PEAD-RP400 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/04 | PEAD-RP400 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/04 | PEAD-RP400 | Served space | Room served | TRANSFORMER ROOM | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/04 | PEAD-RP400 | Served space | Room design temperature | 35 | degC | 35 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/04 | PEAD-RP400 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/04 | PEAD-RP400 | Served space | Room cooling load | 35 | kW | 35 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/04 | PEAD-RP400 | Refrigeration | Matched condensing unit | DX/OD/04 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | The equipment schedule gives this unit an X2 outdoor model, so it takes TWO condensers. The single matching number is not the whole pairing - the pipework layout plan is needed.
DX/B/04 | PEAD-RP400 | Identification | Location (equipment schedule) | Transformer Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/04 | PEAD-RP400 | Identification | Indoor unit model | PEAD-RP400 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/04 | PEAD-RP400 | Refrigeration | Outdoor unit model | PUHZ-RP200X2 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | X2 suffix - two condensers per indoor unit goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/04 | PEAD-RP400 | Refrigeration | Outdoor units required | 2 | n | 2 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Read from the X2 suffix on the outdoor model
DX/B/04 | PEAD-RP400 | Air | Number of speeds | 2 | n | 2 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/14 | PEAD-RP400 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/14 | PEAD-RP400 | Identification | Duty or standby | STANDBY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/14 | PEAD-RP400 | Served space | Room served | TRANSFORMER ROOM | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/14 | PEAD-RP400 | Served space | Room design temperature | 35 | degC | 35 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/14 | PEAD-RP400 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/14 | PEAD-RP400 | Served space | Room cooling load | 35 | kW | 35 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/14 | PEAD-RP400 | Refrigeration | Matched condensing unit | DX/OD/14 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | The equipment schedule gives this unit an X2 outdoor model, so it takes TWO condensers. The single matching number is not the whole pairing - the pipework layout plan is needed.
DX/B/14 | PEAD-RP400 | Identification | Location (equipment schedule) | Transformer Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/14 | PEAD-RP400 | Identification | Indoor unit model | PEAD-RP400 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/14 | PEAD-RP400 | Refrigeration | Outdoor unit model | PUHZ-RP200X2 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | X2 suffix - two condensers per indoor unit goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/14 | PEAD-RP400 | Refrigeration | Outdoor units required | 2 | n | 2 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Read from the X2 suffix on the outdoor model
DX/B/14 | PEAD-RP400 | Air | Number of speeds | 2 | n | 2 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/07 | PEAD-RP35 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/07 | PEAD-RP35 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/07 | PEAD-RP35 | Served space | Room served | MV ROOM 3 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/07 | PEAD-RP35 | Served space | Room design temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/07 | PEAD-RP35 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/07 | PEAD-RP35 | Served space | Room cooling load | 100 | kW | 100 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/07 | PEAD-RP35 | Refrigeration | Matched condensing unit | DX/OD/07 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/B/07 | PEAD-RP35 | Identification | Location (equipment schedule) | MV Room, HV Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/07 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/07 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/07 | PEAD-RP35 | Refrigeration | Outdoor units required | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | No multiplier on the outdoor model
DX/B/07 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/16 | PEAD-RP35 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/16 | PEAD-RP35 | Identification | Duty or standby | STANDBY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/16 | PEAD-RP35 | Served space | Room served | MV ROOM 3 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/16 | PEAD-RP35 | Served space | Room design temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/16 | PEAD-RP35 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/16 | PEAD-RP35 | Served space | Room cooling load | 100 | kW | 100 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/16 | PEAD-RP35 | Refrigeration | Matched condensing unit | DX/OD/16 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing - this condenser is marked (ST.BY)
DX/B/16 | PEAD-RP35 | Identification | Location (equipment schedule) | MV Room, HV Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/16 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/16 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/16 | PEAD-RP35 | Refrigeration | Outdoor units required | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | No multiplier on the outdoor model
DX/B/16 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/08 | PEAD-RP500 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/08 | PEAD-RP500 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/08 | PEAD-RP500 | Served space | Room served | UPS / EMERGENCY LIGHTING BATTERY ROOM | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/08 | PEAD-RP500 | Served space | Room design temperature | 25 | degC | 25 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/08 | PEAD-RP500 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/08 | PEAD-RP500 | Served space | Room cooling load | 44 | kW | 44 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/08 | PEAD-RP500 | Refrigeration | Matched condensing unit | DX/OD/08 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | The equipment schedule gives this unit an X2 outdoor model, so it takes TWO condensers. The single matching number is not the whole pairing - the pipework layout plan is needed.
DX/B/08 | PEAD-RP500 | Identification | Location (equipment schedule) | UPS Room/Emergency Battery Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/08 | PEAD-RP500 | Identification | Indoor unit model | PEAD-RP500 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/08 | PEAD-RP500 | Refrigeration | Outdoor unit model | PUHZ-RP2S0X2 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | X2 suffix - two condensers per indoor unit goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/08 | PEAD-RP500 | Refrigeration | Outdoor units required | 2 | n | 2 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Read from the X2 suffix on the outdoor model
DX/B/08 | PEAD-RP500 | Air | Number of speeds | 2 | n | 2 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/09 | PEAD-RP500 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/09 | PEAD-RP500 | Identification | Duty or standby | STANDBY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/09 | PEAD-RP500 | Served space | Room served | UPS / EMERGENCY LIGHTING BATTERY ROOM | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/09 | PEAD-RP500 | Served space | Room design temperature | 25 | degC | 25 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/09 | PEAD-RP500 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/09 | PEAD-RP500 | Served space | Room cooling load | 44 | kW | 44 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/09 | PEAD-RP500 | Refrigeration | Matched condensing unit | DX/OD/09 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | The equipment schedule gives this unit an X2 outdoor model, so it takes TWO condensers. The single matching number is not the whole pairing - the pipework layout plan is needed.
DX/B/09 | PEAD-RP500 | Identification | Location (equipment schedule) | UPS Room/Emergency Battery Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/09 | PEAD-RP500 | Identification | Indoor unit model | PEAD-RP500 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/09 | PEAD-RP500 | Refrigeration | Outdoor unit model | PUHZ-RP250X2 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | X2 suffix - two condensers per indoor unit goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/09 | PEAD-RP500 | Refrigeration | Outdoor units required | 2 | n | 2 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Read from the X2 suffix on the outdoor model
DX/B/09 | PEAD-RP500 | Air | Number of speeds | 2 | n | 2 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/10 | PEAD-RP125 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/10 | PEAD-RP125 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/10 | PEAD-RP125 | Served space | Room served | SECURITY EQUIPMENT ROOM | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/10 | PEAD-RP125 | Served space | Room design temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/10 | PEAD-RP125 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/10 | PEAD-RP125 | Served space | Room cooling load | 10 | kW | 10 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/10 | PEAD-RP125 | Refrigeration | Matched condensing unit | DX/OD/10 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/B/10 | PEAD-RP125 | Identification | Location (equipment schedule) | Security Equipment Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/10 | PEAD-RP125 | Identification | Indoor unit model | PEAD-RP125 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/10 | PEAD-RP125 | Refrigeration | Outdoor unit model | PUHZ-RP125 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/10 | PEAD-RP125 | Refrigeration | Outdoor units required | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | No multiplier on the outdoor model
DX/B/10 | PEAD-RP125 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/11 | PCA-RP71 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/11 | PCA-RP71 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/11 | PCA-RP71 | Served space | Room served | IRRIGATION PUMP ROOM | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/11 | PCA-RP71 | Served space | Room design temperature | 35 | degC | 35 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/11 | PCA-RP71 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/11 | PCA-RP71 | Served space | Room cooling load | 3.5 | kW | 3.5 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/11 | PCA-RP71 | Refrigeration | Matched condensing unit | DX/OD/11 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/B/11 | PCA-RP71 | Identification | Location (equipment schedule) | Irrigation Pump Room | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/11 | PCA-RP71 | Identification | Indoor unit model | PCA-RP71 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/11 | PCA-RP71 | Refrigeration | Outdoor unit model | PUHZ-RP71 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/11 | PCA-RP71 | Refrigeration | Outdoor units required | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | No multiplier on the outdoor model
DX/B/11 | PCA-RP71 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/12 | PEAD-RP50 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/12 | PEAD-RP50 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/12 | PEAD-RP50 | Served space | Room served | SECURITY STORES, SECURITY UPS | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/12 | PEAD-RP50 | Served space | Room design temperature | 25 | degC | 25 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/12 | PEAD-RP50 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/12 | PEAD-RP50 | Served space | Room cooling load | 4 | kW | 4 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/12 | PEAD-RP50 | Refrigeration | Matched condensing unit | DX/OD/12 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/B/12 | PEAD-RP50 | Identification | Location (equipment schedule) | Security Store/Security UPS | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/12 | PEAD-RP50 | Identification | Indoor unit model | PEAD-RP50 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/12 | PEAD-RP50 | Refrigeration | Outdoor unit model | PUHZ-RP50 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/12 | PEAD-RP50 | Refrigeration | Outdoor units required | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | No multiplier on the outdoor model
DX/B/12 | PEAD-RP50 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/13 | PCA-RP71 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/13 | PCA-RP71 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/13 | PCA-RP71 | Served space | Room served | TRASH CHAMBER | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/13 | PCA-RP71 | Served space | Room design temperature | 20 | degC | 20 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/13 | PCA-RP71 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/13 | PCA-RP71 | Served space | Room cooling load | 12 | kW | 12 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/13 | PCA-RP71 | Refrigeration | Matched condensing unit | DX/OD/13 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/B/13 | PCA-RP71 | Identification | Location (equipment schedule) | Trash Chamber | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/13 | PCA-RP71 | Identification | Indoor unit model | PCA-RP71 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/13 | PCA-RP71 | Refrigeration | Outdoor unit model | PUHZ-RP71 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/13 | PCA-RP71 | Refrigeration | Outdoor units required | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | No multiplier on the outdoor model
DX/B/13 | PCA-RP71 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/15 | PCA-RP71 | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/15 | PCA-RP71 | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/15 | PCA-RP71 | Served space | Room served | TRASH CHAMBER | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/15 | PCA-RP71 | Served space | Room design temperature | 20 | degC | 20 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/15 | PCA-RP71 | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/15 | PCA-RP71 | Served space | Room cooling load | 12 | kW | 12 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/15 | PCA-RP71 | Refrigeration | Matched condensing unit | DX/OD/15 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/B/15 | PCA-RP71 | Identification | Location (equipment schedule) | Trash Chamber | [5 empty] | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Coarser than the schematic's room; both are recorded
DX/B/15 | PCA-RP71 | Identification | Indoor unit model | PCA-RP71 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/15 | PCA-RP71 | Refrigeration | Outdoor unit model | PUHZ-RP71 |  |  |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/15 | PCA-RP71 | Refrigeration | Outdoor units required | 1 | n | 1 | unit:UNITLESS |  |  | reference | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | No multiplier on the outdoor model
DX/B/15 | PCA-RP71 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/17 |  | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/17 |  | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/17 |  | Served space | Room served | REFRIGERATED STORAGE (KITCHEN BACK OF HOUSE) | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/17 |  | Served space | Room design temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/17 |  | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/17 |  | Served space | Room cooling load | 3.75 | kW | 3.75 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/17 |  | Refrigeration | Matched condensing unit | DX/OD/17 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/B/17 |  | Data quality | Model not stated | This unit is on the schematic but not on SYSTEM DETAILS Table 3.6, which stops at DX/B/16. No indoor or outdoor model is available for it. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/18 |  | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/18 |  | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/18 |  | Served space | Room served | REFRIGERATED STORAGE (KITCHEN BACK OF HOUSE) | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/18 |  | Served space | Room design temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/18 |  | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/18 |  | Served space | Room cooling load | 3.75 | kW | 3.75 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/18 |  | Refrigeration | Matched condensing unit | DX/OD/18 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/B/18 |  | Data quality | Model not stated | This unit is on the schematic but not on SYSTEM DETAILS Table 3.6, which stops at DX/B/16. No indoor or outdoor model is available for it. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/19 |  | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/19 |  | Identification | Duty or standby | STANDBY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/19 |  | Served space | Room served | REFRIGERATED STORAGE (KITCHEN BACK OF HOUSE) | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/19 |  | Served space | Room design temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/19 |  | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/19 |  | Served space | Room cooling load | 3.75 | kW | 3.75 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; stated as SENSIBLE
DX/B/19 |  | Refrigeration | Matched condensing unit | DX/OD/19 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing - this condenser is marked (ST.BY)
DX/B/19 |  | Data quality | Model not stated | This unit is on the schematic but not on SYSTEM DETAILS Table 3.6, which stops at DX/B/16. No indoor or outdoor model is available for it. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/20 |  | Identification | Level | Lower level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/20 |  | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/B/20 |  | Served space | Room served | PLC 7 / IDF LOWER LEVEL ZONE 5 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/20 |  | Served space | Room design temperature | 22 | degC | 22 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/20 |  | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/20 |  | Served space | Room cooling load | 4.4 | kW | 4.4 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; the schematic does not say whether this is total or sensible
DX/B/20 |  | Refrigeration | Matched condensing unit | DX/OD/20 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/B/20 |  | Data quality | Model not stated | This unit is on the schematic but not on SYSTEM DETAILS Table 3.6, which stops at DX/B/16. No indoor or outdoor model is available for it. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/RP/21 |  | Identification | Level | Roof level | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/RP/21 |  | Identification | Duty or standby | DUTY | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | No (ST.BY) marking against this unit
DX/RP/21 |  | Served space | Room served | PLC 8 / IDF ROOF PLANT | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/RP/21 |  | Served space | Room design temperature | 35 | degC | 35 | unit:DEG_C |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/RP/21 |  | Served space | Room design relative humidity | 50 | % | 50 | unit:PERCENT_RH |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/RP/21 |  | Served space | Room cooling load | 6 | kW | 6 | unit:KiloW |  |  | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Room load printed on the room box, not a per-unit capacity; the schematic does not say whether this is total or sensible
DX/RP/21 |  | Refrigeration | Matched condensing unit | DX/OD/21 | [5 empty] | reference | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Paired by matching number, not stated on the drawing
DX/RP/21 |  | Data quality | Model not stated | This unit is on the schematic but not on SYSTEM DETAILS Table 3.6, which stops at DX/B/16. No indoor or outdoor model is available for it. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/01 |  | Data quality | Source reference | Read off a schematic riser supplied as an image, not from a schedule. No drawing number, sheet or revision is recorded. Ask for the sheet reference before handover. | [6 empty] | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Applies to the whole schematic
DX/B/01 |  | Data quality | Cooling figure is a room load | Each cooling figure is printed on the room box, not on an indoor unit. Where a room is served by two or three units the schematic does not say how the load divides, so the figure is recorded against every unit serving that room as a room load. Do not write it as a per-unit brick:coolingCapacity without the equipment schedule. | [6 empty] | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Applies to the whole schematic
DX/B/01 |  | Data quality | Indoor to outdoor pairing - superseded | The schematic numbers condensers to match their indoor units, which suggested DX/B/nn pairs with DX/OD/nn. SYSTEM DETAILS Table 3.6 shows that does not hold for every unit - five take an X2 outdoor model, meaning two condensers each. See the pairing correction note against the equipment schedule. | [6 empty] | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Applies to the whole schematic
DX/B/01 |  | Data quality | Standby marking disagreement | DX/OD/05 is marked (ST.BY) at the condenser row, but DX/B/05 carries no standby marking at the indoor row. One of the two is wrong; the drawing does not say which. Recorded as printed on each side. | [6 empty] | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Applies to the whole schematic
DX/B/01 |  | Data quality | Room design condition | Tr is the room design temperature and the paired figure is design relative humidity - 50% on every room on this schematic. | [6 empty] | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Applies to the whole schematic
DX/B/01 |  | Data quality | Drainage | The trash chamber units carry the note 'TO NEAREST DRAIN, AS REFER TO PIPE WORK LAYOUT PLAN (TYPICAL)'. No condensate route is scheduled on this drawing. | [6 empty] | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Applies to the whole schematic
DX/B/01 |  | Data quality | Scope | The schematic states no model, no make, no electrical data and no air flow for any DX unit. Those were not inferred - the equipment schedule is still needed. | [6 empty] | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC | Applies to the whole schematic
DX/B/01 |  | Data quality | Pairing correction | The schematic numbers condensers to match their indoor units, and this workbook previously recorded DX/B/nn as paired one-to-one with DX/OD/nn on that basis. Table 3.6 shows that is not right for every unit: DX/B/03, 04 and 14 each take a PUHZ-RP200X2 and DX/B/08 and 09 each take a PUHZ-RP250X2, where the X2 suffix means two condensers per indoor unit. Those five units need two DX/OD tags each, and the schematic's numbering does not say which two. The pipework layout plan is still needed. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Applies to the DX set
DX/B/01 |  | Data quality | Schedule is partial | Table 3.6 covers DX/B/01 to DX/B/16. DX/B/17, 18, 19, 20 and DX/RP/21 are on the schematic but not on this schedule, so they still carry no model. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Applies to the DX set
DX/B/01 |  | Data quality | Location granularity | Table 3.6 writes 'MV Room, HV Room' for DX/B/01, 02, 05, 06, 07 and 16, where the schematic separates MV ROOM (01, 02), HV ROOM (05, 06) and MV ROOM 3 (07, 16). The two do not conflict - the schedule is simply coarser. The schematic's room is kept as the served space and the schedule's text is recorded alongside it. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Applies to the DX set
DX/B/01 |  | Data quality | Probable typo | DX/B/08 reads PUHZ-RP2S0X2. DX/B/09 has the same indoor unit in the same room and reads PUHZ-RP250X2, so the 'S' is almost certainly a misprint for '5'. Recorded as printed; confirm before ordering. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Applies to the DX set
DX/B/01 |  | Data quality | Manufacturer not stated | The PEAD, PCA and PUHZ prefixes are Mitsubishi Electric Mr. Slim naming, but Table 3.6 has no manufacturer column and no other document supplied names one. No manufacturer property was created from the model prefix alone. | [6 empty] | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Applies to the DX set

## Ontology Scope
Ontology Scope
Which transcribed properties belong in the ontology. Targets are the predicates Dar Cairo, QF SSC and QF HQ actually use for equipment metadata - about twenty in total. Everything else is engineering reference, kept but not modelled.
Scope | Ontology predicate | Predicate source | Component | Property | Rows | Sheets
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Capacity | Total capacity (cooling) | 28 | FCU
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Construction | Duty | 5 | Heat Exchangers
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Cooling coil | Total capacity | 15 | AHU
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | External auxiliary cooling coil | Total capacity | 1 | AHU
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Thermal specification | Heat exchanged | 1 | Heat Exchangers
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Unit performance | Total cooling capacity | 5 | Closed Control Units
core | brick:operationalStageCount | Brick 1.4 - not yet used by any reference model | Air | Number of speeds | 16 | DX Units
core | brick:ratedCurrentInput | Brick 1.4 - not yet used by any reference model | Return fan drive motor | Full load current | 7 | AHU
core | brick:ratedCurrentInput | Brick 1.4 - not yet used by any reference model | Supply fan drive motor | Full load current | 15 | AHU
core | brick:ratedPowerInput | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Drive motor | Motor size | 4 | Pumps
core | brick:ratedPowerInput | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Other data | Max. absorbed power | 28 | FCU
core | brick:ratedPowerInput | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Return fan drive motor | Rating | 7 | AHU
core | brick:ratedPowerInput | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Supply fan drive motor | Rating | 15 | AHU
core | brick:ratedPowerInput | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Unit performance | Unit power input | 5 | Closed Control Units
core | para:Rated_Tank_Level | para: - Dar Cairo 3; brick:volume would outrank it by the ladder | Expansion tank | Capacity | 1 | Pressurization Unit
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | CHW flow rate | Cold side | 4 | Heat Exchangers
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | CW coil | Unit fluid flow | 1 | Closed Control Units
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | Cooling coil | Water flow | 15 | AHU
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | Design condition | Unit fluid flow | 1 | Closed Control Units
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | External auxiliary cooling coil | Water flow | 1 | AHU
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | Fluid | Flow rate | 28 | FCU
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | Performance | CHW flow rate | 4 | Pumps
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | Pump design | Duty flow | 4 | Pumps
core | para:ratedExhaustAirFlowrate | para: - Dar Cairo 18 (Brick has no air flowrate) | Air | Air flow | 35 | Exhaust Fans
core | para:ratedExhaustAirFlowrate | para: - Dar Cairo 18 (Brick has no air flowrate) | Return fan | Air flow | 7 | AHU
core | para:ratedHead | para: - Dar Cairo 41 (Brick has no head) | Pump design | Duty head | 4 | Pumps
core | para:ratedReheatCapacity | para: - SSC 108, HQ 602 (Brick has no reheat capacity) | Electric coil | Total capacity | 15 | AHU
core | para:ratedReheatCapacity | para: - SSC 108, HQ 602 (Brick has no reheat capacity) | Heating | Heating capacity | 113 | VAV Units
core | para:ratedReheatCapacity | para: - SSC 108, HQ 602 (Brick has no reheat capacity) | Option - electrical re-heating | Max re-heating capacity | 5 | Closed Control Units
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Drive motor | Motor speed | 4 | Pumps
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Return fan | Speed | 7 | AHU
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Return fan drive motor | Full load speed | 7 | AHU
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Supply fan | Speed | 15 | AHU
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Supply fan drive motor | Full load speed | 15 | AHU
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Technical data | Speed | 1 | Climate Control Units
core | para:ratedSupplyAirFlowrate | para: - Dar Cairo 81, SSC 113, HQ 628 (Brick has no air flowrate) | Air | Air flow (per box) | 243 | CAV Units, VAV Units
core | para:ratedSupplyAirFlowrate | para: - Dar Cairo 81, SSC 113, HQ 628 (Brick has no air flowrate) | Air | Flow rate | 28 | FCU
core | para:ratedSupplyAirFlowrate | para: - Dar Cairo 81, SSC 113, HQ 628 (Brick has no air flowrate) | Design condition | Unit airflow | 5 | Closed Control Units
core | para:ratedSupplyAirFlowrate | para: - Dar Cairo 81, SSC 113, HQ 628 (Brick has no air flowrate) | Supply fan | Air flow | 15 | AHU
core | para:ratedWaterFlowrate | para: - Dar Cairo 34 (Brick has no water flowrate) | CHW flow rate | Hot side | 4 | Heat Exchangers
core | para:refrigerant | para: - Dar Cairo 2 | Design condition | Refrigerant | 4 | Closed Control Units
core | rec:installationDate | REC - Dar Cairo 494 | Maintenance | Date installed | 1 | Generators
core | rec:manufacturedBy | REC - Dar Cairo 449, SSC 7, HQ 42 | Expansion tank | Make | 1 | Pressurization Unit
core | rec:manufacturedBy | REC - Dar Cairo 449, SSC 7, HQ 42 | Identification | Make | 163 | CAV Units, Heat Exchangers, Pressurization Unit, Pumps, VAV Units
core | rec:manufacturedBy | REC - Dar Cairo 449, SSC 7, HQ 42 | Identification | Manufacturer | 73 | Climate Control Units, Closed Control Units, Exhaust Fans, FCU, Generators
core | rec:manufacturedBy | REC - Dar Cairo 449, SSC 7, HQ 42 | Pressurisation unit | Make | 1 | Pressurization Unit
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Cooling coil | Model | 15 | AHU
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Expansion tank | Model | 1 | Pressurization Unit
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Identification | Indoor unit model | 16 | DX Units
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Identification | Model | 176 | CAV Units, Climate Control Units, Closed Control Units, Exhaust Fans, FCU, Heat Exchangers, Pressurization Unit, Pumps, VAV Units
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Identification | Model number | 1 | Generators
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Pressurisation unit | Model | 1 | Pressurization Unit
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Refrigeration | Outdoor unit model | 16 | DX Units
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Return fan | Fan model | 7 | AHU
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Supply fan | Fan model | 15 | AHU
reference |  |  | Air | Air pressure drop | 28 | FCU
reference |  |  | Air | Air velocity | 28 | FCU
reference |  |  | Air | Fan speed setting | 28 | FCU
reference |  |  | Air | Inlet DBT | 28 | FCU
reference |  |  | Air | Inlet RH | 28 | FCU
reference |  |  | Air | Inlet WBT | 28 | FCU
reference |  |  | Air | Outlet DBT | 28 | FCU
reference |  |  | Air | Outlet RH | 28 | FCU
reference |  |  | Air | Outlet WBT | 28 | FCU
reference |  |  | Application | Application | 1 | Climate Control Units
reference |  |  | Asset register | Equipment name | 1 | Generators
reference |  |  | Asset register | Location info | 1 | Generators
reference |  |  | Asset register | Main category | 1 | Generators
reference |  |  | Asset register | Quantity | 1 | Generators
reference |  |  | Asset register | Sub category | 1 | Generators
reference |  |  | CW coil | Fluid pressure drop coil + connections | 1 | Closed Control Units
reference |  |  | CW coil | Quantity | 1 | Closed Control Units
reference |  |  | CW coil | Unit fluid side pressure drop | 1 | Closed Control Units
reference |  |  | CW coil | Valve pressure drop | 1 | Closed Control Units
reference |  |  | Capacity | Condensed water | 27 | FCU
reference |  |  | Capacity | Heating capacity | 28 | FCU
reference |  |  | Capacity | Sensible capacity (cooling) | 28 | FCU
reference |  |  | Coil | Rows | 28 | FCU
reference |  |  | Compliance | Declared performance / directives | 5 | Closed Control Units
reference |  |  | Compressors | Compressors COP | 4 | Closed Control Units
reference |  |  | Compressors | Full load ampere | 4 | Closed Control Units
reference |  |  | Compressors | Locked rotor amp. | 4 | Closed Control Units
reference |  |  | Compressors | Operating ampere | 4 | Closed Control Units
reference |  |  | Compressors | Power input | 4 | Closed Control Units
reference |  |  | Compressors | Power supply | 4 | Closed Control Units
reference |  |  | Compressors | Quantity | 4 | Closed Control Units
reference |  |  | Condenser | Actual outdoor SPL (@ 5 m, f.f.) | 4 | Closed Control Units
reference |  |  | Condenser | Air discharge | 4 | Closed Control Units
reference |  |  | Condenser | Condenser ESP (@ max speed) | 4 | Closed Control Units
reference |  |  | Condenser | Condenser actual airflow | 4 | Closed Control Units
reference |  |  | Condenser | Condenser airflow (@ max speed) | 4 | Closed Control Units
reference |  |  | Condenser | Condenser model | 4 | Closed Control Units
reference |  |  | Condenser | Depth | 4 | Closed Control Units
reference |  |  | Condenser | Full load ampere | 4 | Closed Control Units
reference |  |  | Condenser | Heat load | 4 | Closed Control Units
reference |  |  | Condenser | Height | 4 | Closed Control Units
reference |  |  | Condenser | Locked rotor amp. | 4 | Closed Control Units
reference |  |  | Condenser | Max outdoor SPL (@ 5 m, f.f.) | 4 | Closed Control Units
reference |  |  | Condenser | Note | 1 | Closed Control Units
reference |  |  | Condenser | Outdoor air temperature | 4 | Closed Control Units
reference |  |  | Condenser | Power input | 4 | Closed Control Units
reference |  |  | Condenser | Power supply | 4 | Closed Control Units
reference |  |  | Condenser | Variex | 4 | Closed Control Units
reference |  |  | Condenser | Version | 4 | Closed Control Units
reference |  |  | Condenser | Weight | 4 | Closed Control Units
reference |  |  | Condenser | Width | 4 | Closed Control Units
reference |  |  | Construction | Effective heat transfer area | 5 | Heat Exchangers
reference |  |  | Construction | Item reference | 5 | Heat Exchangers
reference |  |  | Construction | Net weight, empty | 5 | Heat Exchangers
reference |  |  | Construction | Net weight, operating | 5 | Heat Exchangers
reference |  |  | Construction | Number of plates | 5 | Heat Exchangers
reference |  |  | Construction | Overall dimensions per PHE (L x W x H) | 5 | Heat Exchangers
reference |  |  | Construction | Overall heat transfer coefficient | 5 | Heat Exchangers
reference |  |  | Construction | Packed dimensions per PHE (L x W x H) | 5 | Heat Exchangers
reference |  |  | Construction | Packed weight per PHE | 5 | Heat Exchangers
reference |  |  | Construction | Plate material | 5 | Heat Exchangers
reference |  |  | Construction | Plate thickness | 5 | Heat Exchangers
reference |  |  | Control wiring | Black | 1 | Climate Control Units
reference |  |  | Control wiring | Blue | 1 | Climate Control Units
reference |  |  | Control wiring | Green | 1 | Climate Control Units
reference |  |  | Control wiring | Grey | 1 | Climate Control Units
reference |  |  | Control wiring | Modes | 1 | Climate Control Units
reference |  |  | Control wiring | Red | 1 | Climate Control Units
reference |  |  | Control wiring | White | 1 | Climate Control Units
reference |  |  | Cooling coil | Binder tapping points | 15 | AHU
reference |  |  | Cooling coil | Casing | 15 | AHU
reference |  |  | Cooling coil | Connection return | 15 | AHU
reference |  |  | Cooling coil | Connection supply | 15 | AHU
reference |  |  | Cooling coil | Connection type | 15 | AHU
reference |  |  | Cooling coil | Drain connection | 15 | AHU
reference |  |  | Cooling coil | Drain pan | 15 | AHU
reference |  |  | Cooling coil | Entering air (DB) | 15 | AHU
reference |  |  | Cooling coil | Entering air RH | 15 | AHU
reference |  |  | Cooling coil | Entering water | 15 | AHU
reference |  |  | Cooling coil | Fin spacing | 15 | AHU
reference |  |  | Cooling coil | Fins | 15 | AHU
reference |  |  | Cooling coil | Glycol | 15 | AHU
reference |  |  | Cooling coil | Glycol type | 15 | AHU
reference |  |  | Cooling coil | Leaving air (DB) | 15 | AHU
reference |  |  | Cooling coil | Leaving air RH | 15 | AHU
reference |  |  | Cooling coil | Leaving water | 15 | AHU
reference |  |  | Cooling coil | Moisture eliminator | 15 | AHU
reference |  |  | Cooling coil | Note | 9 | AHU
reference |  |  | Cooling coil | Rows | 15 | AHU
reference |  |  | Cooling coil | Tubes | 15 | AHU
reference |  |  | Cooling coil | Water pressure drop | 15 | AHU
reference |  |  | Design condition | Cold side temperature | 5 | Heat Exchangers
reference |  |  | Design condition | ESP | 5 | Closed Control Units
reference |  |  | Design condition | Fluid | 1 | Closed Control Units
reference |  |  | Design condition | Hot side temperature | 5 | Heat Exchangers
reference |  |  | Design condition | Inlet fluid temperature | 1 | Closed Control Units
reference |  |  | Design condition | Outlet fluid temperature | 1 | Closed Control Units
reference |  |  | Design condition | Sea level | 5 | Closed Control Units
reference |  |  | Design condition | Unit inlet air relative humidity | 5 | Closed Control Units
reference |  |  | Design condition | Unit inlet air temperature | 5 | Closed Control Units
reference |  |  | Design condition | Unit power supply | 5 | Closed Control Units
reference |  |  | Dimension drawing | Date | 1 | Climate Control Units
reference |  |  | Dimension drawing | Drawn by | 1 | Climate Control Units
reference |  |  | Dimension drawing | Dwg no | 1 | Climate Control Units
reference |  |  | Dimension drawing | Front view height | 1 | Climate Control Units
reference |  |  | Dimension drawing | Front view width | 1 | Climate Control Units
reference |  |  | Dimension drawing | Plan view depth | 1 | Climate Control Units
reference |  |  | Dimension drawing | Rev | 1 | Climate Control Units
reference |  |  | Dimension drawing | Scale | 1 | Climate Control Units
reference |  |  | Dimension drawing | Side view height | 1 | Climate Control Units
reference |  |  | Dimension drawing | Side view width | 1 | Climate Control Units
reference |  |  | Dimension drawing | Size | 1 | Climate Control Units
reference |  |  | Dimensional data | Configuration code | 4 | Pumps
reference |  |  | Dimensional data | D | 4 | Pumps
reference |  |  | Dimensional data | HA | 4 | Pumps
reference |  |  | Dimensional data | HB | 4 | Pumps
reference |  |  | Dimensional data | HC | 4 | Pumps
reference |  |  | Dimensional data | HD | 4 | Pumps
reference |  |  | Dimensional data | HE | 4 | Pumps
reference |  |  | Dimensional data | HF | 4 | Pumps
reference |  |  | Dimensional data | HG | 4 | Pumps
reference |  |  | Dimensional data | HL | 4 | Pumps
reference |  |  | Dimensional data | HM | 4 | Pumps
reference |  |  | Dimensional data | HO | 4 | Pumps
reference |  |  | Dimensional data | HP | 4 | Pumps
reference |  |  | Dimensional data | S | 4 | Pumps
reference |  |  | Dimensional data | SD | 4 | Pumps
reference |  |  | Dimensional data | Weight | 4 | Pumps
reference |  |  | Dimensions | Body od | 1 | Climate Control Units
reference |  |  | Dimensions | Bolt circle | 1 | Climate Control Units
reference |  |  | Dimensions | Depth | 1 | Climate Control Units
reference |  |  | Dimensions | Flange od | 1 | Climate Control Units
reference |  |  | Dimensions | Height | 1 | Climate Control Units
reference |  |  | Dimensions | Hub | 1 | Climate Control Units
reference |  |  | Dimensions | Mounting | 1 | Climate Control Units
reference |  |  | Dimensions | Width across | 1 | Climate Control Units
reference |  |  | Dimensions and weight | Max height | 28 | FCU
reference |  |  | Dimensions and weight | Max thickness | 28 | FCU
reference |  |  | Dimensions and weight | Max width | 28 | FCU
reference |  |  | Dimensions and weight | Operating weight | 4 | Heat Exchangers
reference |  |  | Dimensions and weight | Unit dimension (L x W x H) | 8 | Heat Exchangers, Pumps
reference |  |  | Dimensions and weight | Weight | 32 | FCU, Pumps
reference |  |  | Drawing | Drawing number | 15 | AHU
reference |  |  | Drawing | Sheet | 15 | AHU
reference |  |  | Drive motor | Insulation class | 4 | Pumps
reference |  |  | Drive motor | Inverter motor type | 4 | Pumps
reference |  |  | Drive motor | Motor efficiency class | 4 | Pumps
reference |  |  | Drive motor | Motor enclosure | 4 | Pumps
reference |  |  | Drive motor | Motor frame number | 4 | Pumps
reference |  |  | Drive motor | Motor supplier | 4 | Pumps
reference |  |  | Drive motor | Power supply | 4 | Pumps
reference |  |  | Electric coil | Electrical supply | 15 | AHU
reference |  |  | Electric coil | Entering air | 15 | AHU
reference |  |  | Electric coil | Leaving air | 15 | AHU
reference |  |  | Electric coil | Note | 15 | AHU
reference |  |  | Electric coil | Stages | 15 | AHU
reference |  |  | Expansion tank | Quantity | 1 | Pressurization Unit
reference |  |  | External auxiliary cooling coil | Air flow | 1 | AHU
reference |  |  | External auxiliary cooling coil | Air mass flow | 1 | AHU
reference |  |  | External auxiliary cooling coil | Air pressure drop | 1 | AHU
reference |  |  | External auxiliary cooling coil | Description | 1 | AHU
reference |  |  | External auxiliary cooling coil | Entering air | 1 | AHU
reference |  |  | External auxiliary cooling coil | Entering air RH | 1 | AHU
reference |  |  | External auxiliary cooling coil | Entering water | 1 | AHU
reference |  |  | External auxiliary cooling coil | Leaving air | 1 | AHU
reference |  |  | External auxiliary cooling coil | Leaving air RH | 1 | AHU
reference |  |  | External auxiliary cooling coil | Leaving water | 1 | AHU
reference |  |  | External auxiliary cooling coil | Tubes | 1 | AHU
reference |  |  | External auxiliary cooling coil | Water mass flow | 1 | AHU
reference |  |  | External auxiliary cooling coil | Water pressure drop | 1 | AHU
reference |  |  | Fans | Fan input voltage | 5 | Closed Control Units
reference |  |  | Fans | Full load ampere | 5 | Closed Control Units
reference |  |  | Fans | Locked rotor amp. | 5 | Closed Control Units
reference |  |  | Fans | Operating ampere | 5 | Closed Control Units
reference |  |  | Fans | Power input | 5 | Closed Control Units
reference |  |  | Fans | Power supply | 5 | Closed Control Units
reference |  |  | Fans | Quantity | 5 | Closed Control Units
reference |  |  | Fans | Type | 5 | Closed Control Units
reference |  |  | Feature | Feature 1 | 2 | Climate Control Units
reference |  |  | Feature | Feature 2 | 2 | Climate Control Units
reference |  |  | Feature | Feature 3 | 1 | Climate Control Units
reference |  |  | Feature | Feature 4 | 1 | Climate Control Units
reference |  |  | Feature | Feature 5 | 1 | Climate Control Units
reference |  |  | Feature | Feature 6 | 1 | Climate Control Units
reference |  |  | Filtration stages | Primary | 1 | Climate Control Units
reference |  |  | Filtration stages | Secondary | 1 | Climate Control Units
reference |  |  | Filtration stages | Tertiary | 1 | Climate Control Units
reference |  |  | Finish | Extract fan base | 15 | AHU
reference |  |  | Finish | Frames | 15 | AHU
reference |  |  | Finish | Panels inner skin | 15 | AHU
reference |  |  | Finish | Panels inner skin at coil section | 15 | AHU
reference |  |  | Finish | Panels outer skin | 15 | AHU
reference |  |  | Finish | Supply fan base | 15 | AHU
reference |  |  | Finish | Unit base | 15 | AHU
reference |  |  | Flexible connection | Material | 15 | AHU
reference |  |  | Fluid | Fluid | 28 | FCU
reference |  |  | Fluid | Inlet temperature | 28 | FCU
reference |  |  | Fluid | Outlet temperature | 28 | FCU
reference |  |  | Fluid | Pressure drop | 28 | FCU
reference |  |  | Identification | Alternate reference | 5 | Pressurization Unit, Pumps
reference |  |  | Identification | Dimension drawing pages | 1 | Closed Control Units
reference |  |  | Identification | Document status | 1 | Climate Control Units
reference |  |  | Identification | Duty or standby | 30 | DX Units, Heat Exchangers, Pumps
reference |  |  | Identification | Equipment type | 3 | Climate Control Units
reference |  |  | Identification | Issued by | 5 | Closed Control Units
reference |  |  | Identification | Level | 21 | DX Units
reference |  |  | Identification | Location | 9 | Heat Exchangers, Pressurization Unit, Pumps
reference |  |  | Identification | Location (equipment schedule) | 16 | DX Units
reference |  |  | Identification | Offer | 28 | FCU
reference |  |  | Identification | Quantity | 9 | Heat Exchangers, Pressurization Unit, Pumps
reference |  |  | Identification | Range | 28 | FCU
reference |  |  | Identification | Selection date | 5 | Closed Control Units
reference |  |  | Identification | Selection software release | 5 | Closed Control Units
reference |  |  | Identification | Serial number | 1 | Generators
reference |  |  | Identification | System type | 5 | Closed Control Units
reference |  |  | Identification | Type | 8 | Heat Exchangers, Pumps
reference |  |  | Identification | Version | 28 | FCU
reference |  |  | Installation | Clearance | 1 | Climate Control Units
reference |  |  | Installation | Mounting | 1 | Climate Control Units
reference |  |  | Installation requirement | Installation requirement 1 | 1 | Climate Control Units
reference |  |  | Installation requirement | Installation requirement 2 | 1 | Climate Control Units
reference |  |  | Installation requirement | Installation requirement 3 | 1 | Climate Control Units
reference |  |  | Installation requirement | Installation requirement 4 | 1 | Climate Control Units
reference |  |  | Installation requirement | Installation requirement 5 | 1 | Climate Control Units
reference |  |  | Installation requirement | Installation requirement 6 | 1 | Climate Control Units
reference |  |  | Installation requirement | Installation requirement 7 | 1 | Climate Control Units
reference |  |  | Installation requirement | Installation requirement 8 | 1 | Climate Control Units
reference |  |  | Insulation | Panels | 15 | AHU
reference |  |  | Location | Building name | 1 | Generators
reference |  |  | Location | Floor | 1 | Generators
reference |  |  | Location | Room no. | 1 | Generators
reference |  |  | Maintenance | PM procedure description | 1 | Generators
reference |  |  | Maintenance | Procedure document | 1 | Generators
reference |  |  | Maintenance | Recommended spare parts | 1 | Generators
reference |  |  | Materials of construction | Bearings | 4 | Pumps
reference |  |  | Materials of construction | Casing gasket | 4 | Pumps
reference |  |  | Materials of construction | Construction | 4 | Pumps
reference |  |  | Materials of construction | Flexible couplings | 4 | Pumps
reference |  |  | Materials of construction | Flush line | 4 | Pumps
reference |  |  | Materials of construction | Hydrostatic test | 4 | Pumps
reference |  |  | Materials of construction | Impeller | 4 | Pumps
reference |  |  | Materials of construction | Pump casing | 4 | Pumps
reference |  |  | Materials of construction | Pump shaft | 4 | Pumps
reference |  |  | Materials of construction | Pump suction | 4 | Pumps
reference |  |  | Materials of construction | Rating | 4 | Pumps
reference |  |  | Materials of construction | Shaft sleeve | 4 | Pumps
reference |  |  | Materials of construction | Size | 4 | Pumps
reference |  |  | Materials of construction | Suction/discharge flange | 4 | Pumps
reference |  |  | Mechanical seal | Fluid type | 4 | Pumps
reference |  |  | Mechanical seal | Manufacturer | 4 | Pumps
reference |  |  | Mechanical seal | Manufacturer code | 4 | Pumps
reference |  |  | Mechanical seal | Rotating face | 4 | Pumps
reference |  |  | Mechanical seal | Rotating hardware | 4 | Pumps
reference |  |  | Mechanical seal | Seal | 4 | Pumps
reference |  |  | Mechanical seal | Seal type | 4 | Pumps
reference |  |  | Mechanical seal | Secondary seal | 4 | Pumps
reference |  |  | Mechanical seal | Springs | 4 | Pumps
reference |  |  | Mechanical seal | Stationary seat | 4 | Pumps
reference |  |  | Note | Note | 1 | Climate Control Units
reference |  |  | Note | Sheet note | 3 | Closed Control Units
reference |  |  | Option - electrical re-heating | FLA | 5 | Closed Control Units
reference |  |  | Option - electrical re-heating | Inlet air relative humidity | 5 | Closed Control Units
reference |  |  | Option - electrical re-heating | Inlet air temperature | 5 | Closed Control Units
reference |  |  | Option - electrical re-heating | Outlet air relative humidity | 5 | Closed Control Units
reference |  |  | Option - electrical re-heating | Outlet air temperature | 5 | Closed Control Units
reference |  |  | Option - electrical re-heating | Sheet heading | 1 | Closed Control Units
reference |  |  | Option - humidifier | Max absorption current | 5 | Closed Control Units
reference |  |  | Option - humidifier | Max capacity steam | 5 | Closed Control Units
reference |  |  | Option - humidifier | Min capacity steam | 5 | Closed Control Units
reference |  |  | Option - humidifier | Nominal power input | 5 | Closed Control Units
reference |  |  | Option - humidifier | Power supply | 5 | Closed Control Units
reference |  |  | Option - humidifier | Quantity | 5 | Closed Control Units
reference |  |  | Option - humidifier | Type of humidifier | 5 | Closed Control Units
reference |  |  | Options | Options | 1 | Climate Control Units
reference |  |  | Other data | Max. absorbed current | 28 | FCU
reference |  |  | Other data | Power supply | 28 | FCU
reference |  |  | Other data | Sound power level | 28 | FCU
reference |  |  | Other data | Sound pressure level | 28 | FCU
reference |  |  | Other data | Static pressure | 28 | FCU
reference |  |  | Performance | System volume (as printed) | 1 | Pressurization Unit
reference |  |  | Polyseal filter (item 1) - MAIN | Efficiency | 6 | AHU
reference |  |  | Polyseal filter (item 1) - MAIN | Media | 6 | AHU
reference |  |  | Polyseal filter (item 1) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 6 | AHU
reference |  |  | Polyseal filter (item 1) - MAIN | Spare sets | 6 | AHU
reference |  |  | Polyseal filter (item 1) - PRE | Arrestance | 6 | AHU
reference |  |  | Polyseal filter (item 1) - PRE | Media | 6 | AHU
reference |  |  | Polyseal filter (item 1) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 6 | AHU
reference |  |  | Polyseal filter (item 1) - PRE | Spare sets | 6 | AHU
reference |  |  | Polyseal filter (item 2) - MAIN | Efficiency | 8 | AHU
reference |  |  | Polyseal filter (item 2) - MAIN | Media | 8 | AHU
reference |  |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 8 | AHU
reference |  |  | Polyseal filter (item 2) - MAIN | Part no AHFL-5234200320 (W x H x D mm) | 5 | AHU
reference |  |  | Polyseal filter (item 2) - MAIN | Spare sets | 8 | AHU
reference |  |  | Polyseal filter (item 2) - PRE | Arrestance | 8 | AHU
reference |  |  | Polyseal filter (item 2) - PRE | Media | 8 | AHU
reference |  |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702001224 (W x H x D mm) | 5 | AHU
reference |  |  | Polyseal filter (item 2) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 8 | AHU
reference |  |  | Polyseal filter (item 2) - PRE | Spare sets | 8 | AHU
reference |  |  | Polyseal filter (item 6) - MAIN | Efficiency | 1 | AHU
reference |  |  | Polyseal filter (item 6) - MAIN | Media | 1 | AHU
reference |  |  | Polyseal filter (item 6) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 1 | AHU
reference |  |  | Polyseal filter (item 6) - MAIN | Part no AHFL-5234200320 (W x H x D mm) | 1 | AHU
reference |  |  | Polyseal filter (item 6) - MAIN | Spare sets | 1 | AHU
reference |  |  | Polyseal filter (item 6) - PRE | Arrestance | 1 | AHU
reference |  |  | Polyseal filter (item 6) - PRE | Media | 1 | AHU
reference |  |  | Polyseal filter (item 6) - PRE | Part no AHFL-3702001224 (W x H x D mm) | 1 | AHU
reference |  |  | Polyseal filter (item 6) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 1 | AHU
reference |  |  | Polyseal filter (item 6) - PRE | Spare sets | 1 | AHU
reference |  |  | Polyseal filter (item 7) - MAIN | Efficiency | 6 | AHU
reference |  |  | Polyseal filter (item 7) - MAIN | Media | 6 | AHU
reference |  |  | Polyseal filter (item 7) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 6 | AHU
reference |  |  | Polyseal filter (item 7) - MAIN | Part no AHFL-5234200320 (W x H x D mm) | 2 | AHU
reference |  |  | Polyseal filter (item 7) - MAIN | Spare sets | 6 | AHU
reference |  |  | Polyseal filter (item 7) - PRE | Arrestance | 6 | AHU
reference |  |  | Polyseal filter (item 7) - PRE | Media | 6 | AHU
reference |  |  | Polyseal filter (item 7) - PRE | Part no AHFL-3702001224 (W x H x D mm) | 2 | AHU
reference |  |  | Polyseal filter (item 7) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 6 | AHU
reference |  |  | Polyseal filter (item 7) - PRE | Spare sets | 6 | AHU
reference |  |  | Polyseal filter (item 8) - MAIN | Efficiency | 1 | AHU
reference |  |  | Polyseal filter (item 8) - MAIN | Media | 1 | AHU
reference |  |  | Polyseal filter (item 8) - MAIN | Part no AHFL-5234100620 (W x H x D mm) | 1 | AHU
reference |  |  | Polyseal filter (item 8) - MAIN | Spare sets | 1 | AHU
reference |  |  | Polyseal filter (item 8) - PRE | Arrestance | 1 | AHU
reference |  |  | Polyseal filter (item 8) - PRE | Media | 1 | AHU
reference |  |  | Polyseal filter (item 8) - PRE | Part no AHFL-3702002424 (W x H x D mm) | 1 | AHU
reference |  |  | Polyseal filter (item 8) - PRE | Spare sets | 1 | AHU
reference |  |  | Pressurisation unit | Capacity | 1 | Pressurization Unit
reference |  |  | Pressurisation unit | Quantity | 1 | Pressurization Unit
reference |  |  | Project | Consultant | 5 | Heat Exchangers
reference |  |  | Project | Contractor | 5 | Heat Exchangers
reference |  |  | Project | Project | 5 | Heat Exchangers
reference |  |  | Provenance | Scheduled as | 182 | CAV Units, VAV Units
reference |  |  | Pump design | Discharge | 4 | Pumps
reference |  |  | Pump design | Fluid | 4 | Pumps
reference |  |  | Pump design | Operating temperature | 4 | Pumps
reference |  |  | Pump design | Pipe orientation | 4 | Pumps
reference |  |  | Pump design | Pump run quantity | 4 | Pumps
reference |  |  | Pump design | Quantity | 4 | Pumps
reference |  |  | Pump design | Service | 4 | Pumps
reference |  |  | Pump design | Specific gravity | 4 | Pumps
reference |  |  | Pump design | Suction | 4 | Pumps
reference |  |  | Pump design | Suction pressure | 4 | Pumps
reference |  |  | Pump design | Tag num | 4 | Pumps
reference |  |  | Pump design | Viscosity | 4 | Pumps
reference |  |  | Refrigeration | Matched condensing unit | 21 | DX Units
reference |  |  | Refrigeration | Outdoor units required | 16 | DX Units
reference |  |  | Return fan | AVM type | 7 | AHU
reference |  |  | Return fan | Absorbed power | 7 | AHU
reference |  |  | Return fan | Drain plug | 7 | AHU
reference |  |  | Return fan | External static pressure | 7 | AHU
reference |  |  | Return fan | Fan pulley | 1 | AHU
reference |  |  | Return fan | Fan static pressure | 7 | AHU
reference |  |  | Return fan | Finish | 7 | AHU
reference |  |  | Return fan | Impeller type | 7 | AHU
reference |  |  | Return fan | Inlet guards | 7 | AHU
reference |  |  | Return fan | Inspection door | 7 | AHU
reference |  |  | Return fan | Shaft guards | 7 | AHU
reference |  |  | Return fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 7 | AHU
reference |  |  | Return fan | Spark minimising features | 7 | AHU
reference |  |  | Return fan | Stainless steel shaft | 7 | AHU
reference |  |  | Return fan | Volume control | 7 | AHU
reference |  |  | Return fan drive motor | Belt type | 1 | AHU
reference |  |  | Return fan drive motor | Belts | 1 | AHU
reference |  |  | Return fan drive motor | Efficiency class | 6 | AHU
reference |  |  | Return fan drive motor | Epoxy paint finish | 7 | AHU
reference |  |  | Return fan drive motor | Frame type | 7 | AHU
reference |  |  | Return fan drive motor | Motor pulley | 1 | AHU
reference |  |  | Return fan drive motor | Spare drive belts | 7 | AHU
reference |  |  | Return fan drive motor | Starting current | 7 | AHU
reference |  |  | Return fan drive motor | Starting method | 7 | AHU
reference |  |  | Return fan drive motor | Supply | 7 | AHU
reference |  |  | Return fan drive motor | Thermistor fitted | 7 | AHU
reference |  |  | Return fan drive motor | Winding type | 7 | AHU
reference |  |  | Served space | Room cooling load | 21 | DX Units
reference |  |  | Served space | Room design relative humidity | 21 | DX Units
reference |  |  | Served space | Room design temperature | 21 | DX Units
reference |  |  | Served space | Room served | 21 | DX Units
reference |  |  | Silencer (item 1) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 8 | AHU
reference |  |  | Silencer (item 1) | Silencer length | 8 | AHU
reference |  |  | Silencer (item 4) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 1 | AHU
reference |  |  | Silencer (item 4) | Silencer length | 1 | AHU
reference |  |  | Silencer (item 5) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 7 | AHU
reference |  |  | Silencer (item 5) | Silencer length | 7 | AHU
reference |  |  | Silencer (item 6) | Insertion loss (63/125/250/500/1k/2k/4k/8k Hz) | 14 | AHU
reference |  |  | Silencer (item 6) | Silencer length | 14 | AHU
reference |  |  | Specifications | Air hose connection | 1 | Climate Control Units
reference |  |  | Specifications | Average arrestance | 1 | Climate Control Units
reference |  |  | Specifications | Capacity | 1 | Climate Control Units
reference |  |  | Specifications | Filter case dimension | 1 | Climate Control Units
reference |  |  | Specifications | Filter dimension | 1 | Climate Control Units
reference |  |  | Specifications | Final resistance | 1 | Climate Control Units
reference |  |  | Specifications | Gac alumina wts per sqft | 1 | Climate Control Units
reference |  |  | Specifications | Hose connections | 1 | Climate Control Units
reference |  |  | Specifications | Initial resistance | 1 | Climate Control Units
reference |  |  | Specifications | Intake air filter | 1 | Climate Control Units
reference |  |  | Specifications | Nominal thickness | 1 | Climate Control Units
reference |  |  | Specifications | Operating temp | 1 | Climate Control Units
reference |  |  | Specifications | Particulates capacity | 1 | Climate Control Units
reference |  |  | Specifications | Power | 1 | Climate Control Units
reference |  |  | Specifications | Power consumption | 1 | Climate Control Units
reference |  |  | Specifications | Size | 1 | Climate Control Units
reference |  |  | Specifications | Tolerance | 1 | Climate Control Units
reference |  |  | Specifications | Water feed | 1 | Climate Control Units
reference |  |  | Specifications | Weight | 2 | Climate Control Units
reference |  |  | Specifications | Weight note | 1 | Climate Control Units
reference |  |  | Submittal | Project location | 4 | Pumps
reference |  |  | Submittal | Project name | 4 | Pumps
reference |  |  | Submittal | Project number | 4 | Pumps
reference |  |  | Submittal | Reference | 4 | Pumps
reference |  |  | Submittal | Representative | 4 | Pumps
reference |  |  | Submittal | Submitted by | 4 | Pumps
reference |  |  | Submittal | Type | 4 | Pumps
reference |  |  | Supply fan | AVM type | 15 | AHU
reference |  |  | Supply fan | Absorbed power | 15 | AHU
reference |  |  | Supply fan | Drain plug | 15 | AHU
reference |  |  | Supply fan | External static pressure | 15 | AHU
reference |  |  | Supply fan | Fan pulley | 6 | AHU
reference |  |  | Supply fan | Fan static pressure | 15 | AHU
reference |  |  | Supply fan | Finish | 15 | AHU
reference |  |  | Supply fan | Impeller type | 15 | AHU
reference |  |  | Supply fan | Inlet guards | 15 | AHU
reference |  |  | Supply fan | Inspection door | 15 | AHU
reference |  |  | Supply fan | Note | 1 | AHU
reference |  |  | Supply fan | Shaft guards | 15 | AHU
reference |  |  | Supply fan | Sound power level (63/125/250/500/1k/2k/4k/8k Hz) | 15 | AHU
reference |  |  | Supply fan | Spark minimising features | 15 | AHU
reference |  |  | Supply fan | Stainless steel shaft | 15 | AHU
reference |  |  | Supply fan | Volume control | 15 | AHU
reference |  |  | Supply fan drive motor | Belt type | 6 | AHU
reference |  |  | Supply fan drive motor | Belts | 4 | AHU
reference |  |  | Supply fan drive motor | Efficiency class | 11 | AHU
reference |  |  | Supply fan drive motor | Epoxy paint finish | 15 | AHU
reference |  |  | Supply fan drive motor | Frame type | 15 | AHU
reference |  |  | Supply fan drive motor | Motor pulley | 6 | AHU
reference |  |  | Supply fan drive motor | Spare drive belts | 15 | AHU
reference |  |  | Supply fan drive motor | Starting current | 15 | AHU
reference |  |  | Supply fan drive motor | Starting method | 15 | AHU
reference |  |  | Supply fan drive motor | Supply | 15 | AHU
reference |  |  | Supply fan drive motor | Thermistor fitted | 15 | AHU
reference |  |  | Supply fan drive motor | Winding type | 15 | AHU
reference |  |  | System included | System included 1 | 1 | Climate Control Units
reference |  |  | System included | System included 2 | 1 | Climate Control Units
reference |  |  | System included | System included 3 | 1 | Climate Control Units
reference |  |  | System included | System included 4 | 1 | Climate Control Units
reference |  |  | System included | System included 5 | 1 | Climate Control Units
reference |  |  | Technical data | Bearing life | 1 | Climate Control Units
reference |  |  | Technical data | Electronics | 1 | Climate Control Units
reference |  |  | Technical data | Input current | 1 | Climate Control Units
reference |  |  | Technical data | Input voltage | 1 | Climate Control Units
reference |  |  | Technical data | Motor rating | 1 | Climate Control Units
reference |  |  | Technical data | Permissible ambient | 1 | Climate Control Units
reference |  |  | Technical data | Speed control range | 1 | Climate Control Units
reference |  |  | Technical data | Spl | 1 | Climate Control Units
reference |  |  | Technical data | Total pressure difference pressure | 1 | Climate Control Units
reference |  |  | Technical data | Total pressure difference vacuum | 1 | Climate Control Units
reference |  |  | Technical data | Weight | 1 | Climate Control Units
reference |  |  | Thermal specification | Customer | 1 | Heat Exchangers
reference |  |  | Thermal specification | Flange rating | 1 | Heat Exchangers
reference |  |  | Thermal specification | Item | 1 | Heat Exchangers
reference |  |  | Thermal specification | L.M.T.D. | 1 | Heat Exchangers
reference |  |  | Thermal specification | Overall length x width x height | 1 | Heat Exchangers
reference |  |  | Thermal specification | Plate material / thickness | 1 | Heat Exchangers
reference |  |  | Thermal specification | Pressure vessel code | 1 | Heat Exchangers
reference |  |  | Thermal specification | Project | 1 | Heat Exchangers
reference |  |  | Thermal specification | Relative directions of fluids | 1 | Heat Exchangers
reference |  |  | Thermal specification | Specification date | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Connection diameter | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Density | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Design pressure | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Design temperature | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Fluid | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Inlet temperature | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Nozzle orientation | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Number of passes | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Outlet temperature | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Pressure drop | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Sealing material | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Specific heat capacity | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Test pressure | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Thermal conductivity | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Viscosity inlet | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Viscosity outlet | 1 | Heat Exchangers
reference |  |  | Thermal specification - cold side | Volume flow rate | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Connection diameter | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Density | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Design pressure | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Design temperature | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Fluid | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Inlet temperature | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Nozzle orientation | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Number of passes | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Outlet temperature | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Pressure drop | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Sealing material | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Specific heat capacity | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Test pressure | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Thermal conductivity | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Viscosity inlet | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Viscosity outlet | 1 | Heat Exchangers
reference |  |  | Thermal specification - hot side | Volume flow rate | 1 | Heat Exchangers
reference |  |  | Unit performance | Condensing temperature | 4 | Closed Control Units
reference |  |  | Unit performance | Depth | 5 | Closed Control Units
reference |  |  | Unit performance | Height | 5 | Closed Control Units
reference |  |  | Unit performance | Internal filter class (EN779 std) | 5 | Closed Control Units
reference |  |  | Unit performance | Off coil air relative humidity | 5 | Closed Control Units
reference |  |  | Unit performance | Off coil air temperature | 5 | Closed Control Units
reference |  |  | Unit performance | Room SPL (@ 2 m, f.f) | 5 | Closed Control Units
reference |  |  | Unit performance | SHR | 5 | Closed Control Units
reference |  |  | Unit performance | Sensible cooling capacity | 5 | Closed Control Units
reference |  |  | Unit performance | System EER | 4 | Closed Control Units
reference |  |  | Unit performance | System power input | 4 | Closed Control Units
reference |  |  | Unit performance | Unit EER | 5 | Closed Control Units
reference |  |  | Unit performance | Weight | 5 | Closed Control Units
reference |  |  | Unit performance | Width | 5 | Closed Control Units
reference |  |  | Warranty | Warranty | 2 | Climate Control Units, Generators
reference |  |  | Warranty | Warranty expires | 1 | Generators
reference |  |  | Warranty | Warranty notes | 1 | Generators

## Units
Units
Source unit to Dar Cairo unit. Targets read off reference-models/DarCairo_V93.csv - air and water flow both land on unit:L-PER-SEC, power on unit:KiloW, length on unit:M.
Unit (as printed) | Unit (QUDT) | Factor applied | Used in Dar Cairo | Dar Cairo uses (rows) | Note
kW | unit:KiloW | x 1 | yes | 1593
W | unit:KiloW | / 1000 | yes | 1593 | W / 1000
A | unit:A | x 1 | yes | 227
V | unit:V | x 1 | yes | 451
V DC | unit:V | x 1 | yes | 451 | DC noted in the property name
Hz | unit:HZ | x 1 | yes | 61
degC | unit:DEG_C | x 1 | yes | 883
m3/s | unit:L-PER-SEC | x 1000 | yes | 535 | m3/s x 1000
m3/h | unit:L-PER-SEC | / 3.6 | yes | 535 | m3/h / 3.6
l/h | unit:L-PER-SEC | / 3600 | yes | 535 | l/h / 3600
l/s | unit:L-PER-SEC | x 1 | yes | 535
kg/s | unit:L-PER-SEC | x 1 | yes | 535 | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference
Pa | unit:PA | x 1 | yes | 172
kPa | unit:PA | x 1000 | yes | 172 | kPa x 1000
mbar | unit:PA | x 100 | yes | 172 | mbar x 100
bar | unit:BAR | x 1 | yes
psig | unit:PA | x 6894.76 | yes | 172 | psi x 6894.757; the submittal states it as gauge pressure
mm | unit:M | / 1000 | yes | 47 | mm / 1000
m | unit:M | x 1 | yes | 47
in | unit:M | / 39.3701 | yes | 47 | in x 0.0254
m2 | unit:M2 | x 1 | yes | 755
litre | unit:L | x 1 | NO
rpm | unit:RPM | x 1 | yes | 21
hours | unit:HR | x 1 | yes | 613
dB | unit:DeciB | x 1 | yes | 171
dB(A) | unit:DeciB | x 1 | yes | 171 | A-weighting kept in the property name
n | unit:UNITLESS | x 1 | yes | 3376
set(s) | unit:UNITLESS | x 1 | yes | 3376
kg | unit:KiloGM | x 1 | NO
lb | unit:KiloGM | / 2.20462 | NO |  | lb x 0.45359237
kg/h | unit:KiloGM-PER-HR | x 1 | NO
g/h | unit:KiloGM-PER-HR | / 1000 | NO |  | g/h / 1000
m/s | unit:M-PER-SEC | x 1 | NO
kg/m3 | unit:KiloGM-PER-M3 | x 1 | NO
kJ/(kg*K) | unit:KiloJ-PER-KiloGM-K | x 1 | NO
W/(m*K) | unit:W-PER-M-K | x 1 | NO
W/m2 K | unit:W-PER-M2-K | x 1 | NO
cP | unit:CentiP | x 1 | NO
K | unit:K | x 1 | NO |  | temperature difference, not a temperature
BSP | (none) |  | n/a |  | thread designation, not a quantity
V-ph-Hz | (none) |  | n/a |  | composite nameplate string, not a quantity
% | unit:PERCENT_RH | x 1 | yes | 79 | used when the property is a relative humidity
% | unit:PERCENT | x 1 | yes | 708 | used for every other percentage
(none printed) | unit:UNITLESS | x 1 | yes | 3376 | dimensionless ratios - SHR, EER, COP, fan speed setting
Highlighted rows are QUDT units Dar Cairo has never used - it carries no mass, mass-flow or velocity quantity. They are genuine QUDT terms, not minted ones, but the PARA team should confirm them before handover.