## README
QNL Equipment Metadata - Needed for Ontology
Qatar National Library, Education City BP#7A
This workbook
- The subset of the full transcription that becomes triples: 1,225 rows across 16 predicates, every one mapping to a Brick 1.4 entity property or a predicate Dar Cairo, QF SSC or QF HQ already uses. Its companion, QNL_Full_Metadata.xlsx, holds all 4,728 rows including the 3,418 kept as engineering reference.
- Read 'Value (Dar Cairo)' and 'Unit (QUDT)' as the object of the triple. For a string-valued predicate such as rec:modelNumber there is nothing to convert, so that cell carries the printed value unchanged.
- The Open Items sheet holds the 85 data quality findings. None are triples, but each one qualifies rows that are - read it before writing the ontology.
- Every row still names its source document and page, so any object can be traced back.
What this workbook is
One sheet per equipment type. Every row is a single manufacturer property for a single unit, and carries the source PDF and the page it was read from, so any value can be traced back to the document.
Sheets
AHU | 15 air handling units, AHU-001 to AHU-015. AS BUILT general arrangement drawings, drawing 1844-SD-05-AC-0077, Mercury Mena for Qatar Foundation, 26-10-2015 / 28-11-2015.
Closed Control Units | 5 selection sheets covering CC/B/01 to CC/B/09. Emerson Network Power, issued by Qatar Site & Power, April and October 2013.
Climate Control Units | Museum Climate Controls MCG-10P humidity control unit with its VCB1000 blower option and AF4 intake air filter.
FCU | 28 Euroclima selection sheets covering positions on Basement, 1F and 2F.
Heat Exchangers | 5 Alfa Laval plate heat exchangers, PHX/B/01 to PHX/B/05, with the manufacturer's construction data and the M10-MFM thermal specification.
Pumps | 4 Armstrong horizontal split case chilled water pumps, CHWP/B/01 to CHWP/B/04, with the full Armstrong submittal - pump, motor, seal, materials and dimensions.
Exhaust Fans | 39 exhaust fans - mostly Nuaire, two Colasit - from the supplied schedule spreadsheet.
Generators | One standby diesel generator from the GENERATOR ASSET LIST, a multi-equipment asset register.
Pressurization Unit | PU/B/01 (PRO1) - Armstrong 3750 2 EM-S pressurisation unit plus a Reflex DE10 1000 litre expansion tank.
CAV Units | 42 constant air volume boxes, one row per box, from six schedules.
VAV Units | 180 variable air volume boxes, one row per box, from six schedules.
DX Units | 21 DX split systems, DX/B/01-20 and DX/RP/21, from the schematic riser and the SYSTEM DETAILS equipment schedule, which names models for 16 of them.
Ontology Scope | Every distinct property in this workbook, the reference-model predicate it maps to, and whether it belongs in the ontology at all.
Units | Every source unit, the Dar Cairo unit it maps to, the factor applied, and whether Dar Cairo uses that unit at all.
Columns
Equipment Tag | The position or unit reference exactly as the source document writes it.
Model | Manufacturer model designation where the sheet gives one.
Component | The part of the unit the property belongs to - cooling coil, supply fan, condenser, etc.
Property | The property name, kept close to the source wording.
Value (as printed) | The value exactly as the document prints it. Nothing converted, rounded or inferred.
Unit (as printed) | The unit exactly as the document prints it.
Value (Dar Cairo) | The same quantity converted to the unit Dar Cairo uses for it.
Unit (QUDT) | The QUDT unit token to write into brick:hasUnit.
Conversion | The arithmetic applied, and any assumption behind it. Blank means no conversion was needed.
Source File | The document the value came from - a PDF, a spreadsheet, or a supplied drawing image.
Page | Where in that document: a 1-based page for a PDF, a sheet and row for a spreadsheet, the schedule title for a drawing.
Note | Anything that qualifies the value - a quantity off, a source conflict, a mislabelled row.
Units
- The source documents are transcribed in their own units, and each row then carries the same quantity in the unit Dar Cairo uses for it. Both are kept side by side: the printed pair stays traceable to the page, the converted pair is what goes into brick:hasUnit.
- Targets were read off DarCairo_V93.csv, not assumed. Air flow and water flow both land on unit:L-PER-SEC (para:ratedSupplyAirFlowrate, para:ratedChilledWaterFlowrate and their siblings), power on unit:KiloW (brick:ratedPowerInput, brick:coolingCapacity), length on unit:M (para:ratedHead), relative humidity on unit:PERCENT_RH rather than unit:PERCENT.
- The Units sheet lists every mapping, the factor applied, and the four QUDT units Dar Cairo has never used - mass, mass flow and velocity, which it carries no quantity for. Those need the PARA team's confirmation.
- Converting kg/s to l/s treats water as 1 kg/l. At 7-15 degC it is about 0.9997 kg/l, so the converted flow is high by roughly 0.03%.
What belongs in the ontology
- Most of this workbook is engineering reference, not ontology metadata. Dar Cairo, QF SSC and QF HQ agree on a short vocabulary for equipment - about twenty predicates - and everything outside it has no precedent in any of them.
- Brick 1.4 is checked FIRST, per the class ladder - it is step 2 and the reference models are step 3. Brick has no water or air flow-rate entity property and no heat-exchanger duty property, which is why Dar Cairo minted para:ratedWaterFlowrate, para:ratedChilledWaterFlowrate and the air-flowrate family. Where Brick does carry the term it wins: brick:coolingCapacity for heat exchanger duty, brick:ratedCurrentInput for full load current, brick:operationalStageCount for a fan's speed count, and brick:Condensing_Unit as the entity an outdoor unit's model sits on.
- Every row carries an 'Ontology predicate' and a 'Scope'. core means it maps unambiguously to a Brick 1.4 entity property or a predicate the reference models use. candidate means the match is plausible but needs a decision. reference means neither Brick nor any reference model carries anything like it - dimensions, weights, materials, seal specifications, sound power levels, filter part numbers, psychrometrics, warranty text. Those rows stay because they are useful to engineers, not because they will be modelled.
- The Ontology Scope sheet lists every distinct property with its verdict, the predicate it maps to and where that predicate comes from - Brick 1.4, Dar Cairo, QF SSC or QF HQ.
- The predicates in play: para:ratedSupplyAirFlowrate, rec:modelNumber, rec:manufacturedBy, para:ratedReheatCapacity, brick:ratedPowerInput, para:ratedChilledWaterFlowrate, brick:coolingCapacity, para:ratedSpeed, brick:ratedCurrentInput, para:ratedExhaustAirFlowrate, brick:operationalStageCount, para:ratedHead, para:refrigerant, rec:installationDate, para:ratedWaterFlowrate, para:Rated_Tank_Level.
- One open point: the expansion tank's 1000 litre capacity is written as para:Rated_Tank_Level at the user's direction. brick:volume exists in Brick 1.4 and by the ladder would outrank a para: term - reversible in one line of ontology_map.py if the team prefers it.
- An outdoor DX unit's model belongs on its own brick:Condensing_Unit entity, which Brick 1.4 carries, so no para: class needed to be minted for it. Those entities are not in this workbook yet - it holds the model against the indoor unit that names it.
- A component's own maker is not the equipment's manufacturer. The pump's mechanical seal is made by Armstrong and its motor by WEG; neither becomes rec:manufacturedBy on the pump.
- The QF HQ v0.4 draft was read for structure, not for units - several of its rows carry a wrong brick:hasUnit (an air flow tagged unit:V, a cooling capacity tagged unit:HZ). Dar Cairo remains the authority for unit choice, as the Units sheet records.
Read before using the data
- Values are transcribed from the documents as printed. Where a document contradicts itself the conflict is recorded as a 'Data quality' row rather than resolved - those need the supplier's answer.
- AHU-011 carries two Item 3 ELECTRIC COIL blocks; the first is an unfilled template (capacity POW, stages NST, entering air AON, leaving air AOF). The populated block is the one recorded.
- MCG-10P size is given as 500 x 650 x 650 mm on the specification sheet and 475 x 430 x 400 mm on dimension drawing MCG10P-1. Both are recorded; neither is confirmed.
- On 27 of the 28 Euroclima sheets the air pressure drop row is printed as 'Perdita di carico aria' with the unit [degC]. It is air-side pressure drop in Pa - page 2 labels the same row correctly.
- The CC/B/05,06,07 sheet heading reads M5DUA while its own Unit row reads M5DOA.
- The heat exchanger and pump rows come from an image of a schedule drawing whose title block is cropped out. They carry no drawing number, sheet or revision - ask for the sheet reference before handover.
- The exhaust fan schedule uses two identifier shapes: 28 slash-separated tags (EF/B/nn, EF/RP/n) and 11 underscore-separated (TEF_B01A, KEF_101). Both were kept as written because the tag is the BMS join key. EF/B numbering also runs 4 to 16 with no 1, 2 or 3.
- The pump model designation ends in 55KW. The schedule states no motor rating of its own, so no rated-power property was created from it - confirm against the pump submittal.
- The same schedule drawing carries a SCHEDULE OF PRESSURIZATION UNIT (PU/B/01, Armstrong 3750 2 EM-S). It was not asked for and is not in this workbook; say the word and it gets a sheet.
- On the DX sheet the cooling figure is the load printed on the ROOM box, not a per-unit capacity. Rooms served by two or three units are not split by the schematic, so do not write it as brick:coolingCapacity on a unit without a per-unit duty.
- The DX indoor-to-outdoor pairing recorded from the schematic's matching numbers is NOT reliable. SYSTEM DETAILS Table 3.6 shows DX/B/03, 04, 08, 09 and 14 each take an X2 outdoor model - two condensers per indoor unit - so those five need two DX/OD tags each and the numbering does not say which two. The pipework layout plan is still needed. DX/OD/05 is also marked (ST.BY) while DX/B/05 is not.
- Table 3.6 covers DX/B/01 to DX/B/16 only, so DX/B/17, 18, 19, 20 and DX/RP/21 still carry no model. DX/B/08 reads PUHZ-RP2S0X2 where its twin DX/B/09 reads PUHZ-RP250X2 - almost certainly a misprint, recorded as printed. The PEAD, PCA and PUHZ prefixes are Mitsubishi Electric Mr. Slim naming, but no document states a manufacturer, so none was inferred.
- CAV and VAV schedules write many references as ranges. Each range is split into one row per box, so every box carries its own air flow, heating capacity, model and make, and keeps a 'Scheduled as' row naming the line it came from. A range is only split when its box count matches the stated quantity; three do not and keep the printed reference with a Data quality row instead: VAV/1F/S15/012, VAV/B/S14/009 TO 012 and VAV/B/S10/001 & 008.
- Two drawings schedule the same basement S10/S15 VAV boxes and disagree on VAV/B/S15/001 TO 004 (261 l/s against 251 l/s). Both are recorded against their own drawing. On the second 1F schedule VAV/1F/S15/014 TO 015 also falls inside VAV/1F/S15/013 TO 020 with a different flow and model.
- VAV/1F/S11/022 was scheduled twice; the user confirmed the standalone row governs (220 l/s, NBOQOB200), so the overlapping VAV/1F/S11/022 TO 24 row is read as covering 023 and 024 only. Five further rows carrying out-of-range box numbers were excluded on instruction.
- The fire damper and supply/return grille schedules on the same images were struck through in red and were read as cancelled, so they are not in this workbook.
- PHX/B/05 exists only on the Alfa Laval data and the SYSTEM DETAILS schedule - the drawing schedule stops at PHX/B/04. It is a 300 kW M10-MFM described as the 'Main HEX'. SYSTEM DETAILS states one hot-side temperature across all five rows (15.5 in / 6.5 out) but the M10-MFM specification gives 50.0 in / 20.0 out. Both are recorded; the conflict is unresolved.
- SYSTEM DETAILS writes the pump tags with dashes (CHWP-B-01) and tags the pressurisation unit PRO1, where the drawing schedules write CHWP/B/01 and PU/B/01. The slash forms are used as the Equipment Tag because they match the rest of the workbook; the alternates are recorded as an 'Alternate reference' property on each unit. Confirm which the BMS uses.
- The Armstrong pump submittal is dimensioned in inches and pounds and is marked NOT for CONSTRUCTION. Its weight of 1874 lb converts to 850 kg against the drawing schedule's 843 kg. Its letter callouts (D, HA, HB, ...) are keyed to an outline drawing that does not say which feature each measures.
- The GENERATOR ASSET LIST is a multi-equipment asset register. The row cropped off below the generator belongs to different equipment, so the single row on the Generators sheet is the complete record for this machine. Its ASSET TAG NUMBER column reads 'GENERATOR SET' - the same text as the equipment name - so it does not identify an individual machine; only the serial number does.
- These are equipment selection and as-built documents, not nameplate photographs. Where the installed plant differs from the selection, the installed plant governs.
Source documents
Ahu_manual_1.pdf | 8 pages - AHU-001 to AHU-008 general arrangement drawings
ahu_2.pdf | 7 pages - AHU-009 to AHU-015 general arrangement drawings
qnl_closed_control_units_manual.pdf | 17 pages - Emerson closed control unit selections
climate_control_units_manual.pdf | 7 pages - Museum Climate Controls MCG-10P data sheets
FCU_Manual.pdf | 29 pages - Euroclima fan coil unit selection sheets
MEP schedule drawing | image - Heat exchanger, pump and pressurization unit schedules, supplied as an image in chat. The image crops the title block, so no drawing number, sheet number or revision is recorded against these rows.
Book1.xlsx | Sheet1, 39 rows - Exhaust fan schedule - equipment tag, model, manufacturer and air flow only
CAV and VAV schedules | 6 + 6 schedules - Supplied as drawing images in chat, title blocks cropped. Each schedule is a separate source; the Page column names which.
Armstrong submittal | TENDER301358.1 rev3, p14/22 - Full nameplate for the chilled water pumps - pump design, WEG motor, mechanical seal, materials and imperial dimensions
Alfa Laval PHE data | 2 sheets - Construction comparison for T20-BFG and M10-MFM, and the M10-MFM thermal specification for PHX/B/05
SYSTEM DETAILS | Tables 3.1-3.3, 3.6 - Duty/standby split for the pumps and heat exchangers, the pressurisation unit broken into its two components, and indoor/outdoor models for DX/B/01 to DX/B/16
GENERATOR ASSET LIST | image - Asset register row for a standby diesel generator
DX split system schematic | image - Riser diagram giving the room each DX unit serves, its design condition and a room cooling load

## AHU
AHU
Air handling units AHU-001 to AHU-015 - AS BUILT general arrangement drawings, drawing 1844-SD-05-AC-0077 (Mercury Mena for Qatar Foundation). Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
AHU-001 |  | Cooling coil | Model | 1226C3808517125W0176 |  | 1226C3808517125W0176 |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Water flow | 9.48 | kg/s | 9.48 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Cooling coil | Total capacity | 318.13 | kW | 318.13 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Water flow | 15493 | l/h | 4.3036 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 1
AHU-001 |  | External auxiliary cooling coil | Total capacity | 144 | kW | 144 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Electric coil | Total capacity | 57 | kW | 57 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Fan model | TZAF 630 T2L |  | TZAF 630 T2L |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 1 | on the fan sub-entity, not the parent unit
AHU-001 |  | Supply fan | Air flow | 14.9 | m3/s | 14900 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan | Speed | 2517 | rpm | 2517 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Rating | 18.5 | kW | 18.5 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Full load speed | 2517 | rpm | 2517 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Supply fan drive motor | Full load current | 34 | A | 34 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 1 | Brick 1.4 entity property; no reference model uses it yet
AHU-001 |  | Return fan | Fan model | TZAF 630 T1 |  | TZAF 630 T1 |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 1 | on the fan sub-entity, not the parent unit
AHU-001 |  | Return fan | Air flow | 14.9 | m3/s | 14900 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | Ahu_manual_1.pdf | 1 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-001 |  | Return fan | Speed | 2012 | rpm | 2012 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Rating | 11 | kW | 11 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Full load speed | 2012 | rpm | 2012 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 1
AHU-001 |  | Return fan drive motor | Full load current | 21 | A | 21 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 1 | Brick 1.4 entity property; no reference model uses it yet
AHU-002 |  | Cooling coil | Model | 1226C6408261120W02(64+64) |  | 1226C6408261120W02(64+64) |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Water flow | 12.52 | kg/s | 12.52 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Cooling coil | Total capacity | 419.67 | kW | 419.67 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Electric coil | Total capacity | 47 | kW | 47 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Fan model | TZAF 800 T2L |  | TZAF 800 T2L |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 2 | on the fan sub-entity, not the parent unit
AHU-002 |  | Supply fan | Air flow | 12.3 | m3/s | 12300 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan | Speed | 1245 | rpm | 1245 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 2
AHU-002 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 2 | Brick 1.4 entity property; no reference model uses it yet
AHU-003 |  | Cooling coil | Model | 1226C6408261120W02(64+64) |  | 1226C6408261120W02(64+64) |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Water flow | 12.52 | kg/s | 12.52 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Cooling coil | Total capacity | 419.67 | kW | 419.67 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Electric coil | Total capacity | 47 | kW | 47 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Fan model | TZAF 800 T2L |  | TZAF 800 T2L |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 3 | on the fan sub-entity, not the parent unit
AHU-003 |  | Supply fan | Air flow | 12.3 | m3/s | 12300 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan | Speed | 1245 | rpm | 1245 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 3
AHU-003 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 3 | Brick 1.4 entity property; no reference model uses it yet
AHU-004 |  | Cooling coil | Model | 1226C6408261120W01(64+64) |  | 1226C6408261120W01(64+64) |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Water flow | 12.52 | kg/s | 12.52 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Cooling coil | Total capacity | 419.67 | kW | 419.67 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Electric coil | Total capacity | 47 | kW | 47 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Fan model | TZAF 800 T2L |  | TZAF 800 T2L |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 4 | on the fan sub-entity, not the parent unit
AHU-004 |  | Supply fan | Air flow | 12.3 | m3/s | 12300 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan | Speed | 1317 | rpm | 1317 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Full load speed | 1482 | rpm | 1482 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 4
AHU-004 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 4 | Brick 1.4 entity property; no reference model uses it yet
AHU-005 |  | Cooling coil | Model | 1226C6408352125W01(64+64) |  | 1226C6408352125W01(64+64) |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Water flow | 15.69 | kg/s | 15.69 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Cooling coil | Total capacity | 526.13 | kW | 526.13 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Electric coil | Total capacity | 63 | kW | 63 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Fan model | TZAF 900 T2L |  | TZAF 900 T2L |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 5 | on the fan sub-entity, not the parent unit
AHU-005 |  | Supply fan | Air flow | 16.5 | m3/s | 16500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan | Speed | 1313 | rpm | 1313 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Rating | 45 | kW | 45 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Full load speed | 1480 | rpm | 1480 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 5
AHU-005 |  | Supply fan drive motor | Full load current | 81 | A | 81 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 5 | Brick 1.4 entity property; no reference model uses it yet
AHU-006 |  | Cooling coil | Model | 1226C6408352125W01(64+64) |  | 1226C6408352125W01(64+64) |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Water flow | 15.68 | kg/s | 15.68 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Cooling coil | Total capacity | 525.67 | kW | 525.67 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Electric coil | Total capacity | 63 | kW | 63 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Fan model | TZAF 900 T2L |  | TZAF 900 T2L |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 6 | on the fan sub-entity, not the parent unit
AHU-006 |  | Supply fan | Air flow | 16.5 | m3/s | 16500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan | Speed | 1285 | rpm | 1285 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Rating | 37 | kW | 37 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Full load speed | 980 | rpm | 980 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 6
AHU-006 |  | Supply fan drive motor | Full load current | 67.3 | A | 67.3 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 6 | Brick 1.4 entity property; no reference model uses it yet
AHU-007 |  | Cooling coil | Model | 1226C6408352125W01(64+64) |  | 1226C6408352125W01(64+64) |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Water flow | 15.68 | kg/s | 15.68 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Cooling coil | Total capacity | 525.67 | kW | 525.67 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Electric coil | Total capacity | 63 | kW | 63 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Fan model | TZAF 900 T2 |  | TZAF 900 T2 |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 7 | on the fan sub-entity, not the parent unit
AHU-007 |  | Supply fan | Air flow | 16.5 | m3/s | 16500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan | Speed | 1316 | rpm | 1316 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Rating | 45 | kW | 45 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Full load speed | 1480 | rpm | 1480 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 7
AHU-007 |  | Supply fan drive motor | Full load current | 81 | A | 81 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 7 | Brick 1.4 entity property; no reference model uses it yet
AHU-008 |  | Cooling coil | Model | 1226C6408189120W0164 |  | 1226C6408189120W0164 |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Water flow | 9.04 | kg/s | 9.04 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Cooling coil | Total capacity | 303.68 | kW | 303.68 | unit:KiloW |  | brick:coolingCapacity | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Electric coil | Total capacity | 35 | kW | 35 | unit:KiloW |  | para:ratedReheatCapacity | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Fan model | TZAF 710 FF T2L |  | TZAF 710 FF T2L |  |  | rec:modelNumber | core | Ahu_manual_1.pdf | 8 | on the fan sub-entity, not the parent unit
AHU-008 |  | Supply fan | Air flow | 9.2 | m3/s | 9200 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan | Speed | 2517 | rpm | 2517 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Full load speed | 2517 | rpm | 2517 | unit:RPM |  | para:ratedSpeed | core | Ahu_manual_1.pdf | 8
AHU-008 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | Ahu_manual_1.pdf | 8 | Brick 1.4 entity property; no reference model uses it yet
AHU-009 |  | Cooling coil | Model | 1226C6408261120W 02(64+64) |  | 1226C6408261120W 02(64+64) |  |  | rec:modelNumber | core | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Water flow | 12.05 | kg/s | 12.05 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 1
AHU-009 |  | Cooling coil | Total capacity | 400.82 | kW | 400.82 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 1
AHU-009 |  | Electric coil | Total capacity | 46 | kW | 46 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Fan model | TZAF 800 T2L |  | TZAF 800 T2L |  |  | rec:modelNumber | core | ahu_2.pdf | 1 | on the fan sub-entity, not the parent unit
AHU-009 |  | Supply fan | Air flow | 12 | m3/s | 12000 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 1
AHU-009 |  | Supply fan | Speed | 1176 | rpm | 1176 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 1
AHU-009 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 1 | Brick 1.4 entity property; no reference model uses it yet
AHU-010 |  | Cooling coil | Model | 1226C5808161120W0158 |  | 1226C5808161120W0158 |  |  | rec:modelNumber | core | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Water flow | 5.6 | kg/s | 5.6 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 2
AHU-010 |  | Cooling coil | Total capacity | 187.83 | kW | 187.83 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 2
AHU-010 |  | Electric coil | Total capacity | 28 | kW | 28 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Fan model | TZAF 630 T2L |  | TZAF 630 T2L |  |  | rec:modelNumber | core | ahu_2.pdf | 2 | on the fan sub-entity, not the parent unit
AHU-010 |  | Supply fan | Air flow | 7.2 | m3/s | 7200 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 2
AHU-010 |  | Supply fan | Speed | 1640 | rpm | 1640 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Rating | 18.5 | kW | 18.5 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 2
AHU-010 |  | Supply fan drive motor | Full load current | 34 | A | 34 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 2 | Brick 1.4 entity property; no reference model uses it yet
AHU-010 |  | Return fan | Fan model | TZAF 710 T1 |  | TZAF 710 T1 |  |  | rec:modelNumber | core | ahu_2.pdf | 2 | on the fan sub-entity, not the parent unit
AHU-010 |  | Return fan | Air flow | 7.2 | m3/s | 7200 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 2 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-010 |  | Return fan | Speed | 1080 | rpm | 1080 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Rating | 11 | kW | 11 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Full load speed | 960 | rpm | 960 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 2
AHU-010 |  | Return fan drive motor | Full load current | 22.9 | A | 22.9 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 2 | Brick 1.4 entity property; no reference model uses it yet
AHU-011 |  | Cooling coil | Model | UCUC-FEZN P404R7R-23T-28924-2.0PA4OC2 1/2" |  | UCUC-FEZN P404R7R-23T-28924-2.0PA4OC2 1/2" |  |  | rec:modelNumber | core | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Water flow | 16.26 | kg/s | 16.26 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 3
AHU-011 |  | Cooling coil | Total capacity | 545.2 | kW | 545.2 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 3
AHU-011 |  | Electric coil | Total capacity | 51 | kW | 51 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Fan model | TZAF 900 T1 |  | TZAF 900 T1 |  |  | rec:modelNumber | core | ahu_2.pdf | 3 | on the fan sub-entity, not the parent unit
AHU-011 |  | Supply fan | Air flow | 13.4 | m3/s | 13400 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 3
AHU-011 |  | Supply fan | Speed | 1097 | rpm | 1097 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Full load speed | 980 | rpm | 980 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 3
AHU-011 |  | Supply fan drive motor | Full load current | 56.2 | A | 56.2 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 3 | Brick 1.4 entity property; no reference model uses it yet
AHU-011 |  | Return fan | Fan model | TZAF 900 T1 |  | TZAF 900 T1 |  |  | rec:modelNumber | core | ahu_2.pdf | 3 | on the fan sub-entity, not the parent unit
AHU-011 |  | Return fan | Air flow | 13.4 | m3/s | 13400 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 3 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-011 |  | Return fan | Speed | 827 | rpm | 827 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Rating | 18.5 | kW | 18.5 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Full load speed | 975 | rpm | 975 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 3
AHU-011 |  | Return fan drive motor | Full load current | 36.4 | A | 36.4 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 3 | Brick 1.4 entity property; no reference model uses it yet
AHU-012 |  | Cooling coil | Model | 1226C5606179120W0256 |  | 1226C5606179120W0256 |  |  | rec:modelNumber | core | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Water flow | 6.29 | kg/s | 6.29 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 4
AHU-012 |  | Cooling coil | Total capacity | 211.5 | kW | 211.5 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 4
AHU-012 |  | Electric coil | Total capacity | 29 | kW | 29 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Fan model | TZAF 710 T1 |  | TZAF 710 T1 |  |  | rec:modelNumber | core | ahu_2.pdf | 4 | on the fan sub-entity, not the parent unit
AHU-012 |  | Supply fan | Air flow | 7.5 | m3/s | 7500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 4
AHU-012 |  | Supply fan | Speed | 1175 | rpm | 1175 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Rating | 15 | kW | 15 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Full load speed | 1460 | rpm | 1460 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 4
AHU-012 |  | Supply fan drive motor | Full load current | 28.1 | A | 28.1 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 4 | Brick 1.4 entity property; no reference model uses it yet
AHU-012 |  | Return fan | Fan model | TZFA 710 T1 |  | TZFA 710 T1 |  |  | rec:modelNumber | core | ahu_2.pdf | 4 | on the fan sub-entity, not the parent unit
AHU-012 |  | Return fan | Air flow | 7.5 | m3/s | 7500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 4 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-012 |  | Return fan | Speed | 1020 | rpm | 1020 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Rating | 11 | kW | 11 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Full load speed | 960 | rpm | 960 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 4
AHU-012 |  | Return fan drive motor | Full load current | 22.9 | A | 22.9 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 4 | Brick 1.4 entity property; no reference model uses it yet
AHU-013 |  | Cooling coil | Model | 1226C6206179130W0162 |  | 1226C6206179130W0162 |  |  | rec:modelNumber | core | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Water flow | 6.81 | kg/s | 6.81 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 5
AHU-013 |  | Cooling coil | Total capacity | 228 | kW | 228 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 5
AHU-013 |  | Electric coil | Total capacity | 32 | kW | 32 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Fan model | TZAF 710 T1 |  | TZAF 710 T1 |  |  | rec:modelNumber | core | ahu_2.pdf | 5 | on the fan sub-entity, not the parent unit
AHU-013 |  | Supply fan | Air flow | 8.5 | m3/s | 8500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 5
AHU-013 |  | Supply fan | Speed | 1317 | rpm | 1317 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Rating | 18.5 | kW | 18.5 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 5
AHU-013 |  | Supply fan drive motor | Full load current | 34 | A | 34 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 5 | Brick 1.4 entity property; no reference model uses it yet
AHU-013 |  | Return fan | Fan model | TZAF 710 T1 |  | TZAF 710 T1 |  |  | rec:modelNumber | core | ahu_2.pdf | 5 | on the fan sub-entity, not the parent unit
AHU-013 |  | Return fan | Air flow | 8.5 | m3/s | 8500 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 5 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-013 |  | Return fan | Speed | 1175 | rpm | 1175 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Rating | 15 | kW | 15 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Full load speed | 1460 | rpm | 1460 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 5
AHU-013 |  | Return fan drive motor | Full load current | 28.1 | A | 28.1 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 5 | Brick 1.4 entity property; no reference model uses it yet
AHU-014 |  | Cooling coil | Model | 1226C6405255120W0280 |  | 1226C6405255120W0280 |  |  | rec:modelNumber | core | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Water flow | 9.33 | kg/s | 9.33 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 6
AHU-014 |  | Cooling coil | Total capacity | 313 | kW | 313 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 6
AHU-014 |  | Electric coil | Total capacity | 45 | kW | 45 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Fan model | TZAF 800 T2L |  | TZAF 800 T2L |  |  | rec:modelNumber | core | ahu_2.pdf | 6 | on the fan sub-entity, not the parent unit
AHU-014 |  | Supply fan | Air flow | 11.8 | m3/s | 11800 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 6
AHU-014 |  | Supply fan | Speed | 1176 | rpm | 1176 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Rating | 30 | kW | 30 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Full load speed | 1470 | rpm | 1470 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 6
AHU-014 |  | Supply fan drive motor | Full load current | 54.4 | A | 54.4 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 6 | Brick 1.4 entity property; no reference model uses it yet
AHU-014 |  | Return fan | Fan model | TZAF 800 T1 |  | TZAF 800 T1 |  |  | rec:modelNumber | core | ahu_2.pdf | 6 | on the fan sub-entity, not the parent unit
AHU-014 |  | Return fan | Air flow | 11.8 | m3/s | 11800 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 6 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-014 |  | Return fan | Speed | 1026 | rpm | 1026 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Rating | 18.5 | kW | 18.5 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Full load speed | 975 | rpm | 975 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 6
AHU-014 |  | Return fan drive motor | Full load current | 36.4 | A | 36.4 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 6 | Brick 1.4 entity property; no reference model uses it yet
AHU-015 |  | Cooling coil | Model | 1226C6406276120W02(48+48) |  | 1226C6406276120W02(48+48) |  |  | rec:modelNumber | core | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Water flow | 15.47 | kg/s | 15.47 | unit:L-PER-SEC | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference | para:ratedChilledWaterFlowrate | core | ahu_2.pdf | 7
AHU-015 |  | Cooling coil | Total capacity | 518.09 | kW | 518.09 | unit:KiloW |  | brick:coolingCapacity | core | ahu_2.pdf | 7
AHU-015 |  | Electric coil | Total capacity | 64 | kW | 64 | unit:KiloW |  | para:ratedReheatCapacity | core | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Fan model | TZAF 800 T2L |  | TZAF 800 T2L |  |  | rec:modelNumber | core | ahu_2.pdf | 7 | on the fan sub-entity, not the parent unit
AHU-015 |  | Supply fan | Air flow | 12.8 | m3/s | 12800 | unit:L-PER-SEC | m3/s x 1000 | para:ratedSupplyAirFlowrate | core | ahu_2.pdf | 7
AHU-015 |  | Supply fan | Speed | 1256 | rpm | 1256 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Rating | 37 | kW | 37 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Full load speed | 1480 | rpm | 1480 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 7
AHU-015 |  | Supply fan drive motor | Full load current | 66.2 | A | 66.2 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 7 | Brick 1.4 entity property; no reference model uses it yet
AHU-015 |  | Return fan | Fan model | TZAF 800 T1 |  | TZAF 800 T1 |  |  | rec:modelNumber | core | ahu_2.pdf | 7 | on the fan sub-entity, not the parent unit
AHU-015 |  | Return fan | Air flow | 12.8 | m3/s | 12800 | unit:L-PER-SEC | m3/s x 1000 | para:ratedExhaustAirFlowrate | core | ahu_2.pdf | 7 | Brick has no air-flowrate entity property; Dar Cairo's exhaust predicate confirmed by the user
AHU-015 |  | Return fan | Speed | 1087 | rpm | 1087 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Rating | 22 | kW | 22 | unit:KiloW |  | brick:ratedPowerInput | core | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Full load speed | 975 | rpm | 975 | unit:RPM |  | para:ratedSpeed | core | ahu_2.pdf | 7
AHU-015 |  | Return fan drive motor | Full load current | 42 | A | 42 | unit:A |  | brick:ratedCurrentInput | core | ahu_2.pdf | 7 | Brick 1.4 entity property; no reference model uses it yet

## Closed Control Units
Closed Control Units
Emerson Network Power closed control units CC/B/01 to CC/B/09 - selection sheets issued by Qatar Site & Power. Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
CC/B/01,02 | S1GOA | Identification | Manufacturer | Emerson Network Power |  | Emerson Network Power |  |  | rec:manufacturedBy | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Identification | Model | S1GOA |  | S1GOA |  |  | rec:modelNumber | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Design condition | Unit airflow | 3700 | m3/h | 1027.78 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Design condition | Refrigerant | R410A |  | R410A |  |  | para:refrigerant | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Total cooling capacity | 14 | kW | 14 | unit:KiloW |  | brick:coolingCapacity | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Unit performance | Unit power input | 5.52 | kW | 5.52 | unit:KiloW |  | brick:ratedPowerInput | core | qnl_closed_control_units_manual.pdf | 2
CC/B/01,02 | S1GOA | Option - electrical re-heating | Max re-heating capacity | 5.85 | kW | 5.85 | unit:KiloW |  | para:ratedReheatCapacity | core | qnl_closed_control_units_manual.pdf | 3
CC/B/03,04 | S1DOA + 1 x HCR24 | Identification | Manufacturer | Emerson Network Power |  | Emerson Network Power |  |  | rec:manufacturedBy | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Identification | Model | S1DOA + 1 x HCR24 |  | S1DOA + 1 x HCR24 |  |  | rec:modelNumber | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Design condition | Unit airflow | 2412 | m3/h | 670 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Design condition | Refrigerant | R410A |  | R410A |  |  | para:refrigerant | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Total cooling capacity | 10.6 | kW | 10.6 | unit:KiloW |  | brick:coolingCapacity | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Unit performance | Unit power input | 4.85 | kW | 4.85 | unit:KiloW |  | brick:ratedPowerInput | core | qnl_closed_control_units_manual.pdf | 5
CC/B/03,04 | S1DOA + 1 x HCR24 | Option - electrical re-heating | Max re-heating capacity | 4.5 | kW | 4.5 | unit:KiloW |  | para:ratedReheatCapacity | core | qnl_closed_control_units_manual.pdf | 6
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Identification | Manufacturer | Emerson Network Power |  | Emerson Network Power |  |  | rec:manufacturedBy | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Identification | Model | M5DUA + 2 x HCR59 |  | M5DUA + 2 x HCR59 |  |  | rec:modelNumber | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Design condition | Unit airflow | 13320 | m3/h | 3700 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Design condition | Refrigerant | R410A |  | R410A |  |  | para:refrigerant | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Total cooling capacity | 50.1 | kW | 50.1 | unit:KiloW |  | brick:coolingCapacity | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Unit performance | Unit power input | 20.23 | kW | 20.23 | unit:KiloW |  | brick:ratedPowerInput | core | qnl_closed_control_units_manual.pdf | 8
CC/B/05,06,07 | M5DUA + 2 x HCR59 | Option - electrical re-heating | Max re-heating capacity | 15 | kW | 15 | unit:KiloW |  | para:ratedReheatCapacity | core | qnl_closed_control_units_manual.pdf | 9
CC/B/08 | S11OC | Identification | Manufacturer | Emerson Network Power |  | Emerson Network Power |  |  | rec:manufacturedBy | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Identification | Model | S11OC |  | S11OC |  |  | rec:modelNumber | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Design condition | Unit airflow | 2800 | m3/h | 777.778 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Design condition | Unit fluid flow | 0.42 | l/s | 0.42 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Total cooling capacity | 8.7 | kW | 8.7 | unit:KiloW |  | brick:coolingCapacity | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Unit performance | Unit power input | 0.35 | kW | 0.35 | unit:KiloW |  | brick:ratedPowerInput | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | CW coil | Unit fluid flow | 0.42 | l/s | 0.42 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | qnl_closed_control_units_manual.pdf | 11
CC/B/08 | S11OC | Option - electrical re-heating | Max re-heating capacity | 4.5 | kW | 4.5 | unit:KiloW |  | para:ratedReheatCapacity | core | qnl_closed_control_units_manual.pdf | 12
CC/B/09 | S1DOA + 1 x HCR33 | Identification | Manufacturer | Emerson Network Power |  | Emerson Network Power |  |  | rec:manufacturedBy | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Identification | Model | S1DOA + 1 x HCR33 |  | S1DOA + 1 x HCR33 |  |  | rec:modelNumber | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Design condition | Unit airflow | 2100 | m3/h | 583.333 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Design condition | Refrigerant | R410A |  | R410A |  |  | para:refrigerant | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Total cooling capacity | 10.4 | kW | 10.4 | unit:KiloW |  | brick:coolingCapacity | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Unit performance | Unit power input | 4.47 | kW | 4.47 | unit:KiloW |  | brick:ratedPowerInput | core | qnl_closed_control_units_manual.pdf | 16
CC/B/09 | S1DOA + 1 x HCR33 | Option - electrical re-heating | Max re-heating capacity | 4.5 | kW | 4.5 | unit:KiloW |  | para:ratedReheatCapacity | core | qnl_closed_control_units_manual.pdf | 17

## Climate Control Units
Climate Control Units
Museum Climate Controls MCG-10P positive-pressure humidity control unit, VCB1000 blower option and AF4 intake air filter. Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
MCG-10P | MCG-10P | Identification | Manufacturer | Museum Climate Controls |  | Museum Climate Controls |  |  | rec:manufacturedBy | core | climate_control_units_manual.pdf | 2
MCG-10P | MCG-10P | Identification | Model | MCG-10P |  | MCG-10P |  |  | rec:modelNumber | core | climate_control_units_manual.pdf | 2
VCB1000-AB32 | VCB1000-AB32 | Identification | Manufacturer | VCBtech |  | VCBtech |  |  | rec:manufacturedBy | core | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Identification | Model | VCB1000-AB32 |  | VCB1000-AB32 |  |  | rec:modelNumber | core | climate_control_units_manual.pdf | 4
VCB1000-AB32 | VCB1000-AB32 | Technical data | Speed | 9000 | rpm | 9000 | unit:RPM |  | para:ratedSpeed | core | climate_control_units_manual.pdf | 4
MCG Air Filter AF4 | AF4 | Identification | Manufacturer | Museum Climate Controls |  | Museum Climate Controls |  |  | rec:manufacturedBy | core | climate_control_units_manual.pdf | 7
MCG Air Filter AF4 | AF4 | Identification | Model | AF4 |  | AF4 |  |  | rec:modelNumber | core | climate_control_units_manual.pdf | 7

## FCU
FCU
Euroclima fan coil units - one selection sheet per position, offer CENTRAL LIBRARY. Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
FCU/B/01 | TO50-4R-2 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Identification | Model | TO50-4R-2 |  | TO50-4R-2 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Capacity | Total capacity (cooling) | 13.21 | kW | 13.21 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Air | Flow rate | 4182 | m3/h | 1161.67 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Fluid | Flow rate | 1296 | l/h | 0.36 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 2
FCU/B/01 | TO50-4R-2 | Other data | Max. absorbed power | 970 | W | 0.97 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 2
B/02 | CR32-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Identification | Model | CR32-4R-6 |  | CR32-4R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Capacity | Total capacity (cooling) | 6.52 | kW | 6.52 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Air | Flow rate | 1836 | m3/h | 510 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Fluid | Flow rate | 698 | l/h | 0.19389 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 3
B/02 | CR32-4R-6 | Other data | Max. absorbed power | 570 | W | 0.57 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 3
B/03,04 | CR32-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Identification | Model | CR32-3R-6 |  | CR32-3R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Capacity | Total capacity (cooling) | 6.09 | kW | 6.09 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Air | Flow rate | 1836 | m3/h | 510 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Fluid | Flow rate | 720 | l/h | 0.2 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 4
B/03,04 | CR32-3R-6 | Other data | Max. absorbed power | 570 | W | 0.57 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 4
B5 | CR23-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Identification | Model | CR23-3R-6 |  | CR23-3R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Capacity | Total capacity (cooling) | 3.52 | kW | 3.52 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Air | Flow rate | 1365 | m3/h | 379.167 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Fluid | Flow rate | 360 | l/h | 0.1 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 5
B5 | CR23-3R-6 | Other data | Max. absorbed power | 420 | W | 0.42 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 5
B/06,08,17,24 | FH090-3R-7 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Identification | Model | FH090-3R-7 |  | FH090-3R-7 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Capacity | Total capacity (cooling) | 3.8 | kW | 3.8 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Air | Flow rate | 720 | m3/h | 200 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Fluid | Flow rate | 360 | l/h | 0.1 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 6
B/06,08,17,24 | FH090-3R-7 | Other data | Max. absorbed power | 285 | W | 0.285 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 6
B/07 | TO30-3R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Identification | Model | TO30-3R-3 |  | TO30-3R-3 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Capacity | Total capacity (cooling) | 12 | kW | 12 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Air | Flow rate | 2576 | m3/h | 715.556 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Fluid | Flow rate | 1296 | l/h | 0.36 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 7
B/07 | TO30-3R-3 | Other data | Max. absorbed power | 770 | W | 0.77 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 7
B/09 | CR32-3R-6-5NC | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Identification | Model | CR32-3R-6-5NC |  | CR32-3R-6-5NC |  |  | rec:modelNumber | core | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Capacity | Total capacity (cooling) | 9.03 | kW | 9.03 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Air | Flow rate | 1820 | m3/h | 505.556 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Fluid | Flow rate | 972 | l/h | 0.27 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 8
B/09 | CR32-3R-6-5NC | Other data | Max. absorbed power | 570 | W | 0.57 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 8
B/10 | CR23-4R-7 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Identification | Model | CR23-4R-7 |  | CR23-4R-7 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Capacity | Total capacity (cooling) | 3.67 | kW | 3.67 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Air | Flow rate | 1106 | m3/h | 307.222 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Fluid | Flow rate | 360 | l/h | 0.1 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 9
B/10 | CR23-4R-7 | Other data | Max. absorbed power | 420 | W | 0.42 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 9
B/11-12 (OPT-1) | CR23-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Identification | Model | CR23-4R-6 |  | CR23-4R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Capacity | Total capacity (cooling) | 7.38 | kW | 7.38 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Air | Flow rate | 1404 | m3/h | 390 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Fluid | Flow rate | 756 | l/h | 0.21 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 10
B/11-12 (OPT-1) | CR23-4R-6 | Other data | Max. absorbed power | 420 | W | 0.42 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 10
B/13-14 | CR23-4R-7 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Identification | Model | CR23-4R-7 |  | CR23-4R-7 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Capacity | Total capacity (cooling) | 5.8 | kW | 5.8 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Air | Flow rate | 1080 | m3/h | 300 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Fluid | Flow rate | 576 | l/h | 0.16 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 11
B/13-14 | CR23-4R-7 | Other data | Max. absorbed power | 420 | W | 0.42 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 11
B/15-16 | CR26-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Identification | Model | CR26-4R-6 |  | CR26-4R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Capacity | Total capacity (cooling) | 8.35 | kW | 8.35 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Air | Flow rate | 1584 | m3/h | 440 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Fluid | Flow rate | 864 | l/h | 0.24 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 12
B/15-16 | CR26-4R-6 | Other data | Max. absorbed power | 535 | W | 0.535 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 12
B/18-21 | CR23-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Identification | Model | CR23-4R-6 |  | CR23-4R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Capacity | Total capacity (cooling) | 7.31 | kW | 7.31 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Air | Flow rate | 1386 | m3/h | 385 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Fluid | Flow rate | 756 | l/h | 0.21 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 13
B/18-21 | CR23-4R-6 | Other data | Max. absorbed power | 420 | W | 0.42 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 13
B/22-23 | FH105-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Identification | Model | FH105-3R-6 |  | FH105-3R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Capacity | Total capacity (cooling) | 5.32 | kW | 5.32 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Air | Flow rate | 1008 | m3/h | 280 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Fluid | Flow rate | 540 | l/h | 0.15 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 14
B/22-23 | FH105-3R-6 | Other data | Max. absorbed power | 300 | W | 0.3 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 14
B/25-26 | TO50-4R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Identification | Model | TO50-4R-3 |  | TO50-4R-3 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Capacity | Total capacity (cooling) | 19.16 | kW | 19.16 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Air | Flow rate | 3780 | m3/h | 1050 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Fluid | Flow rate | 1980 | l/h | 0.55 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 15
B/25-26 | TO50-4R-3 | Other data | Max. absorbed power | 970 | W | 0.97 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 15
B/27-28 | FH070-2R-7 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Identification | Model | FH070-2R-7 |  | FH070-2R-7 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Capacity | Total capacity (cooling) | 2.34 | kW | 2.34 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Air | Flow rate | 770 | m3/h | 213.889 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Fluid | Flow rate | 251 | l/h | 0.069722 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 16
B/27-28 | FH070-2R-7 | Other data | Max. absorbed power | 281 | W | 0.281 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 16
B/29 | CR32-4R-6-4NC | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Identification | Model | CR32-4R-6-4NC |  | CR32-4R-6-4NC |  |  | rec:modelNumber | core | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Capacity | Total capacity (cooling) | 8.03 | kW | 8.03 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Air | Flow rate | 1813 | m3/h | 503.611 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Fluid | Flow rate | 862 | l/h | 0.23944 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 17
B/29 | CR32-4R-6-4NC | Other data | Max. absorbed power | 570 | W | 0.57 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 17
B/30 | TO50-4R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Identification | Model | TO50-4R-3 |  | TO50-4R-3 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Capacity | Total capacity (cooling) | 17.59 | kW | 17.59 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Air | Flow rate | 3420 | m3/h | 950 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Fluid | Flow rate | 1800 | l/h | 0.5 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 18
B/30 | TO50-4R-3 | Other data | Max. absorbed power | 970 | W | 0.97 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 18
FCU/B/31 | CR32-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Identification | Model | CR32-3R-6 |  | CR32-3R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Capacity | Total capacity (cooling) | 6.09 | kW | 6.09 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Air | Flow rate | 1836 | m3/h | 510 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Fluid | Flow rate | 720 | l/h | 0.2 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 19
FCU/B/31 | CR32-3R-6 | Other data | Max. absorbed power | 570 | W | 0.57 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 19
FCU/1F/01 | CR26-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Identification | Model | CR26-3R-6 |  | CR26-3R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Capacity | Total capacity (cooling) | 6.12 | kW | 6.12 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Air | Flow rate | 1925 | m3/h | 534.722 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Fluid | Flow rate | 720 | l/h | 0.2 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 20
FCU/1F/01 | CR26-3R-6 | Other data | Max. absorbed power | 535 | W | 0.535 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 20
1F/02-03 | TO30-4R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Identification | Model | TO30-4R-3 |  | TO30-4R-3 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Capacity | Total capacity (cooling) | 9.09 | kW | 9.09 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Air | Flow rate | 2648 | m3/h | 735.556 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Fluid | Flow rate | 972 | l/h | 0.27 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 21
1F/02-03 | TO30-4R-3 | Other data | Max. absorbed power | 770 | W | 0.77 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 21
1F/04-54 | CR17-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Identification | Model | CR17-4R-6 |  | CR17-4R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Capacity | Total capacity (cooling) | 3.73 | kW | 3.73 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Air | Flow rate | 825 | m3/h | 229.167 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Fluid | Flow rate | 396 | l/h | 0.11 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 22
1F/04-54 | CR17-4R-6 | Other data | Max. absorbed power | 253 | W | 0.253 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 22
1F/55 | TO50-4R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Identification | Model | TO50-4R-3 |  | TO50-4R-3 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Capacity | Total capacity (cooling) | 14.14 | kW | 14.14 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Air | Flow rate | 4189 | m3/h | 1163.61 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Fluid | Flow rate | 1512 | l/h | 0.42 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 23
1F/55 | TO50-4R-3 | Other data | Max. absorbed power | 970 | W | 0.97 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 23
1F/56 | CR09-3R-7 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Identification | Model | CR09-3R-7 |  | CR09-3R-7 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Capacity | Total capacity (cooling) | 3.08 | kW | 3.08 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Air | Flow rate | 473 | m3/h | 131.389 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Fluid | Flow rate | 331 | l/h | 0.091944 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 24
1F/56 | CR09-3R-7 | Other data | Max. absorbed power | 178 | W | 0.178 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 24
1F/57-58 | CR17-4R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Identification | Model | CR17-4R-6 |  | CR17-4R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Capacity | Total capacity (cooling) | 3.73 | kW | 3.73 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Air | Flow rate | 825 | m3/h | 229.167 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Fluid | Flow rate | 396 | l/h | 0.11 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 25
1F/57-58 | CR17-4R-6 | Other data | Max. absorbed power | 253 | W | 0.253 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 25
FCU/2F/01-04 | CR26-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Identification | Model | CR26-3R-6 |  | CR26-3R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Capacity | Total capacity (cooling) | 6.12 | kW | 6.12 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Air | Flow rate | 1925 | m3/h | 534.722 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Fluid | Flow rate | 720 | l/h | 0.2 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 26
FCU/2F/01-04 | CR26-3R-6 | Other data | Max. absorbed power | 535 | W | 0.535 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 26
2F/05 | TO30-4R-3 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Identification | Model | TO30-4R-3 |  | TO30-4R-3 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Capacity | Total capacity (cooling) | 9.07 | kW | 9.07 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Air | Flow rate | 2646 | m3/h | 735 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Fluid | Flow rate | 972 | l/h | 0.27 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 27
2F/05 | TO30-4R-3 | Other data | Max. absorbed power | 770 | W | 0.77 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 27
2F/06-29 | CR26-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Identification | Model | CR26-3R-6 |  | CR26-3R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Capacity | Total capacity (cooling) | 4.45 | kW | 4.45 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Air | Flow rate | 1512 | m3/h | 420 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Fluid | Flow rate | 360 | l/h | 0.1 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 28
2F/06-29 | CR26-3R-6 | Other data | Max. absorbed power | 535 | W | 0.535 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 28
2F/30-33 | CR20-3R-6 | Identification | Manufacturer | Euroclima AG/Spa-Ges.m.b.H |  | Euroclima AG/Spa-Ges.m.b.H |  |  | rec:manufacturedBy | core | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Identification | Model | CR20-3R-6 |  | CR20-3R-6 |  |  | rec:modelNumber | core | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Capacity | Total capacity (cooling) | 2.95 | kW | 2.95 | unit:KiloW |  | brick:coolingCapacity | core | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Air | Flow rate | 902 | m3/h | 250.556 | unit:L-PER-SEC | m3/h / 3.6 | para:ratedSupplyAirFlowrate | core | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Fluid | Flow rate | 317 | l/h | 0.088056 | unit:L-PER-SEC | l/h / 3600 | para:ratedChilledWaterFlowrate | core | FCU_Manual.pdf | 29
2F/30-33 | CR20-3R-6 | Other data | Max. absorbed power | 294 | W | 0.294 | unit:KiloW | W / 1000 | brick:ratedPowerInput | core | FCU_Manual.pdf | 29

## Heat Exchangers
Heat Exchangers
Plate heat exchangers PHX/B/01 to PHX/B/04 - SCHEDULE OF HEAT EXCHANGER. Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
PHX/B/01 |  | Identification | Make | ALFA LAVAL |  | ALFA LAVAL |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/01 |  | CHW flow rate | Cold side | 62.8 | l/s | 62.8 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/01 |  | CHW flow rate | Hot side | 62.2 | l/s | 62.2 | unit:L-PER-SEC |  | para:ratedWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER | Brick 1.4 has no water-flowrate entity property at all; Dar Cairo's generic para: term is the next rung of the ladder and already exists
PHX/B/02 |  | Identification | Make | ALFA LAVAL |  | ALFA LAVAL |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/02 |  | CHW flow rate | Cold side | 62.8 | l/s | 62.8 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/02 |  | CHW flow rate | Hot side | 62.2 | l/s | 62.2 | unit:L-PER-SEC |  | para:ratedWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER | Brick 1.4 has no water-flowrate entity property at all; Dar Cairo's generic para: term is the next rung of the ladder and already exists
PHX/B/03 |  | Identification | Make | ALFA LAVAL |  | ALFA LAVAL |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/03 |  | CHW flow rate | Cold side | 62.8 | l/s | 62.8 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/03 |  | CHW flow rate | Hot side | 62.2 | l/s | 62.2 | unit:L-PER-SEC |  | para:ratedWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER | Brick 1.4 has no water-flowrate entity property at all; Dar Cairo's generic para: term is the next rung of the ladder and already exists
PHX/B/04 |  | Identification | Make | ALFA LAVAL |  | ALFA LAVAL |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/04 |  | CHW flow rate | Cold side | 62.8 | l/s | 62.8 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/04 |  | CHW flow rate | Hot side | 62.2 | l/s | 62.2 | unit:L-PER-SEC |  | para:ratedWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER | Brick 1.4 has no water-flowrate entity property at all; Dar Cairo's generic para: term is the next rung of the ladder and already exists
PHX/B/01 | T20-BFG | Identification | Model | T20-BFG |  | T20-BFG |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/01 | T20-BFG | Construction | Duty | 2350 | kW | 2350 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger Brick 1.4 has no heat-exchanger duty property; coolingCapacity is the Brick term and these exchangers deliver cooling to the secondary loop
PHX/B/02 | T20-BFG | Identification | Model | T20-BFG |  | T20-BFG |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/02 | T20-BFG | Construction | Duty | 2350 | kW | 2350 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger Brick 1.4 has no heat-exchanger duty property; coolingCapacity is the Brick term and these exchangers deliver cooling to the secondary loop
PHX/B/03 | T20-BFG | Identification | Model | T20-BFG |  | T20-BFG |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/03 | T20-BFG | Construction | Duty | 2350 | kW | 2350 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger Brick 1.4 has no heat-exchanger duty property; coolingCapacity is the Brick term and these exchangers deliver cooling to the secondary loop
PHX/B/04 | T20-BFG | Identification | Model | T20-BFG |  | T20-BFG |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/04 | T20-BFG | Construction | Duty | 2350 | kW | 2350 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger Brick 1.4 has no heat-exchanger duty property; coolingCapacity is the Brick term and these exchangers deliver cooling to the secondary loop
PHX/B/05 | M10-MFM | Identification | Model | M10-MFM |  | M10-MFM |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.3 - Heat Exchangers Equipment Schedule
PHX/B/05 | M10-MFM | Construction | Duty | 300 | kW | 300 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library | Per exchanger Brick 1.4 has no heat-exchanger duty property; coolingCapacity is the Brick term and these exchangers deliver cooling to the secondary loop
PHX/B/05 | M10-MFM | Thermal specification | Heat exchanged | 300 | kW | 300 | unit:KiloW |  | brick:coolingCapacity | core | Alfa Laval Plate Heat Exchanger Technical Specification (image supplied in chat) | PHX/B/05-300 KW A, M10-MFM, 5/21/2012 | same Brick term as the duty above

## Pumps
Pumps
Chilled water pumps CHWP/B/01 to CHWP/B/04 - SCHEDULE OF PUMPS, same drawing as the heat exchanger schedule. Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Identification | Make | ARMSTRONG |  | ARMSTRONG |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Identification | Model | 4600-STARFLO-125-380H-55KW |  | 4600-STARFLO-125-380H-55KW |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS | Designation ends in 55KW; the schedule states no motor rating of its own
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Performance | CHW flow rate | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Identification | Make | ARMSTRONG |  | ARMSTRONG |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Identification | Model | 4600-STARFLO-125-380H-55KW |  | 4600-STARFLO-125-380H-55KW |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS | Designation ends in 55KW; the schedule states no motor rating of its own
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Performance | CHW flow rate | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Identification | Make | ARMSTRONG |  | ARMSTRONG |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Identification | Model | 4600-STARFLO-125-380H-55KW |  | 4600-STARFLO-125-380H-55KW |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS | Designation ends in 55KW; the schedule states no motor rating of its own
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Performance | CHW flow rate | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Identification | Make | ARMSTRONG |  | ARMSTRONG |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Identification | Model | 4600-STARFLO-125-380H-55KW |  | 4600-STARFLO-125-380H-55KW |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS | Designation ends in 55KW; the schedule states no motor rating of its own
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Performance | CHW flow rate | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Duty flow | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Pump design | Duty head | 460 | kPa | 460000 | unit:PA | kPa x 1000 | para:ratedHead | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dar Cairo writes ratedHead in metres; this value is kPa
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor size | 55 | kW | 55 | unit:KiloW |  | brick:ratedPowerInput | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor speed | 1500 | rpm | 1500 | unit:RPM |  | para:ratedSpeed | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Duty flow | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Pump design | Duty head | 460 | kPa | 460000 | unit:PA | kPa x 1000 | para:ratedHead | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dar Cairo writes ratedHead in metres; this value is kPa
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor size | 55 | kW | 55 | unit:KiloW |  | brick:ratedPowerInput | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/02 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor speed | 1500 | rpm | 1500 | unit:RPM |  | para:ratedSpeed | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Duty flow | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Pump design | Duty head | 460 | kPa | 460000 | unit:PA | kPa x 1000 | para:ratedHead | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dar Cairo writes ratedHead in metres; this value is kPa
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor size | 55 | kW | 55 | unit:KiloW |  | brick:ratedPowerInput | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/03 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor speed | 1500 | rpm | 1500 | unit:RPM |  | para:ratedSpeed | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Duty flow | 62.3 | l/s | 62.3 | unit:L-PER-SEC |  | para:ratedChilledWaterFlowrate | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Pump design | Duty head | 460 | kPa | 460000 | unit:PA | kPa x 1000 | para:ratedHead | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW | Dar Cairo writes ratedHead in metres; this value is kPa
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor size | 55 | kW | 55 | unit:KiloW |  | brick:ratedPowerInput | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/04 | 4600-STARFLO-125-380H-55KW | Drive motor | Motor speed | 1500 | rpm | 1500 | unit:RPM |  | para:ratedSpeed | core | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW

## Exhaust Fans
Exhaust Fans
39 exhaust fans from the supplied schedule spreadsheet. Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
EF/2/01 | S6-315 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r2
EF/2/01 | S6-315 | Identification | Model | S6-315 |  | S6-315 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r2
EF/2/01 | S6-315 | Air | Air flow | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r2 | source writes '200 l/s' these are exhaust fans
KEF_B020 |  | Air | Air flow | 300 | l/s | 300 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r3 | these are exhaust fans
TEF_B01A | AXT80P-413A | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r4
TEF_B01A | AXT80P-413A | Identification | Model | AXT80P-413A |  | AXT80P-413A |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r4
TEF_B01A | AXT80P-413A | Air | Air flow | 1538 | l/s | 1538 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r4 | these are exhaust fans
TEF_B01B | AXT80P-413A | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r5
TEF_B01B | AXT80P-413A | Identification | Model | AXT80P-413A |  | AXT80P-413A |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r5
TEF_B01B | AXT80P-413A | Air | Air flow | 1538 | l/s | 1538 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r5 | these are exhaust fans
TEF_B02A | AXT71P-413A | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r6
TEF_B02A | AXT71P-413A | Identification | Model | AXT71P-413A |  | AXT71P-413A |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r6
TEF_B02A | AXT71P-413A | Air | Air flow | 970 | l/s | 970 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r6 | these are exhaust fans
TEF_B02B | AXT71P-413A | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r7
TEF_B02B | AXT71P-413A | Identification | Model | AXT71P-413A |  | AXT71P-413A |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r7
TEF_B02B | AXT71P-413A | Air | Air flow | 970 | l/s | 970 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r7 | these are exhaust fans
TEF_B03A | AXT35M-211A | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r8
TEF_B03A | AXT35M-211A | Identification | Model | AXT35M-211A |  | AXT35M-211A |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r8
TEF_B03A | AXT35M-211A | Air | Air flow | 400 | l/s | 400 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r8 | these are exhaust fans
TEF_B03B | AXT35M-211A | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r9
TEF_B03B | AXT35M-211A | Identification | Model | AXT35M-211A |  | AXT35M-211A |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r9
TEF_B03B | AXT35M-211A | Air | Air flow | 400 | l/s | 400 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r9 | these are exhaust fans
EF/RP/1 | AX71P-453A1 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r10
EF/RP/1 | AX71P-453A1 | Identification | Model | AX71P-453A1 |  | AX71P-453A1 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r10
EF/RP/1 | AX71P-453A1 | Air | Air flow | 5000 | l/s | 5000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r10 | these are exhaust fans
EF/RP/2 | AX71P-453A1 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r11
EF/RP/2 | AX71P-453A1 | Identification | Model | AX71P-453A1 |  | AX71P-453A1 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r11
EF/RP/2 | AX71P-453A1 | Air | Air flow | 5000 | l/s | 5000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r11 | these are exhaust fans
EF/RP/3 | AX71P-453A1 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r12
EF/RP/3 | AX71P-453A1 | Identification | Model | AX71P-453A1 |  | AX71P-453A1 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r12
EF/RP/3 | AX71P-453A1 | Air | Air flow | 5000 | l/s | 5000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r12 | these are exhaust fans
TEF_101C | S - Squrbo | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r13
TEF_101C | S - Squrbo | Identification | Model | S - Squrbo |  | S - Squrbo |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r13
TEF_102C | S - Squrbo | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r14
TEF_102C | S - Squrbo | Identification | Model | S - Squrbo |  | S - Squrbo |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r14
EF/BV/01 | AX719-41AKZ+0WE | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r15
EF/BV/01 | AX719-41AKZ+0WE | Identification | Model | AX719-41AKZ+0WE |  | AX719-41AKZ+0WE |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r15
EF/BV/01 | AX719-41AKZ+0WE | Air | Air flow | 330 | l/s | 330 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r15 | source writes '330L/S' these are exhaust fans
EF/BV/02 | AX719-41AKZ+0WE | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r16
EF/BV/02 | AX719-41AKZ+0WE | Identification | Model | AX719-41AKZ+0WE |  | AX719-41AKZ+0WE |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r16
EF/BV/02 | AX719-41AKZ+0WE | Air | Air flow | 330 | l/s | 330 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r16 | source writes '330L/S' these are exhaust fans
KEF_B019 |  | Air | Air flow | 1800 | l/s | 1800 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r17 | these are exhaust fans
KEF_101 |  | Air | Air flow | 1500 | l/s | 1500 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r18 | these are exhaust fans
EF/RP/4 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r19
EF/RP/4 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  | AX125CX-463A7-45 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r19
EF/RP/4 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r19 | these are exhaust fans
EF/RP/5 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r20
EF/RP/5 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  | AX125CX-463A7-45 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r20
EF/RP/5 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r20 | these are exhaust fans
EF/RP/6 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r21
EF/RP/6 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  | AX125CX-463A7-45 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r21
EF/RP/6 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r21 | these are exhaust fans
EF/RP/7 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r22
EF/RP/7 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  | AX125CX-463A7-45 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r22
EF/RP/7 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r22 | these are exhaust fans
EF/RP/8 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r23
EF/RP/8 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  | AX125CX-463A7-45 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r23
EF/RP/8 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r23 | these are exhaust fans
EF/RP/9 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r24
EF/RP/9 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  | AX125CX-463A7-45 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r24
EF/RP/9 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r24 | these are exhaust fans
EF/RP/10 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r25
EF/RP/10 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  | AX125CX-463A7-45 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r25
EF/RP/10 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r25 | these are exhaust fans
EF/RP/11 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r26
EF/RP/11 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  | AX125CX-463A7-45 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r26
EF/RP/11 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r26 | these are exhaust fans
EF/RP/12 | AX125CX-463A7-45 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r27
EF/RP/12 | AX125CX-463A7-45 | Identification | Model | AX125CX-463A7-45 |  | AX125CX-463A7-45 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r27
EF/RP/12 | AX125CX-463A7-45 | Air | Air flow | 35000 | l/s | 35000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r27 | these are exhaust fans
EF/B/4 | SQFA41-1 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r28
EF/B/4 | SQFA41-1 | Identification | Model | SQFA41-1 |  | SQFA41-1 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r28
EF/B/4 | SQFA41-1 | Air | Air flow | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r28 | these are exhaust fans
EF/B/5 | NALAF-150 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r29
EF/B/5 | NALAF-150 | Identification | Model | NALAF-150 |  | NALAF-150 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r29
EF/B/5 | NALAF-150 | Air | Air flow | 70 | l/s | 70 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r29 | these are exhaust fans
EF/B/6 | AX63F-413AFG1 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r30
EF/B/6 | AX63F-413AFG1 | Identification | Model | AX63F-413AFG1 |  | AX63F-413AFG1 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r30
EF/B/6 | AX63F-413AFG1 | Air | Air flow | 250 | l/s | 250 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r30 | these are exhaust fans
EF/B/7 | AX100CX-4H3A7I | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r31
EF/B/7 | AX100CX-4H3A7I | Identification | Model | AX100CX-4H3A7I |  | AX100CX-4H3A7I |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r31
EF/B/7 | AX100CX-4H3A7I | Air | Air flow | 11000 | l/s | 11000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r31 | these are exhaust fans
EF/B/8 | AX100CX-4H3A7I | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r32
EF/B/8 | AX100CX-4H3A7I | Identification | Model | AX100CX-4H3A7I |  | AX100CX-4H3A7I |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r32
EF/B/8 | AX100CX-4H3A7I | Air | Air flow | 11000 | l/s | 11000 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r32 | these are exhaust fans
EF/B/9 | AX80P-423A | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r33
EF/B/9 | AX80P-423A | Identification | Model | AX80P-423A |  | AX80P-423A |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r33
EF/B/9 | AX80P-423A | Air | Air flow | 2800 | l/s | 2800 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r33 | these are exhaust fans
EF/B/10 | AX40I-411A | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r34
EF/B/10 | AX40I-411A | Identification | Model | AX40I-411A |  | AX40I-411A |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r34
EF/B/10 | AX40I-411A | Air | Air flow | 475 | l/s | 475 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r34 | these are exhaust fans
EF/B/11 | EZPLATES 315-41 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r35
EF/B/11 | EZPLATES 315-41 | Identification | Model | EZPLATES 315-41 |  | EZPLATES 315-41 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r35
EF/B/11 | EZPLATES 315-41 | Air | Air flow | 90 | l/s | 90 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r35 | these are exhaust fans
EF/B/12 | S6-315 | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r36
EF/B/12 | S6-315 | Identification | Model | S6-315 |  | S6-315 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r36
EF/B/12 | S6-315 | Air | Air flow | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r36 | these are exhaust fans
EF/B/13 | AX63F-411A | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r37
EF/B/13 | AX63F-411A | Identification | Model | AX63F-411A |  | AX63F-411A |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r37
EF/B/13 | AX63F-411A | Air | Air flow | 810 | l/s | 810 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r37 | source writes '810L/S' these are exhaust fans
EF/B/14 | AX63D-411A | Identification | Manufacturer | NUAIRE |  | NUAIRE |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r38
EF/B/14 | AX63D-411A | Identification | Model | AX63D-411A |  | AX63D-411A |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r38
EF/B/14 | AX63D-411A | Air | Air flow | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedExhaustAirFlowrate | core | Book1.xlsx | Sheet1 r38 | these are exhaust fans
EF/B/15 | Cmveco 315/315 | Identification | Manufacturer | COLASIT |  | COLASIT |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r39
EF/B/15 | Cmveco 315/315 | Identification | Model | Cmveco 315/315 |  | Cmveco 315/315 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r39
EF/B/16 | Cmveco 125/125 | Identification | Manufacturer | COLASIT |  | COLASIT |  |  | rec:manufacturedBy | core | Book1.xlsx | Sheet1 r40
EF/B/16 | Cmveco 125/125 | Identification | Model | Cmveco 125/125 |  | Cmveco 125/125 |  |  | rec:modelNumber | core | Book1.xlsx | Sheet1 r40

## Generators
Generators
One standby diesel generator from the GENERATOR ASSET LIST, a multi-equipment asset register. Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
GENERATOR SET | 4012-46TAG3A | Identification | Manufacturer | CTM |  | CTM |  |  | rec:manufacturedBy | core | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Identification | Model number | 4012-46TAG3A |  | 4012-46TAG3A |  |  | rec:modelNumber | core | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | 4012-46TAG3A | Maintenance | Date installed | Jun-12 |  | Jun-12 |  |  | rec:installationDate | core | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST

## Pressurization Unit
Pressurization Unit
PU/B/01 - SCHEDULE OF PRESSURIZATION UNIT, same drawing as the heat exchanger and pump schedules. Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
PU/B/01 | 3750 2 EM-S | Identification | Make | ARMSTRONG |  | ARMSTRONG |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PRESSURIZATION UNIT
PU/B/01 | 3750 2 EM-S | Identification | Model | 3750 2 EM-S |  | 3750 2 EM-S |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PRESSURIZATION UNIT
PU/B/01 |  | Expansion tank | Make | Armstrong |  | Armstrong |  |  | rec:manufacturedBy | core | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 |  | Expansion tank | Model | Reflex DE10 |  | Reflex DE10 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 |  | Expansion tank | Capacity | 1000 | litre | 1000 | unit:L | unit not used in Dar Cairo | para:Rated_Tank_Level | core | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule | chosen by the user. Note brick:volume exists in Brick 1.4 and by the ladder would outrank a para: term for a tank volume - reversible in one line if the team prefers it
PU/B/01 |  | Pressurisation unit | Make | Armstrong |  | Armstrong |  |  | rec:manufacturedBy | core | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 |  | Pressurisation unit | Model | 3750 2 EM-S |  | 3750 2 EM-S |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule

## CAV Units
CAV Units
Constant air volume boxes across six schedules on level 1F and the basement. Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
CAV/1F/S11/001 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/001 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/001 | NBOQOB250 | Air | Air flow (per box) | 300 | l/s | 300 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/002 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/002 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/002 | NBOQOB200 | Air | Air flow (per box) | 175 | l/s | 175 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/004 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/004 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/004 | NBOQOB200 | Air | Air flow (per box) | 190 | l/s | 190 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/006 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/006 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/006 | NBOQOB160 | Air | Air flow (per box) | 165 | l/s | 165 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/007 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/007 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/007 | NBOQOB160 | Air | Air flow (per box) | 165 | l/s | 165 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/008 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/008 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/008 | NBOQOB200 | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/009 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/009 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S11/009 | NBOQOB200 | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S11)
CAV/1F/S15/002 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/002 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/002 | NBOQOB160 | Air | Air flow (per box) | 151 | l/s | 151 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/004 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/004 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/004 | NBOQOB160 | Air | Air flow (per box) | 225 | l/s | 225 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/005 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/005 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/005 | NBOQOB200 | Air | Air flow (per box) | 185 | l/s | 185 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/006 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/006 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/006 | NBOQOB200 | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/007 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/007 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S15/007 | NBOQOB200 | Air | Air flow (per box) | 315 | l/s | 315 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S11/005 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S11/005 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S11/005 | NBOQOB200 | Air | Air flow (per box) | 190 | l/s | 190 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/B/S14/03 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/03 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/03 | NBOQOB250 | Air | Air flow (per box) | 305 | l/s | 305 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/04 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/04 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/04 | NBOQOB250 | Air | Air flow (per box) | 305 | l/s | 305 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/05 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/05 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S14/05 | NBOQOB250 | Air | Air flow (per box) | 305 | l/s | 305 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S14/03-05)
CAV/B/S13/004 |  | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S13/005 |  | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S14/001 |  | Air | Air flow (per box) | 125 | l/s | 125 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S14/002 |  | Air | Air flow (per box) | 250 | l/s | 250 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S15/001 |  | Air | Air flow (per box) | 125 | l/s | 125 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S15/002 |  | Air | Air flow (per box) | 125 | l/s | 125 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S15/003 |  | Air | Air flow (per box) | 125 | l/s | 125 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S13-S15)
CAV/B/S12/001 |  | Air | Air flow (per box) | 105 | l/s | 105 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/001 |  | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/002 |  | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/003 |  | Air | Air flow (per box) | 200 | l/s | 200 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/006 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/007 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/008 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/012 |  | Air | Air flow (per box) | 50 | l/s | 50 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/013 |  | Air | Air flow (per box) | 50 | l/s | 50 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/014 |  | Air | Air flow (per box) | 70 | l/s | 70 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/015 |  | Air | Air flow (per box) | 150 | l/s | 150 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/016 |  | Air | Air flow (per box) | 285 | l/s | 285 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/017 |  | Air | Air flow (per box) | 145 | l/s | 145 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/018 |  | Air | Air flow (per box) | 145 | l/s | 145 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/019 |  | Air | Air flow (per box) | 190 | l/s | 190 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/020 |  | Air | Air flow (per box) | 150 | l/s | 150 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S13/021 |  | Air | Air flow (per box) | 85 | l/s | 85 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (B, S12/S13)
CAV/B/S12/002 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)
CAV/B/S12/002 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)
CAV/B/S12/002 | NBOQOB250 | Air | Air flow (per box) | 292 | l/s | 292 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)
CAV/B/S12/003 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)
CAV/B/S12/003 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)
CAV/B/S12/003 | NBOQOB250 | Air | Air flow (per box) | 292 | l/s | 292 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV (B, S12/002-003)

## VAV Units
VAV Units
Variable air volume boxes across six schedules on level 1F and the basement. Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
VAV/1F/S15/005 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/005 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/005 | NBOQOB250 | Air | Air flow (per box) | 290 | l/s | 290 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/006 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/006 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/006 | NBOQOB250 | Air | Air flow (per box) | 290 | l/s | 290 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/007 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/007 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/007 | NBOQOB250 | Air | Air flow (per box) | 290 | l/s | 290 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/008 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/008 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/008 | NBOQOB250 | Air | Air flow (per box) | 290 | l/s | 290 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/009 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/009 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/009 | NBOQOB250 | Air | Air flow (per box) | 290 | l/s | 290 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/001 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/001 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/001 | NBOQOB200 | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/002 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/002 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/002 | NBOQOB200 | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/003 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/003 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/003 | NBOQOB200 | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/004 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/004 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/004 | NBOQOB250 | Air | Air flow (per box) | 243 | l/s | 243 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/005 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/005 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/005 | NBOQOB250 | Air | Air flow (per box) | 243 | l/s | 243 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/022 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/022 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/022 | NBOQOB200 | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/006 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/006 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/006 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/007 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/007 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/007 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/008 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/008 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/008 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/009 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/009 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/009 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/010 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/010 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/010 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/011 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/011 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/011 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/012 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/012 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/012 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/013 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/013 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/013 | NBOQOB160 | Air | Air flow (per box) | 164 | l/s | 164 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/014 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/014 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/014 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/015 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/015 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/015 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/016 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/016 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/016 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/017 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/017 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/017 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/018 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/018 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/018 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/019 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/019 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/019 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/020 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/020 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/020 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/021 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/021 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/021 | NBOQOB200 | Air | Air flow (per box) | 219 | l/s | 219 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/012 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/012 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/012 | NBOQOB200 | Air | Air flow (per box) | 120 | l/s | 120 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/023 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/023 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/023 | NBOQOB160 | Air | Air flow (per box) | 147 | l/s | 147 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/024 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/024 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/024 | NBOQOB160 | Air | Air flow (per box) | 147 | l/s | 147 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/001 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/001 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/001 | NBOQOB200 | Air | Air flow (per box) | 257 | l/s | 257 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/002 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/002 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/002 | NBOQOB200 | Air | Air flow (per box) | 257 | l/s | 257 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/003 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/003 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/003 | NBOQOB200 | Air | Air flow (per box) | 257 | l/s | 257 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/004 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/004 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/004 | NBOQOB200 | Air | Air flow (per box) | 257 | l/s | 257 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/006 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/006 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/007 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/007 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/008 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/008 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/009 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/009 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/010 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/010 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/011 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/011 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/012 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/012 |  | Air | Air flow (per box) | 120 | l/s | 120 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/013 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/013 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/013 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/016 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/016 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/016 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/017 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/017 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/017 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/018 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/018 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/018 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/019 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/019 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/019 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/020 | NBOQOB200 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/020 | NBOQOB200 | Identification | Model | NBOQOB200 |  | NBOQOB200 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/020 | NBOQOB200 | Air | Air flow (per box) | 174 | l/s | 174 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/021 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/021 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/022 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/022 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/023 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/023 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/024 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/024 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/025 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/025 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/025 | NBOQOB160 | Air | Air flow (per box) | 60 | l/s | 60 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/026 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/026 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/026 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/027 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/027 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/027 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/028 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/028 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/028 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/029 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/029 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/029 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/030 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/030 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/030 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/031 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/031 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/031 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/032 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/032 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/032 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/033 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/033 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/033 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/034 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/034 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/034 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/035 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/035 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/035 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/036 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/036 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/036 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/037 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/037 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/037 | NBOQOB160 | Air | Air flow (per box) | 138 | l/s | 138 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/039 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/039 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/039 | NBOQOB160 | Air | Air flow (per box) | 160 | l/s | 160 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/040 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/040 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/040 | NBOQOB160 | Air | Air flow (per box) | 160 | l/s | 160 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/014 | NBOQOB250 | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB250 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB250 | Identification | Model | NBOQOB250 |  | NBOQOB250 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/015 | NBOQOB250 | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/038 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/038 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S15/038 | NBOQOB160 | Air | Air flow (per box) | 60 | l/s | 60 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S11/025 | NBOQOB160 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S11/025 | NBOQOB160 | Identification | Model | NBOQOB160 |  | NBOQOB160 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/1F/S11/025 | NBOQOB160 | Air | Air flow (per box) | 147 | l/s | 147 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/B/S10/020 |  | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/020 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/021 |  | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/021 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/022 |  | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/022 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/023 |  | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/023 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/001 |  | Air | Air flow (per box) | 261 | l/s | 261 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/001 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/002 |  | Air | Air flow (per box) | 261 | l/s | 261 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/002 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/003 |  | Air | Air flow (per box) | 261 | l/s | 261 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/003 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/004 |  | Air | Air flow (per box) | 261 | l/s | 261 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/004 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/005 |  | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/005 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/006 |  | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/006 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/007 |  | Air | Air flow (per box) | 78 | l/s | 78 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/007 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/008 |  | Air | Air flow (per box) | 227 | l/s | 227 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/008 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/009 |  | Air | Air flow (per box) | 143 | l/s | 143 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/009 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/010 |  | Air | Air flow (per box) | 179 | l/s | 179 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/010 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/011 |  | Air | Air flow (per box) | 262 | l/s | 262 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/011 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/012 |  | Air | Air flow (per box) | 262 | l/s | 262 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/012 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S10/020 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/020 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/020 | NBOQE03 | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/021 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/021 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/021 | NBOQE03 | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/022 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/022 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/022 | NBOQE03 | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/023 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/023 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S10/023 | NBOQE03 | Air | Air flow (per box) | 249 | l/s | 249 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/001 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/001 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/001 | NBOQE03 | Air | Air flow (per box) | 251 | l/s | 251 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/002 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/002 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/002 | NBOQE03 | Air | Air flow (per box) | 251 | l/s | 251 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/003 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/003 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/003 | NBOQE03 | Air | Air flow (per box) | 251 | l/s | 251 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/004 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/004 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/004 | NBOQE03 | Air | Air flow (per box) | 251 | l/s | 251 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/005 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/005 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/005 | NBOQE03 | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/006 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/006 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/006 | NBOQE03 | Air | Air flow (per box) | 240 | l/s | 240 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/007 |  | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/007 |  | Air | Air flow (per box) | 78 | l/s | 78 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/008 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/008 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/008 | NBOQE03 | Air | Air flow (per box) | 227 | l/s | 227 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/009 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/009 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/009 | NBOQE03 | Air | Air flow (per box) | 143 | l/s | 143 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/010 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/010 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/010 | NBOQE03 | Air | Air flow (per box) | 179 | l/s | 179 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/011 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/011 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/011 | NBOQE03 | Air | Air flow (per box) | 262 | l/s | 262 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/012 | NBOQE03 | Identification | Make | HC BARCOL-AIR |  | HC BARCOL-AIR |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/012 | NBOQE03 | Identification | Model | NBOQE03 |  | NBOQE03 |  |  | rec:modelNumber | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/012 | NBOQE03 | Air | Air flow (per box) | 262 | l/s | 262 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S14/001 |  | Air | Air flow (per box) | 230 | l/s | 230 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/001 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/002 |  | Air | Air flow (per box) | 230 | l/s | 230 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/002 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/003 |  | Air | Air flow (per box) | 230 | l/s | 230 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/003 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/004 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/004 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/005 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/005 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/006 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/006 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/007 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/007 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/008 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/008 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/009 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/009 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/010 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/010 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/011 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/011 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/012 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/012 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/013 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/013 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/014 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/014 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/015 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/015 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/016 |  | Air | Air flow (per box) | 170 | l/s | 170 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/016 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/017 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/017 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/018 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/018 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/019 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/019 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/020 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/020 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S21 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S21 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/025 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/025 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/026 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/026 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/027 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/027 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/028 |  | Air | Air flow (per box) | 128 | l/s | 128 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/028 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/029 |  | Air | Air flow (per box) | 160 | l/s | 160 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/029 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/022 |  | Air | Air flow (per box) | 136 | l/s | 136 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/022 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/023 |  | Air | Air flow (per box) | 136 | l/s | 136 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/023 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/024 |  | Air | Air flow (per box) | 136 | l/s | 136 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/024 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/030 |  | Air | Air flow (per box) | 136 | l/s | 136 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/030 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/031 |  | Air | Air flow (per box) | 136 | l/s | 136 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S14/031 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/003 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/003 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/004 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/004 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/005 |  | Air | Air flow (per box) | 220 | l/s | 220 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/005 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/007 |  | Air | Air flow (per box) | 99 | l/s | 99 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/007 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/008 |  | Air | Air flow (per box) | 95 | l/s | 95 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S13/008 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/001 |  | Air | Air flow (per box) | 246 | l/s | 246 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/001 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/008 |  | Air | Air flow (per box) | 246 | l/s | 246 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/008 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/009 |  | Air | Air flow (per box) | 262 | l/s | 262 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/009 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/010 |  | Air | Air flow (per box) | 254 | l/s | 254 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/010 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/011 |  | Air | Air flow (per box) | 254 | l/s | 254 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/011 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/012 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/012 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/013 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/013 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/014 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/014 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/015 |  | Air | Air flow (per box) | 300 | l/s | 300 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/015 |  | Heating | Heating capacity | 1 | kW | 1 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/016 |  | Air | Air flow (per box) | 212 | l/s | 212 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/016 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/017 |  | Air | Air flow (per box) | 212 | l/s | 212 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/017 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/018 |  | Air | Air flow (per box) | 212 | l/s | 212 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/018 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/019 |  | Air | Air flow (per box) | 215 | l/s | 215 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/019 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S11/001 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/001 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/001 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/002 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/002 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/002 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/003 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/003 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/003 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/004 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/004 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/004 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/005 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/005 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/005 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/006 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/006 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/006 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/007 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/007 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/007 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/008 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/008 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/008 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/009 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/009 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/009 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/010 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/010 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/010 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/011 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/011 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/011 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/012 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/012 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/012 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/013 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/013 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/013 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/014 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/014 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/014 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/015 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/015 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/015 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/016 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/016 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/016 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/017 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/017 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/017 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/018 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/018 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/018 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/019 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/019 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/019 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/020 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/020 |  | Air | Air flow (per box) | 194 | l/s | 194 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/020 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/021 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/021 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/021 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/022 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/022 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/022 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/023 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/023 |  | Air | Air flow (per box) | 260 | l/s | 260 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/023 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/024 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/024 |  | Air | Air flow (per box) | 86 | l/s | 86 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/024 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/025 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/025 |  | Air | Air flow (per box) | 86 | l/s | 86 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/025 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/026 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/026 |  | Air | Air flow (per box) | 100 | l/s | 100 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/026 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/027 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/027 |  | Air | Air flow (per box) | 100 | l/s | 100 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/027 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/028 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/028 |  | Air | Air flow (per box) | 90 | l/s | 90 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/028 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/029 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/029 |  | Air | Air flow (per box) | 90 | l/s | 90 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/029 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/030 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/030 |  | Air | Air flow (per box) | 90 | l/s | 90 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/030 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/031 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/031 |  | Air | Air flow (per box) | 90 | l/s | 90 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/031 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/032 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/032 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/032 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/033 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/033 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/033 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/034 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/034 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/034 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/035 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/035 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/035 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/036 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/036 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/036 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/037 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/037 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/037 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/038 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/038 |  | Air | Air flow (per box) | 120 | l/s | 120 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/038 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/039 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/039 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/039 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/040 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/040 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/040 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/041 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/041 |  | Air | Air flow (per box) | 80 | l/s | 80 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/041 |  | Heating | Heating capacity | 0.5 | kW | 0.5 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/042 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/042 |  | Air | Air flow (per box) | 120 | l/s | 120 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/042 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/043 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/043 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/043 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/044 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/044 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/044 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/045 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/045 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/045 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/046 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/046 |  | Air | Air flow (per box) | 224 | l/s | 224 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S11/046 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/001 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/001 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/001 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/002 |  | Identification | Make | TITUS USA |  | TITUS USA |  |  | rec:manufacturedBy | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/002 |  | Air | Air flow (per box) | 155 | l/s | 155 | unit:L-PER-SEC |  | para:ratedSupplyAirFlowrate | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)
VAV/B/S13/002 |  | Heating | Heating capacity | 0.75 | kW | 0.75 | unit:KiloW |  | para:ratedReheatCapacity | core | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S11/S13 - TITUS)

## DX Units
DX Units
21 DX split systems from the schematic riser, with indoor and outdoor models from SYSTEM DETAILS Table 3. Core rows only - every row here maps to an ontology predicate. The full transcription is in the full-metadata workbook.
Equipment Tag | Model | Component | Property | Value (as printed) | Unit (as printed) | Value (Dar Cairo) | Unit (QUDT) | Conversion | Ontology predicate | Scope | Source File | Page | Note
DX/B/01 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  | PEAD-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/01 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  | PUHZ-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/01 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/02 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  | PEAD-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/02 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  | PUHZ-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/02 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/05 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  | PEAD-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/05 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  | PUHZ-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/05 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/06 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  | PEAD-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/06 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  | PUHZ-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/06 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/03 | PEAD-RP400 | Identification | Indoor unit model | PEAD-RP400 |  | PEAD-RP400 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/03 | PEAD-RP400 | Refrigeration | Outdoor unit model | PUHZ-RP200X2 |  | PUHZ-RP200X2 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | X2 suffix - two condensers per indoor unit goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/03 | PEAD-RP400 | Air | Number of speeds | 2 | n | 2 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/04 | PEAD-RP400 | Identification | Indoor unit model | PEAD-RP400 |  | PEAD-RP400 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/04 | PEAD-RP400 | Refrigeration | Outdoor unit model | PUHZ-RP200X2 |  | PUHZ-RP200X2 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | X2 suffix - two condensers per indoor unit goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/04 | PEAD-RP400 | Air | Number of speeds | 2 | n | 2 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/14 | PEAD-RP400 | Identification | Indoor unit model | PEAD-RP400 |  | PEAD-RP400 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/14 | PEAD-RP400 | Refrigeration | Outdoor unit model | PUHZ-RP200X2 |  | PUHZ-RP200X2 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | X2 suffix - two condensers per indoor unit goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/14 | PEAD-RP400 | Air | Number of speeds | 2 | n | 2 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/07 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  | PEAD-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/07 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  | PUHZ-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/07 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/16 | PEAD-RP35 | Identification | Indoor unit model | PEAD-RP35 |  | PEAD-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/16 | PEAD-RP35 | Refrigeration | Outdoor unit model | PUHZ-RP35 |  | PUHZ-RP35 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/16 | PEAD-RP35 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/08 | PEAD-RP500 | Identification | Indoor unit model | PEAD-RP500 |  | PEAD-RP500 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/08 | PEAD-RP500 | Refrigeration | Outdoor unit model | PUHZ-RP2S0X2 |  | PUHZ-RP2S0X2 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | X2 suffix - two condensers per indoor unit goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/08 | PEAD-RP500 | Air | Number of speeds | 2 | n | 2 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/09 | PEAD-RP500 | Identification | Indoor unit model | PEAD-RP500 |  | PEAD-RP500 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/09 | PEAD-RP500 | Refrigeration | Outdoor unit model | PUHZ-RP250X2 |  | PUHZ-RP250X2 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | X2 suffix - two condensers per indoor unit goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/09 | PEAD-RP500 | Air | Number of speeds | 2 | n | 2 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/10 | PEAD-RP125 | Identification | Indoor unit model | PEAD-RP125 |  | PEAD-RP125 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/10 | PEAD-RP125 | Refrigeration | Outdoor unit model | PUHZ-RP125 |  | PUHZ-RP125 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/10 | PEAD-RP125 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/11 | PCA-RP71 | Identification | Indoor unit model | PCA-RP71 |  | PCA-RP71 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/11 | PCA-RP71 | Refrigeration | Outdoor unit model | PUHZ-RP71 |  | PUHZ-RP71 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/11 | PCA-RP71 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/12 | PEAD-RP50 | Identification | Indoor unit model | PEAD-RP50 |  | PEAD-RP50 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/12 | PEAD-RP50 | Refrigeration | Outdoor unit model | PUHZ-RP50 |  | PUHZ-RP50 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/12 | PEAD-RP50 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/13 | PCA-RP71 | Identification | Indoor unit model | PCA-RP71 |  | PCA-RP71 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/13 | PCA-RP71 | Refrigeration | Outdoor unit model | PUHZ-RP71 |  | PUHZ-RP71 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/13 | PCA-RP71 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages
DX/B/15 | PCA-RP71 | Identification | Indoor unit model | PCA-RP71 |  | PCA-RP71 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/15 | PCA-RP71 | Refrigeration | Outdoor unit model | PUHZ-RP71 |  | PUHZ-RP71 |  |  | rec:modelNumber | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | goes on a brick:Condensing_Unit entity - Brick 1.4 carries that class, so no para: is needed
DX/B/15 | PCA-RP71 | Air | Number of speeds | 3 | n | 3 | unit:UNITLESS |  | brick:operationalStageCount | core | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule | Brick 1.4 entity property - a 3-speed fan has 3 operational stages

## Open Items
Open Items
Data quality findings from the source documents. None of these are triples, but each one affects rows that are. Read before writing the ontology.
Equipment Tag | Finding | Detail | Source File | Page
AHU-011 | Drawing anomaly | Item 3 ELECTRIC COIL appears twice: the first block is an unfilled template (TOTAL CAPACITY=POW, STAGES=NST, ENTERING AIR=AON, LEAVING AIR=AOF, description cell reads BLOCKHEIGHT). The second, populated block is recorded here. | ahu_2.pdf | 3
CC/B/05,06,07 | Source anomaly | Sheet heading reads 'M5DUA + 2 x HCR59'; the Unit row of the same sheet reads 'M5DOA + 2 x HCR59'. Heading value recorded. | qnl_closed_control_units_manual.pdf | 8
MCG-10P | Source conflict | Specification sheet (page 2) states size 500 (w) x 650 (d) x 650 (h) mm, while dimension drawing MCG10P-1 (page 6) shows 475 W x 430 D x 400 H mm. Confirm with the manufacturer before using either as nameplate data. | climate_control_units_manual.pdf | 2
B/02 | Sheet note | Only sheet with VERSION 'CPI'; casing dimensions (1980 x 665 x 285) also differ from the CPR sheets. | FCU_Manual.pdf | 3
1F/55 | Sheet note | Dimensions row order differs on this sheet: Max Width 1800, Max Height 920, Max Thickness 420. Compare with the other TO50 sheets (920 / 420 / 1800) before use. | FCU_Manual.pdf | 23
PHX/B/01 | Source reference | The supplied image crops the drawing title block, so the drawing number, sheet number and revision are not recorded. Ask for the sheet reference before handover. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/01 | Schedule scope | The schedule gives dimensions, operating weight and CHW flow rate only. It states no duty, no plate count, no design pressure and no connection sizes - those were not inferred. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF HEAT EXCHANGER
PHX/B/01 | A fifth exchanger | The drawing schedule carries PHX/B/01 to PHX/B/04 only. The Alfa Laval data and the SYSTEM DETAILS schedule both add PHX/B/05, a 300 kW M10-MFM described as the 'Main HEX'. It is included here on that basis. | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/01 | Duty split | SYSTEM DETAILS names PHX/B/01 to 03 as duty, PHX/B/04 as standby and PHX/B/05 as the main HEX. The drawing schedule states no duty split. | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/01 | Temperature conflict on PHX/B/05 | SYSTEM DETAILS gives one hot-side figure across all five rows - 15.5 degC in, 6.5 degC out. The Alfa Laval specification for the M10-MFM gives 50.0 degC in, 20.0 degC out on the hot side. The cold side agrees at 5.5 in / 14.4 out. Both are recorded against their own source; the conflict is unresolved. | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/01 | Weights cross-check | The Alfa Laval net operating weight for the T20-BFG, 4430 kg, and its overall dimensions, 2735 x 780 x 2165 mm, both match the drawing schedule exactly. | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
PHX/B/01 | Flow rate is per unit | The drawing schedule's 62.8 / 62.2 l/s is per exchanger. The Alfa Laval sheet gives 2350 kW per T20-BFG. | Alfa Laval plate heat exchanger data (image supplied in chat) | PHE construction comparison - QF Central Library
CHWP/B/01 | Source reference | The supplied image crops the drawing title block, so the drawing number, sheet number and revision are not recorded. Ask for the sheet reference before handover. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | Motor rating | The model designation ends in '55KW', which reads as a 55 kW motor. The schedule states no motor rating of its own, so no rated-power property was created from it. Confirm against the pump submittal before writing brick:ratedPowerInput. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | Schedule scope | The schedule gives no head, no speed, no efficiency and no electrical data - those were not inferred. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PUMPS
CHWP/B/01 | Submittal dimensions are imperial | The dimensional block is headed '(in, lb) NOT for CONSTRUCTION'. Values are inches and pounds and are converted on that basis. The block is marked not for construction, so do not build to it. | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | Weight disagreement | The submittal gives 1874 lb, which is 850 kg. The drawing schedule gives 843 kg. A 7 kg difference - probably a different scope of supply (baseplate, coupling guard) rather than an error, but neither document says. | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | Dimension callouts are unlabelled | D, HA, HB, HC and the rest are letters keyed to the outline drawing. The submittal does not say which feature each measures, so they are recorded as callouts rather than named dimensions. | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | Duty and standby | The SYSTEM DETAILS schedule names CHWP-B-01 to 03 as duty pumps and CHWP-B-04 as the standby. That matches the submittal's 'Pump Run Qty 3' against 'Qty 4'. | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | Alternate tag shape | The SYSTEM DETAILS schedule writes the tags with dashes (CHWP-B-01) where the drawing schedule writes slashes (CHWP/B/01). The slash form is used as the tag here because it matches every other reference in this workbook; the dash form is recorded against each pump as an alternate reference. Confirm which the BMS uses. | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
CHWP/B/01 | Tag Num on the submittal | The submittal's 'Tag Num' field reads BP#7A, which is the Education City building package reference, not a pump tag. It does not identify an individual pump. | Armstrong submittal TENDER301358.1 rev3 (image supplied in chat) | Page 14/22 - 4600 Starflo-125-380H-55 kW
KEF_B020 | Model and manufacturer | not stated in the source sheet | Book1.xlsx | Sheet1 r3
TEF_101C | Air flow | not stated in the source sheet | Book1.xlsx | Sheet1 r13
TEF_102C | Air flow | not stated in the source sheet | Book1.xlsx | Sheet1 r14
KEF_B019 | Model and manufacturer | not stated in the source sheet | Book1.xlsx | Sheet1 r17
KEF_101 | Model and manufacturer | not stated in the source sheet | Book1.xlsx | Sheet1 r18
EF/B/15 | Air flow | not stated in the source sheet | Book1.xlsx | Sheet1 r39
EF/B/16 | Air flow | not stated in the source sheet | Book1.xlsx | Sheet1 r40
EF/2/01 | Identifier shapes | Two families are in use and neither is a typo: 28 tags are slash separated (EF/B/nn, EF/RP/n, EF/BV/nn, EF/2/01) and 11 are underscore separated (TEF_B01A, KEF_B020, TEF_101C, KEF_101). Tags are the BMS join key, so both were kept exactly as written. Confirm which shape the BMS actually uses before the ontology is built. | Book1.xlsx | Sheet1
EF/2/01 | Whitespace | 'EF/2/01 ' carries a trailing space in the source. Stripped, per the rule that whitespace is the only thing changed on a supplied identifier. | Book1.xlsx | Sheet1
EF/2/01 | Numbering gap | EF/B numbering runs 4 to 16; there is no EF/B/1, EF/B/2 or EF/B/3 in the sheet. Either they are scheduled elsewhere or the list is partial - worth confirming. | Book1.xlsx | Sheet1
EF/2/01 | Air flow spelling | The source writes the unit as both 'l/s' and 'L/S', and sometimes with no space ('330L/S'). All are litres per second; the value was parsed and the unit normalised. | Book1.xlsx | Sheet1
EF/2/01 | Missing data | KEF_B020, KEF_B019 and KEF_101 have no model and no manufacturer. TEF_101C, TEF_102C, EF/B/15 and EF/B/16 have no air flow. Those properties are left out rather than filled with a typical value. | Book1.xlsx | Sheet1
GENERATOR SET | One generator, not a truncated list | The image cuts off partway through the row below, but the user has confirmed that row belongs to a different piece of equipment. The asset list is a multi-equipment register rather than a generator inventory, so the single row transcribed here is the complete record for this generator. | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | Asset tag is not unique | The ASSET TAG NUMBER column holds the words 'GENERATOR SET', the same text as the EQUIPMENT NAME column. It does not identify one machine, so it cannot serve as the join key to the BMS the way every other tag in this workbook does. Ask for the real asset tag. | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | Serial number | The serial number 11 211 038571-16 is specific to one machine, so this row does describe a single generator even though its tag does not name one. | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | Model | CTM 4012-46TAG3A is a Perkins 4012-46TAG3A engine badged by CTM. The list states the manufacturer as CTM; the engine builder was not inferred into the data. | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | Date installed | Given as 'Jun-12' - month and year, no day. | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
GENERATOR SET | Deferred fields | PM procedure, procedure document and recommended spare parts all read 'REFER O&M'. The O&M manual is where those live; nothing was invented for them. | GENERATOR ASSET LIST (image supplied in chat) | GENERATOR ASSET LIST
PU/B/01 | Source reference | The supplied image crops the drawing title block, so the drawing number, sheet number and revision are not recorded. Ask for the sheet reference before handover. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PRESSURIZATION UNIT
PU/B/01 | Column mismatch | The column is headed SYSTEM VOLUME but holds the text 'WITH 10BAR PRESSURE & 1000L TANK' - a pressure and a tank size, not a system volume. Recorded verbatim; the system volume the header asks for is not stated anywhere on the schedule. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF PRESSURIZATION UNIT
PU/B/01 | Column mismatch resolved | The drawing schedule's SYSTEM VOLUME cell reads 'WITH 10BAR PRESSURE & 1000L TANK'. SYSTEM DETAILS Table 3.2 explains it: the assembly is an Armstrong 3750 2 EM-S pressurisation unit rated 10 bar plus a Reflex DE10 expansion tank of 1000 litre. Those are now recorded as two components. The system volume the column header asks for is still not stated on either document. | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
PU/B/01 | Alternate tag | SYSTEM DETAILS tags the assembly PRO1 where the drawing schedule tags it PU/B/01. The drawing form is used here because it matches the rest of the workbook; PRO1 is recorded as an alternate reference. Confirm which the BMS uses. | SYSTEM DETAILS (image supplied in chat) | Table 3.2 - Pressurisation Unit Equipment Schedule
CAV/1F/S11/005 | Row note | Box 005 is absent from the other 1F schedule, which jumps 004 to 006. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF CAV UNITS (1F, S15/S11)
CAV/1F/S11/001 | Source reference | All six CAV schedules were supplied as drawing images with the title block cropped out, so no drawing number, sheet or revision is recorded against any row. | MEP schedule drawing (image supplied in chat) | all CAV schedules
CAV/1F/S11/001 | Reference format | The header reads CAV/FLOOR/AHU NO/BOX NO, so CAV/1F/S11/001 is floor 1F, AHU S11, box 001. Air flow is stated per box. | MEP schedule drawing (image supplied in chat) | all CAV schedules
CAV/1F/S11/001 | Box number width | Most schedules use three-digit box numbers (001); the CAV/B/S14 schedule uses two digits (03, 04, 05). Both kept as written - the tag is the BMS join key. | MEP schedule drawing (image supplied in chat) | all CAV schedules
CAV/1F/S11/001 | Numbering gaps | CAV/1F/S11 runs 001, 002, 004, 005, 006-007, 008-009 once both 1F drawings are read together - box 003 is on neither. CAV/B/S13 runs 001-008 then 012-021, so boxes 009, 010 and 011 are absent. | MEP schedule drawing (image supplied in chat) | all CAV schedules
CAV/1F/S11/001 | Schedule scope | The basement S13-S15 and S12/S13 schedules state no model and no make; those columns do not exist on them. Nothing was carried across from the schedules that do. | MEP schedule drawing (image supplied in chat) | all CAV schedules
VAV/1F/S11/022 | Row note | Governs box 022. Confirmed by the user against the overlapping VAV/1F/S11/022 TO 24 row on the same schedule. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/012 | Reference and quantity disagree | single reference but QTY is 2 - the schedule does not name the other boxes | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S11/023 | Row note | Covers boxes 023 and 024 only. Box 022 is governed by the standalone VAV/1F/S11/022 row on the same schedule, per the user's decision. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S11/S15)
VAV/1F/S15/014 | Row note | Overlaps VAV/1F/S15/013 TO 020 on the same schedule, which gives these boxes 174 l/s on NBOQOB200. Unresolved. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (1F, S15/S11 - second drawing)
VAV/B/S15/001 | Row note | The model-and-make drawing of the same schedule gives 251 l/s for these boxes. Unresolved. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - heating capacity)
VAV/B/S15/001 | Row note | The heating-capacity drawing of the same schedule gives 261 l/s for these boxes. Unresolved. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S15/007 | Row note | Model cell is blank on this schedule; every other row on it reads NBOQE03. | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S15 - model and make)
VAV/B/S14/009 TO 012 | Reference and quantity disagree | reference spans 4 boxes but QTY is 2 | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/B/S10/001 & 008 | Reference and quantity disagree | reference spans 2 boxes but QTY is 8 | MEP schedule drawing (image supplied in chat) | SCHEDULE OF VAV UNITS (B, S10/S13/S14)
VAV/1F/S15/005 | Source reference | All six VAV schedules were supplied as drawing images with the title block cropped out, so no drawing number, sheet or revision is recorded against any row. | MEP schedule drawing (image supplied in chat) | all VAV schedules
VAV/1F/S15/005 | Reference format | The header reads VAV/FLOOR/AHU NO/BOX NO. Air flow is stated per VAV box, so a range row carries that flow on each of its boxes, not across them. | MEP schedule drawing (image supplied in chat) | all VAV schedules
VAV/1F/S15/005 | Duplicate box 022 - resolved | VAV/1F/S11/022 appears twice on the 1F schedule. The user confirmed the standalone row governs: 220 l/s on NBOQOB200. The overlapping 'VAV/1F/S11/022 TO 24' row is therefore read as covering boxes 023 and 024 only. | MEP schedule drawing (image supplied in chat) | all VAV schedules
VAV/1F/S15/005 | Rows excluded on instruction | Five rows carrying box numbers far outside the range their schedule otherwise uses were dropped at the user's direction: VAV/1F/S15/395, VAV/1F/S11/088 and VAV/1F/S11/096-098 from the first 1F schedule, and VAV/1F/S11/088 TO 087 and VAV/1F/S15/096 TO 098 from the second. | MEP schedule drawing (image supplied in chat) | all VAV schedules
VAV/1F/S15/005 | Overlapping drawings - S10/S15 | Two drawings schedule the same basement boxes. One carries heating capacity, the other model and make, and they disagree on VAV/B/S15/001 TO 004 (261 l/s against 251 l/s). Both are recorded against their own drawing; neither was picked. | MEP schedule drawing (image supplied in chat) | all VAV schedules
VAV/1F/S15/005 | Overlapping rows - 1F/S15 | On the second 1F schedule, VAV/1F/S15/014 TO 015 (240 l/s, NBOQOB250) falls inside VAV/1F/S15/013 TO 020 (174 l/s, NBOQOB200). Both are recorded. | MEP schedule drawing (image supplied in chat) | all VAV schedules
VAV/1F/S15/005 | Box 012 disagreement | VAV/1F/S15/012 is scheduled at 120 l/s on both 1F drawings, but the first states QTY 02 and the second QTY 01 for a single-box reference. | MEP schedule drawing (image supplied in chat) | all VAV schedules
VAV/1F/S15/005 | Missing boxes | VAV/B/S14 runs 001-020 then 022-031, so box 021 is absent. On the second 1F schedule VAV/1F/S15 runs 001-004 then 006-011, so box 005 is absent there - though the first 1F schedule does carry VAV/1F/S15/005 TO 009. | MEP schedule drawing (image supplied in chat) | all VAV schedules
VAV/1F/S15/005 | Reference shape | VAV/B/S21 has no floor or box segment, unlike every other reference on its schedule. Kept as written - the tag is the BMS join key. | MEP schedule drawing (image supplied in chat) | all VAV schedules
VAV/1F/S15/005 | Schedule scope | No single schedule carries every column. The 1F drawings give model and make but no heating capacity; the basement S10/S13/S14 and S11/S13 drawings give heating capacity but no model. Nothing was carried across between drawings. | MEP schedule drawing (image supplied in chat) | all VAV schedules
DX/B/17 | Model not stated | This unit is on the schematic but not on SYSTEM DETAILS Table 3.6, which stops at DX/B/16. No indoor or outdoor model is available for it. | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/18 | Model not stated | This unit is on the schematic but not on SYSTEM DETAILS Table 3.6, which stops at DX/B/16. No indoor or outdoor model is available for it. | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/19 | Model not stated | This unit is on the schematic but not on SYSTEM DETAILS Table 3.6, which stops at DX/B/16. No indoor or outdoor model is available for it. | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/20 | Model not stated | This unit is on the schematic but not on SYSTEM DETAILS Table 3.6, which stops at DX/B/16. No indoor or outdoor model is available for it. | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/RP/21 | Model not stated | This unit is on the schematic but not on SYSTEM DETAILS Table 3.6, which stops at DX/B/16. No indoor or outdoor model is available for it. | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/01 | Source reference | Read off a schematic riser supplied as an image, not from a schedule. No drawing number, sheet or revision is recorded. Ask for the sheet reference before handover. | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/01 | Cooling figure is a room load | Each cooling figure is printed on the room box, not on an indoor unit. Where a room is served by two or three units the schematic does not say how the load divides, so the figure is recorded against every unit serving that room as a room load. Do not write it as a per-unit brick:coolingCapacity without the equipment schedule. | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/01 | Indoor to outdoor pairing - superseded | The schematic numbers condensers to match their indoor units, which suggested DX/B/nn pairs with DX/OD/nn. SYSTEM DETAILS Table 3.6 shows that does not hold for every unit - five take an X2 outdoor model, meaning two condensers each. See the pairing correction note against the equipment schedule. | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/01 | Standby marking disagreement | DX/OD/05 is marked (ST.BY) at the condenser row, but DX/B/05 carries no standby marking at the indoor row. One of the two is wrong; the drawing does not say which. Recorded as printed on each side. | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/01 | Room design condition | Tr is the room design temperature and the paired figure is design relative humidity - 50% on every room on this schematic. | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/01 | Drainage | The trash chamber units carry the note 'TO NEAREST DRAIN, AS REFER TO PIPE WORK LAYOUT PLAN (TYPICAL)'. No condensate route is scheduled on this drawing. | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/01 | Scope | The schematic states no model, no make, no electrical data and no air flow for any DX unit. Those were not inferred - the equipment schedule is still needed. | DX split system schematic (image supplied in chat) | DX SPLIT SYSTEM SCHEMATIC
DX/B/01 | Pairing correction | The schematic numbers condensers to match their indoor units, and this workbook previously recorded DX/B/nn as paired one-to-one with DX/OD/nn on that basis. Table 3.6 shows that is not right for every unit: DX/B/03, 04 and 14 each take a PUHZ-RP200X2 and DX/B/08 and 09 each take a PUHZ-RP250X2, where the X2 suffix means two condensers per indoor unit. Those five units need two DX/OD tags each, and the schematic's numbering does not say which two. The pipework layout plan is still needed. | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/01 | Schedule is partial | Table 3.6 covers DX/B/01 to DX/B/16. DX/B/17, 18, 19, 20 and DX/RP/21 are on the schematic but not on this schedule, so they still carry no model. | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/01 | Location granularity | Table 3.6 writes 'MV Room, HV Room' for DX/B/01, 02, 05, 06, 07 and 16, where the schematic separates MV ROOM (01, 02), HV ROOM (05, 06) and MV ROOM 3 (07, 16). The two do not conflict - the schedule is simply coarser. The schematic's room is kept as the served space and the schedule's text is recorded alongside it. | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/01 | Probable typo | DX/B/08 reads PUHZ-RP2S0X2. DX/B/09 has the same indoor unit in the same room and reads PUHZ-RP250X2, so the 'S' is almost certainly a misprint for '5'. Recorded as printed; confirm before ordering. | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule
DX/B/01 | Manufacturer not stated | The PEAD, PCA and PUHZ prefixes are Mitsubishi Electric Mr. Slim naming, but Table 3.6 has no manufacturer column and no other document supplied names one. No manufacturer property was created from the model prefix alone. | SYSTEM DETAILS (image supplied in chat) | Table 3.6 - Split DX Units Equipment Schedule

## Ontology Scope
Ontology Scope
Which transcribed properties belong in the ontology. Targets are the predicates Dar Cairo, QF SSC and QF HQ actually use for equipment metadata - about twenty in total. Everything else is engineering reference, kept but not modelled.
Scope | Ontology predicate | Predicate source | Component | Property | Rows | Sheets
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Capacity | Total capacity (cooling) | 28 | FCU
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Construction | Duty | 5 | Heat Exchangers
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Cooling coil | Total capacity | 15 | AHU
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | External auxiliary cooling coil | Total capacity | 1 | AHU
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Thermal specification | Heat exchanged | 1 | Heat Exchangers
core | brick:coolingCapacity | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Unit performance | Total cooling capacity | 5 | Closed Control Units
core | brick:operationalStageCount | Brick 1.4 - not yet used by any reference model | Air | Number of speeds | 16 | DX Units
core | brick:ratedCurrentInput | Brick 1.4 - not yet used by any reference model | Return fan drive motor | Full load current | 7 | AHU
core | brick:ratedCurrentInput | Brick 1.4 - not yet used by any reference model | Supply fan drive motor | Full load current | 15 | AHU
core | brick:ratedPowerInput | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Drive motor | Motor size | 4 | Pumps
core | brick:ratedPowerInput | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Other data | Max. absorbed power | 28 | FCU
core | brick:ratedPowerInput | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Return fan drive motor | Rating | 7 | AHU
core | brick:ratedPowerInput | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Supply fan drive motor | Rating | 15 | AHU
core | brick:ratedPowerInput | Brick 1.4 - also used by Dar Cairo, SSC, HQ | Unit performance | Unit power input | 5 | Closed Control Units
core | para:Rated_Tank_Level | para: - Dar Cairo 3; brick:volume would outrank it by the ladder | Expansion tank | Capacity | 1 | Pressurization Unit
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | CHW flow rate | Cold side | 4 | Heat Exchangers
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | CW coil | Unit fluid flow | 1 | Closed Control Units
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | Cooling coil | Water flow | 15 | AHU
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | Design condition | Unit fluid flow | 1 | Closed Control Units
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | External auxiliary cooling coil | Water flow | 1 | AHU
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | Fluid | Flow rate | 28 | FCU
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | Performance | CHW flow rate | 4 | Pumps
core | para:ratedChilledWaterFlowrate | para: - Dar Cairo 83 (Brick has no water flowrate) | Pump design | Duty flow | 4 | Pumps
core | para:ratedExhaustAirFlowrate | para: - Dar Cairo 18 (Brick has no air flowrate) | Air | Air flow | 35 | Exhaust Fans
core | para:ratedExhaustAirFlowrate | para: - Dar Cairo 18 (Brick has no air flowrate) | Return fan | Air flow | 7 | AHU
core | para:ratedHead | para: - Dar Cairo 41 (Brick has no head) | Pump design | Duty head | 4 | Pumps
core | para:ratedReheatCapacity | para: - SSC 108, HQ 602 (Brick has no reheat capacity) | Electric coil | Total capacity | 15 | AHU
core | para:ratedReheatCapacity | para: - SSC 108, HQ 602 (Brick has no reheat capacity) | Heating | Heating capacity | 113 | VAV Units
core | para:ratedReheatCapacity | para: - SSC 108, HQ 602 (Brick has no reheat capacity) | Option - electrical re-heating | Max re-heating capacity | 5 | Closed Control Units
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Drive motor | Motor speed | 4 | Pumps
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Return fan | Speed | 7 | AHU
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Return fan drive motor | Full load speed | 7 | AHU
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Supply fan | Speed | 15 | AHU
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Supply fan drive motor | Full load speed | 15 | AHU
core | para:ratedSpeed | para: - Dar Cairo 7 (Brick Rotational_Speed is a quantity, not a property) | Technical data | Speed | 1 | Climate Control Units
core | para:ratedSupplyAirFlowrate | para: - Dar Cairo 81, SSC 113, HQ 628 (Brick has no air flowrate) | Air | Air flow (per box) | 243 | CAV Units, VAV Units
core | para:ratedSupplyAirFlowrate | para: - Dar Cairo 81, SSC 113, HQ 628 (Brick has no air flowrate) | Air | Flow rate | 28 | FCU
core | para:ratedSupplyAirFlowrate | para: - Dar Cairo 81, SSC 113, HQ 628 (Brick has no air flowrate) | Design condition | Unit airflow | 5 | Closed Control Units
core | para:ratedSupplyAirFlowrate | para: - Dar Cairo 81, SSC 113, HQ 628 (Brick has no air flowrate) | Supply fan | Air flow | 15 | AHU
core | para:ratedWaterFlowrate | para: - Dar Cairo 34 (Brick has no water flowrate) | CHW flow rate | Hot side | 4 | Heat Exchangers
core | para:refrigerant | para: - Dar Cairo 2 | Design condition | Refrigerant | 4 | Closed Control Units
core | rec:installationDate | REC - Dar Cairo 494 | Maintenance | Date installed | 1 | Generators
core | rec:manufacturedBy | REC - Dar Cairo 449, SSC 7, HQ 42 | Expansion tank | Make | 1 | Pressurization Unit
core | rec:manufacturedBy | REC - Dar Cairo 449, SSC 7, HQ 42 | Identification | Make | 163 | CAV Units, Heat Exchangers, Pressurization Unit, Pumps, VAV Units
core | rec:manufacturedBy | REC - Dar Cairo 449, SSC 7, HQ 42 | Identification | Manufacturer | 73 | Climate Control Units, Closed Control Units, Exhaust Fans, FCU, Generators
core | rec:manufacturedBy | REC - Dar Cairo 449, SSC 7, HQ 42 | Pressurisation unit | Make | 1 | Pressurization Unit
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Cooling coil | Model | 15 | AHU
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Expansion tank | Model | 1 | Pressurization Unit
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Identification | Indoor unit model | 16 | DX Units
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Identification | Model | 176 | CAV Units, Climate Control Units, Closed Control Units, Exhaust Fans, FCU, Heat Exchangers, Pressurization Unit, Pumps, VAV Units
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Identification | Model number | 1 | Generators
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Pressurisation unit | Model | 1 | Pressurization Unit
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Refrigeration | Outdoor unit model | 16 | DX Units
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Return fan | Fan model | 7 | AHU
core | rec:modelNumber | REC - Dar Cairo 411, SSC 126, HQ 777 | Supply fan | Fan model | 15 | AHU

## Units
Units
Source unit to Dar Cairo unit. Targets read off reference-models/DarCairo_V93.csv - air and water flow both land on unit:L-PER-SEC, power on unit:KiloW, length on unit:M.
Unit (as printed) | Unit (QUDT) | Factor applied | Used in Dar Cairo | Dar Cairo uses (rows) | Note
kW | unit:KiloW | x 1 | yes | 1593
W | unit:KiloW | / 1000 | yes | 1593 | W / 1000
A | unit:A | x 1 | yes | 227
V | unit:V | x 1 | yes | 451
V DC | unit:V | x 1 | yes | 451 | DC noted in the property name
Hz | unit:HZ | x 1 | yes | 61
degC | unit:DEG_C | x 1 | yes | 883
m3/s | unit:L-PER-SEC | x 1000 | yes | 535 | m3/s x 1000
m3/h | unit:L-PER-SEC | / 3.6 | yes | 535 | m3/h / 3.6
l/h | unit:L-PER-SEC | / 3600 | yes | 535 | l/h / 3600
l/s | unit:L-PER-SEC | x 1 | yes | 535
kg/s | unit:L-PER-SEC | x 1 | yes | 535 | water mass flow taken as volume flow at density 1 kg/l; chilled water at 7-15 degC is ~0.9997 kg/l, a 0.03% difference
Pa | unit:PA | x 1 | yes | 172
kPa | unit:PA | x 1000 | yes | 172 | kPa x 1000
mbar | unit:PA | x 100 | yes | 172 | mbar x 100
bar | unit:BAR | x 1 | yes
psig | unit:PA | x 6894.76 | yes | 172 | psi x 6894.757; the submittal states it as gauge pressure
mm | unit:M | / 1000 | yes | 47 | mm / 1000
m | unit:M | x 1 | yes | 47
in | unit:M | / 39.3701 | yes | 47 | in x 0.0254
m2 | unit:M2 | x 1 | yes | 755
litre | unit:L | x 1 | NO
rpm | unit:RPM | x 1 | yes | 21
hours | unit:HR | x 1 | yes | 613
dB | unit:DeciB | x 1 | yes | 171
dB(A) | unit:DeciB | x 1 | yes | 171 | A-weighting kept in the property name
n | unit:UNITLESS | x 1 | yes | 3376
set(s) | unit:UNITLESS | x 1 | yes | 3376
kg | unit:KiloGM | x 1 | NO
lb | unit:KiloGM | / 2.20462 | NO |  | lb x 0.45359237
kg/h | unit:KiloGM-PER-HR | x 1 | NO
g/h | unit:KiloGM-PER-HR | / 1000 | NO |  | g/h / 1000
m/s | unit:M-PER-SEC | x 1 | NO
kg/m3 | unit:KiloGM-PER-M3 | x 1 | NO
kJ/(kg*K) | unit:KiloJ-PER-KiloGM-K | x 1 | NO
W/(m*K) | unit:W-PER-M-K | x 1 | NO
W/m2 K | unit:W-PER-M2-K | x 1 | NO
cP | unit:CentiP | x 1 | NO
K | unit:K | x 1 | NO |  | temperature difference, not a temperature
BSP | (none) |  | n/a |  | thread designation, not a quantity
V-ph-Hz | (none) |  | n/a |  | composite nameplate string, not a quantity
% | unit:PERCENT_RH | x 1 | yes | 79 | used when the property is a relative humidity
% | unit:PERCENT | x 1 | yes | 708 | used for every other percentage
(none printed) | unit:UNITLESS | x 1 | yes | 3376 | dimensionless ratios - SHR, EER, COP, fan speed setting
Highlighted rows are QUDT units Dar Cairo has never used - it carries no mass, mass-flow or velocity quantity. They are genuine QUDT terms, not minted ones, but the PARA team should confirm them before handover.