## SSC BMS allocation
Register row | Register tag | BMS tag | Room per BMS (col J) | Col D (drawings) | Col H (VAV/FCU list) | Compared against | Finding | BMS screen | Read confidence
1318 | AHUB_0001 | AHU-B-0001 | B.013 CHILLED WATER | CHILLED WATER B.013 |  | CHILLED WATER B.013 | confirms the register | BF-part1 | ok
1319 | AHUB_0002 | AHU-B-0002 | B.014 VENT PLANT | VENT PLANT B.014 |  | VENT PLANT B.014 | confirms the register | BF-part1 | ok
1320 | AHUB_0003 | AHU-B-0003 | B.014 VENT PLANT | VENT PLANT B.014 |  | VENT PLANT B.014 | confirms the register | BF-part1 | ok
1321 | AHUB_0004 | AHU-B-0004 | B.008 VENT PLANT | VENT PLANT B.008 |  | VENT PLANT B.008 | confirms the register | BF-part2 | ok
1322 | AHUB_0005 | AHU-B-0005 | B.014 VENT PLANT | CHILLED WATER B.013 |  | CHILLED WATER B.013 | ROOM NUMBER DIFFERS | BF-part1 | ok
1323 | FCU0001 | FCU-0001 | B.016 SPRINKLER AND WATER | SPRINKLER AND WATER B.016 | SPRINKLER & WATER RM B.016 | SPRINKLER & WATER RM B.016 | confirms the register | BF-part1 | ok
1324 | FCU0002 | FCU-0002 | B.025 MAIN SEC CONTROL ROOM | MAIN SEC. CONTROL ROOM B.025 |  | MAIN SEC. CONTROL ROOM B.025 | confirms the register | BF-part1 | ok
1325 | FCU0003 | FCU-0003 | B.030 CORRIDOR | B.M.S B.039 | BMS B.039 | BMS B.039 | ROOM NUMBER DIFFERS | BF-part1 | check
1327 | FCU0005 | FCU-0005 | 01.027 IDF-1 | IDF-1 1.027 |  | IDF-1 1.027 | confirms the register | FF-part2 | ok
1329 | FCU0007 | FCU-0007 | 01.039 IDF-2 | IDF-2 1.039 |  | IDF-2 1.039 | confirms the register | FF-part2 | ok
1332 | FCU0010 | FCU-0010 | 01.013 CORRIDOR | CORRIDOR 1.010 | AIR LOCK 1.011 | AIR LOCK 1.011 | ROOM NUMBER DIFFERS | FF-part1 | ok
1334 | VAV0001 | VAV-0001 | B.015 ENTRANCE | ENTRANCE B.015 |  | ENTRANCE B.015 | confirms the register | BF-part1 | ok
1335 | VAV0002 | VAV-0002 | 01.014 SHELL SPACE | SHARED OFFICE 01.014 | SHELL SPACE NW 01.014 | SHELL SPACE NW 01.014 | confirms the register | FF-part1 | ok
1336 | VAV0003 | VAV-0003 | 01.014 SHELL SPACE | SHARED OFFICE 01.014 |  | SHARED OFFICE 01.014 | confirms the register | FF-part1 | ok
1337 | VAV0004 | VAV-0004 | 01.014 SHELL SPACE | SHARED OFFICE 01.014 |  | SHARED OFFICE 01.014 | confirms the register | FF-part1 | ok
1338 | VAV0005 | VAV-0005 | 01.015 SHELL SPACE | SHARED OFFICE 01.015 | SHELL SPACE SW 01.015 | SHELL SPACE SW 01.015 | confirms the register | FF-part1 | ok
1339 | VAV0006 | VAV-0006 | 01.015 SHELL SPACE | SHARED OFFICE 01.015 |  | SHARED OFFICE 01.015 | confirms the register | FF-part1 | ok
1340 | VAV0007 | VAV-0007 | 01.015 SHELL SPACE | SHARED OFFICE 01.015 |  | SHARED OFFICE 01.015 | confirms the register | FF-part1 | ok
1341 | VAV0008 | VAV-0008 | 01.024 CORRIDOR | CORRIDOR 01.024 | CORRIDORS SE 01.024 | CORRIDORS SE 01.024 | confirms the register | FF-part2 | ok
1342 | VAV0009 | VAV-0009 | 01.002 SHELL SPACE | PRAYER ROOM 01.019 |  | PRAYER ROOM 01.019 | ROOM NUMBER DIFFERS | FF-part1 | ok
1343 | VAV0010 | VAV-0010 | 01.019 PRAYER ROOM | PRAYER ROOM 01.019 |  | PRAYER ROOM 01.019 | confirms the register | FF-part1 | ok
1345 | VAV0012 | VAV-0012 | 01.019 PRAYER ROOM | PRAYER ROOM 01.019 |  | PRAYER ROOM 01.019 | confirms the register | FF-part1 | ok
1346 | VAV0013 | VAV-0013 | 01.019 PRAYER ROOM | PRAYER ROOM 01.019 |  | PRAYER ROOM 01.019 | confirms the register | FF-part2 | ok
1347 | VAV0014 | VAV-0014 | 01.019 PRAYER ROOM | PRAYER ROOM 01.019 |  | PRAYER ROOM 01.019 | confirms the register | FF-part2 | check
1348 | VAV0015 | VAV-0015 | 01.029 SHELL SPACE | ROOM NO 42 | SHELL SPACE E 01.029 | SHELL SPACE E 01.029 | confirms the register | FF-part2 | ok
1349 | VAV0016 | VAV-0016 | 01.029 SHELL SPACE | ROOM NO 43 |  | ROOM NO 43 | could not compare room numbers | FF-part2 | ok
1350 | VAV0017 | VAV-0017 | 01.029 SHELL SPACE | ROOM NO 44 |  | ROOM NO 44 | could not compare room numbers | FF-part2 | ok
1351 | VAV0018 | VAV-0018 | 01.029 SHELL SPACE | SHARED OFFICE 01.029 |  | SHARED OFFICE 01.029 | confirms the register | FF-part2 | ok
1352 | VAV0019 | VAV-0019 | 01.029 SHELL SPACE | SHARED OFFICE 01.029 |  | SHARED OFFICE 01.029 | confirms the register | FF-part2 | ok
1354 | VAV0021 | VAV-0021 | 01.013 CORRIDOR | CORRIDOR 01.013 | CORRIDORS W 01.013 | CORRIDORS W 01.013 | confirms the register | FF-part1 | ok
1357 | VAV0024 | VAV-0024 | 01.003 OPEN SPACE | CORRIDOR 01.001 | CORRIDORS S 01.001 | CORRIDORS S 01.001 | ROOM NUMBER DIFFERS | FF-part1 | ok
1358 | VAV0025 | VAV-0025 | 01.002 SHELL SPACE | TEAM SPACE 01.002 |  | TEAM SPACE 01.002 | confirms the register | FF-part1 | ok
1360 | VAV0027 | VAV-0027 | 01.002 SHELL SPACE | TEAM SPACE 01.002 |  | TEAM SPACE 01.002 | confirms the register | FF-part2 | ok
1361 | VAV0028 | VAV-0028 | 01.002 SHELL SPACE | TEAM SPACE 01.002 | OPEN OFFICE BELOW SKYLIGHT 01.003 | OPEN OFFICE BELOW SKYLIGHT 01.003 | ROOM NUMBER DIFFERS | FF-part2 | ok
1362 | VAV0029 | VAV-0029 | 01.003 OPEN SPACE | CORRIDOR 01.001 |  | CORRIDOR 01.001 | ROOM NUMBER DIFFERS | FF-part2 | ok
1363 | VAV0030 | VAV-0030 | 01.016 SHELL SPACE | PRINT COPY 01.016 | PRINTING ROOM SHELL SPACE 01.016 | PRINTING ROOM SHELL SPACE 01.016 | confirms the register | FF-part1 | ok
1364 | VAV0031 | VAV-0031 | 01.003 OPEN SPACE | CORRIDOR 01.001 |  | CORRIDOR 01.001 | ROOM NUMBER DIFFERS | FF-part1 | ok
1365 | VAV0032 | VAV-0032 | 01.018 CORRIDOR | CORRIDOR 01.018 | CORRIDORS SW 01.018 | CORRIDORS SW 01.018 | confirms the register | FF-part1 | ok
1366 | VAV0033 | VAV-0033 | 01.025 MALE TOILET | CORRIDOR 01.028 | IDF 01.027 & 39 | IDF 01.027 & 39 | ROOM NUMBER DIFFERS | FF-part2 | ok
1367 | VAV0034 | VAV-0034 | 01.003 OPEN SPACE | OPEN SPACE 01.003 | CORRIDOR CENTRAL 01.004 | CORRIDOR CENTRAL 01.004 | ROOM NUMBER DIFFERS | FF-part1 | ok
1368 | VAV0035 | VAV-0035 | 01.028 CORRIDOR | CORRIDOR 01.010 | CORRIDORS E 01.028 | CORRIDORS E 01.028 | confirms the register | FF-part2 | ok
1369 | VAV0036 | VAV-0036 | 01.019 PRAYER ROOM | ABLUTION ROOM 01.022 | ABLUTION ROOMS 01.020 & 23 | ABLUTION ROOMS 01.020 & 23 | ROOM NUMBER DIFFERS | FF-part2 | ok
1372 | VAV0039 | VAV-0039 | 01.028 CORRIDOR | OPEN SPACE 01.003 | CORRIDOR AUDITORIUM E 01.035 | CORRIDOR AUDITORIUM E 01.035 | ROOM NUMBER DIFFERS | FF-part2 | check
1373 | VAV0040 | VAV-0040 | 02.006 CONFERENCE ROOM | CONFERENCE ROOM 02.006 |  | CONFERENCE ROOM 02.006 | confirms the register | Second Floor | ok
1374 | VAV0041 | VAV-0041 | 02.005 EXECUTIVE CONFERENCE ROOM | EXECUTIVE CONFERENCE ROOM 02.005 |  | EXECUTIVE CONFERENCE ROOM 02.005 | confirms the register | Second Floor | ok
1375 | VAV0042 | VAV-0042 | 02.005 EXECUTIVE CONFERENCE ROOM | EXECUTIVE CONFERENCE ROOM 02.005 |  | EXECUTIVE CONFERENCE ROOM 02.005 | confirms the register | Second Floor | ok
1379 | VAV0046 | VAV-0046 | 02.002 LOBBY | LOBBY 02.002 |  | LOBBY 02.002 | confirms the register | Second Floor | check
1380 | VAV0047 | VAV-0047 | 02.002 LOBBY | LOBBY 02.002 |  | LOBBY 02.002 | confirms the register | Second Floor | check
1381 | VAV0048 | VAV-0048 | 02.002 LOBBY | LOBBY 02.002 |  | LOBBY 02.002 | confirms the register | Second Floor | ok
1382 | VAV0049 | VAV-0049 | 02.003 CORRIDOR | LOBBY 02.002 |  | LOBBY 02.002 | ROOM NUMBER DIFFERS | Second Floor | ok
1383 | VAV0050 | VAV-0050 | 02.002 LOBBY | CORRIDOR 02.003 |  | CORRIDOR 02.003 | ROOM NUMBER DIFFERS | Second Floor | check
1384 | VAV0051 | VAV-0051 | 02.005 EXECUTIVE CONFERENCE ROOM | EXECUTIVE CONFERENCE ROOM 02.005 |  | EXECUTIVE CONFERENCE ROOM 02.005 | confirms the register | Second Floor | check
1385 | VAV0052 | VAV-0052 | 02.006 CONFERENCE ROOM | CONFERENCE ROOM 02.006 |  | CONFERENCE ROOM 02.006 | confirms the register | Second Floor | ok
1386 | VAV0053 | VAV-0053 | 03.015 RESEARCHER OFFICE | RESEARCHER OFFICE 03.015 |  | RESEARCHER OFFICE 03.015 | confirms the register | TF-part1 | ok
1387 | VAV0054 | VAV-0054 | 03.014 VISITORS CUBIDE | VISITOR'S CUBICLE 03.014 |  | VISITOR'S CUBICLE 03.014 | confirms the register | TF-part1 | ok
1388 | VAV0055 | VAV-0055 | 03.013 RESEARCHER OFFICE | RESEARCHER OFFICE 03.013 |  | RESEARCHER OFFICE 03.013 | confirms the register | TF-part1 | ok
1389 | VAV0056 | VAV-0056 | 03.012 RESEARCHER OFFICE | RESEARCHER OFFICE 03.012 |  | RESEARCHER OFFICE 03.012 | confirms the register | TF-part1 | ok
1390 | VAV0057 | VAV-0057 | 03.011 VISITORS CUBIDE | VISITOR'S CUBICLE 03.011 |  | VISITOR'S CUBICLE 03.011 | confirms the register | TF-part1 | ok
1391 | VAV0058 | VAV-0058 | 03.010 RESEARCHER OFFICE | RESEARCHER OFFICE 03.010 |  | RESEARCHER OFFICE 03.010 | confirms the register | TF-part1 | ok
1392 | VAV0059 | VAV-0059 | 03.009 RESEARCHER OFFICE | RESEARCHER OFFICE 03.009 |  | RESEARCHER OFFICE 03.009 | confirms the register | TF-part1 | check
1393 | VAV0060 | VAV-0060 | 03.008 VISITORS CUBIDE | VISITOR'S CUBICLE 03.008 |  | VISITOR'S CUBICLE 03.008 | confirms the register | TF-part1 | ok
1394 | VAV0061 | VAV-0061 | 03.007 OPERATIONS MANAGERS | OPERATION MANAGERS 03.007 |  | OPERATION MANAGERS 03.007 | confirms the register | TF-part1 | ok
1395 | VAV0062 | VAV-0062 | 03.006A ROOM | ROOM 03.006B |  | ROOM 03.006B | ROOM NUMBER DIFFERS | TF-part2 | ok
1404 | VAV0071 | VAV-0071 | 03.032 GENERAL OFFICE AREA | GENERAL OFFICE AREA 03.002 |  | GENERAL OFFICE AREA 03.002 | ROOM NUMBER DIFFERS | TF-part2 | ok
1405 | VAV0072 | VAV-0072 | 03.032 GENERAL OFFICE AREA | GENERAL OFFICE AREA 03.002 |  | GENERAL OFFICE AREA 03.002 | ROOM NUMBER DIFFERS | TF-part2 | ok
1408 | VAV0075 | VAV-0075 | 03.032 GENERAL OFFICE AREA | GENERAL OFFICE AREA 03.002 |  | GENERAL OFFICE AREA 03.002 | ROOM NUMBER DIFFERS | TF-part2 | ok
1410 | VAV0077 | VAV-0077 | 03.032 GENERAL OFFICE AREA | GENERAL OFFICE AREA 03.002 |  | GENERAL OFFICE AREA 03.002 | ROOM NUMBER DIFFERS | TF-part2 | ok
1411 | VAV0078 | VAV-0078 | 03.031 ASSOC.DIR OFFICE | ASSOC. DOR. OFFICE 03.031 |  | ASSOC. DOR. OFFICE 03.031 | confirms the register | TF-part2 | check
1413 | VAV0080 | VAV-0080 | 03.030 ASSOC.DIR MEETING ROOM | ASSOC. DIR. MEETING ROOM 03.030 |  | ASSOC. DIR. MEETING ROOM 03.030 | confirms the register | TF-part2 | ok
1414 | VAV0081 | VAV-0081 | 03.029 RESEARCHER OFFICE | RESEARCHER OFFICE 03.029 |  | RESEARCHER OFFICE 03.029 | confirms the register | TF-part2 | ok
1415 | VAV0082 | VAV-0082 | 03.028 VISITORS CUBIDE | VISITOR'S CUBICLE 03.028 |  | VISITOR'S CUBICLE 03.028 | confirms the register | TF-part2 | ok
1416 | VAV0083 | VAV-0083 | 03.027 RESEARCHER OFFICE | RESEARCHER OFFICE 03.027 |  | RESEARCHER OFFICE 03.027 | confirms the register | TF-part2 | ok
1418 | VAV0085 | VAV-0085 | 03.026 MEETING ROOM | MEETING ROOM 03.026 |  | MEETING ROOM 03.026 | confirms the register | TF-part2 | ok
1419 | VAV0086 | VAV-0086 | 03.026 MEETING ROOM | MEETING ROOM 03.026 |  | MEETING ROOM 03.026 | confirms the register | TF-part2 | ok
1420 | VAV0087 | VAV-0087 | 03.025 SECRETARIAL AREA | SECRETARIAL AREA 03.025 |  | SECRETARIAL AREA 03.025 | confirms the register | TF-part1 | ok
1421 | VAV0088 | VAV-0088 | 03.024 VISITORS CUBIDE | VISITOR'S CUBICLE 03.024 |  | VISITOR'S CUBICLE 03.024 | confirms the register | TF-part1 | ok
1422 | VAV0089 | VAV-0089 | 03.023 RESEARCHER OFFICE | RESEARCHER OFFICE 03.023 |  | RESEARCHER OFFICE 03.023 | confirms the register | TF-part1 | ok
1423 | VAV0090 | VAV-0090 | 03.022 RESEARCHER OFFICE | RESEARCHER OFFICE 03.022 |  | RESEARCHER OFFICE 03.022 | confirms the register | TF-part1 | ok
1424 | VAV0091 | VAV-0091 | 03.021 VISITORS CUBIDE | VISITOR'S CUBICLE 03.021 |  | VISITOR'S CUBICLE 03.021 | confirms the register | TF-part1 | ok
1425 | VAV0092 | VAV-0092 | 03.020 RESEARCHER OFFICE | RESEARCHER OFFICE 03.020 |  | RESEARCHER OFFICE 03.020 | confirms the register | TF-part1 | ok
1426 | VAV0093 | VAV-0093 | 03.019 IT MANAGERS OFFICE | IT MANAGERS'S OFFICE 03.019 |  | IT MANAGERS'S OFFICE 03.019 | confirms the register | TF-part1 | ok
1427 | VAV0094 | VAV-0094 | 03.018 VISITORS CUBIDE | VISITOR'S CUBICLE 03.018 |  | VISITOR'S CUBICLE 03.018 | confirms the register | TF-part1 | ok
1428 | VAV0095 | VAV-0095 | 03.017 RESEARCHER OFFICE | RESEARCHER OFFICE 03.017 |  | RESEARCHER OFFICE 03.017 | confirms the register | TF-part1 | ok
1440 | VAV0107 | VAV-0107 | 03.032 GENERAL OFFICE AREA | GENERAL OFFICE AREA 03.002 | GENERAL OFFICE AREA 03.032 | GENERAL OFFICE AREA 03.032 | confirms the register | TF-part2 | ok
1441 | VAV0108 | VAV-0108 | 03.032 GENERAL OFFICE AREA | GENERAL OFFICE AREA 03.002 | GENERAL OFFICE AREA 03.032 | GENERAL OFFICE AREA 03.032 | confirms the register | TF-part2 | ok
| KEF0103 | KEF-1F-0103 | 01.005 KITCHEN |  |  |  | not in the SSC controllable register | FF-part2 | ok
| TEF0101 | TEF-1F-0101 | 01.028 CORRIDOR |  |  |  | not in the SSC controllable register | FF-part2 | ok

## Basement plant
BMS tag | Room per BMS | Screen | Read confidence
CCU-B-005B | B.023 Q TEL | BF-part1 | ok
CCU-B-006B | B.023 Q TEL | BF-part1 | ok
CCU-B-006A | B.023 Q TEL | BF-part1 | check
CCU-B-0007 | B.026 MDF/SER.1 | BF-part1 | ok
CCU-B-0004 | B.017 MDF-2 | BF-part1 | ok
CCU-B-002A | B.038 SER-2 | BF-part1 | check
CCU-B-001B | B.038 SER-2 | BF-part1 | check
CCU-B-002B | B.038 SER-2 | BF-part1 | check
DX-B-0001 | B.022 SSP | BF-part1 | check
DX-B-0002 | B.022 SSP | BF-part1 | check
DX-B-0003 | B.005 UPS | BF-part2 | ok
DX-B-0004 | B.008 VENT PLANT | BF-part2 | check
DX-B-0006 | B.001 FM STORAGE | BF-part2 | ok
DX-B-0007 | B.006 SERVICE AREA | BF-part2 | ok
DX-B-0008 | B.008 VENT PLANT | BF-part2 | ok
DX-B-0009 | B.002 HV ROOM | BF-part2 | ok
DX-B-0010 | B.033 CLOSET | BF-part2 | check
KEF-1F-0103 | 01.005 KITCHEN | FF-part2 | ok
TEF-1F-0101 | 01.028 CORRIDOR | FF-part2 | ok

## Still to do
SSC screen | What is not yet allocated
BF-part1 | CCU-B-001A, CCU-B-0003, CCU-B-0008, CCU-B-005A - leaders share a path with their neighbours and cannot be told apart at this resolution
BF-part2 | DX-B-0005, GEF-B-0001
FF-part1 | FCU-0004, VAV-0037, VAV-0038, VAV-0026, VAV-0022, VAV-0011
FF-part2 | FCU-0009, VAV-0020, FCU-0006, FCU-0008, TEF-1F-0102, VAV-0023
Second Floor | VAV-0043, VAV-0044, VAV-0045, EF-RF-0001
TF-part1 | VAV-0096/0097/0098, VAV-0100/0102/0103, TEF-3F-0301, KEF-3F-0303, CCU-3F-0301, CCU-3F-0302
TF-part2 | VAV-0063..0070 top row, VAV-0073/0074/0076/0079, VAV-0084, VAV-0099, VAV-0101, VAV-0104/0105/0106, FCU-0011
not on any floor plan | CHW Pump x8, HEX x5, Generator - these need the plant/system screens