## START HERE
HQ and SSC equipment and the rooms they are in
One row per piece of equipment that is NOT an AHU, a VAV or an FCU - those three were covered by the earlier BMS screen pass and are left out here.
Two sources, side by side:
Room per BMS screen - the room the serving-area leader on the BMS floor-plan screen points at. Harvested from the earlier pass in projects/bms-room-allocation. It covers SSC only: the HQ pass recorded VAVs and FCUs and did not read the plant icons, and the HQ screen images are no longer in this session to re-read.
Room per ontology - the rec:locatedIn on the equipment entity in the delivered ontology, named by that room entity's own rdfs:label_en.
A row is filled GREEN where it needs revision, for one of three reasons, spelled out in the Why column:
1. the two sources name different rooms;
2. the ontology points at a placeholder rather than a room - entity:<Location> on HQ - or at a room entity that carries no readable name, or at nothing at all;
3. the equipment carries points but the ontology gives it no rec:locatedIn at all;
4. the class and the room do not go together - eight CRACs, which are computer-room units, are located in VVIP parking bays.
One pattern worth knowing about before you start. On SSC the four DX units DXB0001 to DXB0004 all sit in B1.005 UPS in the ontology while the screens spread them across three different rooms, and DXB0007 and DXB0008 share B1.019 FM STORAGE the same way. A block of units carrying one room where the screens disagree is the signature of a fill-down, not of a reading.
Where the Room per BMS screen column is empty there was no reading to compare against, so the row is judged on the ontology alone.

## Equipment and rooms
Building | Tag | Equipment class | Ontology entity | Ontology room entity | Room per ontology | Room per BMS screen | BMS screen | Screen reading | Needs revision | Why
HQ | CCU_B0001 | brick:CRAC | entity:HQ_CCU_B0001 | entity:HQ_B1_005_MDF_1_ROOM | B1.005 MDF 1 ROOM
HQ | CCU_B0002 | brick:CRAC | entity:HQ_CCU_B0002 | entity:HQ_B1_005_MDF_1_ROOM | B1.005 MDF 1 ROOM
HQ | CCU-B-0003A | brick:CRAC | entity:HQ_CCU_B0003A | entity:HQ_B1_106_VVIP_PARKING_6_CAR_SPOTS | B1.106 VVIP PARKING 6 CAR SPOTS | Chauffer Room B.117 | HQ/Basment Floor/BF-2 | ok | YES | the BMS screen puts it in Chauffer Room B.117 and the ontology in B1.106 VVIP PARKING 6 CAR SPOTS; the dot is in the Chauffer Room band, one wall north of VIP Parking B.106
HQ | CCU_B0003B | brick:CRAC | entity:HQ_CCU_B0003B | entity:HQ_B1_106_VVIP_PARKING_6_CAR_SPOTS | B1.106 VVIP PARKING 6 CAR SPOTS | Chauffer Room B.117
HQ | CCU_B0004A | brick:CRAC | entity:HQ_CCU_B0004A | entity:HQ_B1_106_VVIP_PARKING_6_CAR_SPOTS | B1.106 VVIP PARKING 6 CAR SPOTS | Chauffer Room B.117 | `
HQ | CCU_B0004B | brick:CRAC | entity:HQ_CCU_B0004B | entity:HQ_B1_106_VVIP_PARKING_6_CAR_SPOTS | B1.106 VVIP PARKING 6 CAR SPOTS | Chauffer Room B.117
HQ | CCU-B-0005 | brick:CRAC | entity:HQ_CCU_B0005 | entity:<Location> |  | VIP Parking B.115 | HQ/Basment Floor/BF-2 | check | YES | the ontology points at the placeholder entity:<Location> rather than a room; the BMS screen puts it in VIP Parking B.115 and the ontology in entity:<Location>; and the screen reading was itself marked as wanting a second look when it was made; four leaders converge on one dot inside VIP Parking B.115, so the room is certain and which of the four walked it is not
HQ | CCU-B-0006 | brick:CRAC | entity:HQ_CCU_B0006 | entity:HQ_B1_115_VVIP_PARKING_4_CAR_SPOTS | B1.115 VVIP PARKING 4 CAR SPOTS | VIP Parking B.115 | HQ/Basment Floor/BF-2 | check |  | four leaders converge on one dot inside VIP Parking B.115
HQ | CCU-B-0007 | brick:CRAC | entity:HQ_CCU_B0007 | entity:HQ_B1_115_VVIP_PARKING_4_CAR_SPOTS | B1.115 VVIP PARKING 4 CAR SPOTS | VIP Parking B.115 | HQ/Basment Floor/BF-2 | check |  | four leaders converge on one dot inside VIP Parking B.115
HQ | CCU-B-0008 | brick:CRAC | entity:HQ_CCU_B0008 | entity:HQ_B1_115_VVIP_PARKING_4_CAR_SPOTS | B1.115 VVIP PARKING 4 CAR SPOTS | VIP Parking B.115 | HQ/Basment Floor/BF-2 | check |  | four leaders converge on one dot inside VIP Parking B.115
HQ | CCU_B0009 | brick:CRAC | entity:HQ_CCU_B0009 | entity:HQ_B1_115_VVIP_PARKING_4_CAR_SPOTS | B1.115 VVIP PARKING 4 CAR SPOTS | CBS ROOM B.023
HQ | CHW_CHWP01 | brick:Chilled_Water_Booster_Pump | entity:HQ_CHW_CHWP01 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | CHW_CHWP02 | brick:Chilled_Water_Booster_Pump | entity:HQ_CHW_CHWP02 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | CHW_CHWP03 | brick:Chilled_Water_Booster_Pump | entity:HQ_CHW_CHWP03 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | CHW_CHWP04 | brick:Chilled_Water_Booster_Pump | entity:HQ_CHW_CHWP04 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | HEX | brick:Heat_Exchanger | entity:HQ_HEX | None |  |  |  |  | YES | the rec:locatedIn row carries no room at all
HQ | HEX01 | brick:Heat_Exchanger | entity:HQ_HEX01 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | HEX02 | brick:Heat_Exchanger | entity:HQ_HEX02 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | HEX03 | brick:Heat_Exchanger | entity:HQ_HEX03 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | HEX04 | brick:Heat_Exchanger | entity:HQ_HEX04 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | HEX05 | brick:Heat_Exchanger | entity:HQ_HEX05 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | CEF_CPZ1_B01 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ1_B01 | entity:<Location> |  |  | HQ/Cark Park/CPF-3 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ1_B02 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ1_B02 | entity:<Location> |  |  | HQ/Cark Park/CPF-3 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ1_B03 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ1_B03 | entity:<Location> |  |  | HQ/Cark Park/CPF-3 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ1_B04 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ1_B04 | entity:<Location> |  |  | HQ/Cark Park/CPF-3 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ1_B05 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ1_B05 | entity:<Location> |  |  | HQ/Cark Park/CPF-3 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ2_B06 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ2_B06 | entity:<Location> |  |  | HQ/Cark Park/CPF-3 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ2_B07 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ2_B07 | entity:<Location> |  |  | HQ/Cark Park/CPF-3 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ2_B08 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ2_B08 | entity:<Location> |  |  | HQ/Cark Park/CPF-4 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ2_B09 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ2_B09 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | CEF_CPZ2_B10 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ2_B10 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | CEF_CPZ3_B13 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ3_B13 | entity:<Location> |  |  | HQ/Cark Park/CPF-4 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ3_B14 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ3_B14 | entity:<Location> |  |  | HQ/Cark Park/CPF-4 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ3_B15 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ3_B15 | entity:<Location> |  |  | HQ/Cark Park/CPF-4 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ3_B19 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ3_B19 | entity:<Location> |  |  | HQ/Cark Park/CPF-4 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ4_B20 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ4_B20 | entity:<Location> |  |  | HQ/Cark Park/CPF-4 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ4_B22 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ4_B22 | entity:<Location> |  |  | HQ/Cark Park/CPF-4 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ4_B23 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ4_B23 | entity:<Location> |  |  | HQ/Cark Park/CPF-4 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ4_B24 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ4_B24 | entity:<Location> |  |  | HQ/Cark Park/CPF-4 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ5_B21 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ5_B21 | entity:<Location> |  |  | HQ/Cark Park/CPF-4 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ5_B25 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ5_B25 | entity:<Location> |  |  | HQ/Cark Park/CPF-2 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ5_B26 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ5_B26 | entity:<Location> |  |  | HQ/Cark Park/CPF-2 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ5_B27 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ5_B27 | entity:<Location> |  |  | HQ/Cark Park/CPF-2 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ7_B16 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ7_B16 | entity:<Location> |  |  | HQ/Cark Park/CPF-2 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ7_B17 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ7_B17 | entity:<Location> |  |  | HQ/Cark Park/CPF-2 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ7_B18 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ7_B18 | entity:<Location> |  |  | HQ/Cark Park/CPF-2 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ8_B11 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ8_B11 | entity:<Location> |  |  | HQ/Cark Park/CPF-1 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | CEF_CPZ8_B12 | para:Car-Parking_Exhaust-Fan | entity:HQ_CEF_CPZ8_B12 | entity:<Location> |  |  | HQ/Cark Park/CPF-1 |  | YES | the ontology points at the placeholder entity:<Location> rather than a room; the screen shows it on this car park deck, but the deck carries no room names at all - bay numbers, Exit and nothing else - so the placeholder cannot be resolved from it
HQ | DX-B-0001 | para:DXUnit | entity:HQ_DX_B0001 | entity:HQ_B1_011_HV_INTAKE | B1.011 HV INTAKE | HV Room B.011 | HQ/Basment Floor/BF-1 | ok
HQ | DX_B0002 | para:DXUnit | entity:HQ_DX_B0002 | entity:HQ_B1_011_HV_INTAKE | B1.011 HV INTAKE
HQ | DX-B-0003 | para:DXUnit | entity:HQ_DX_B0003 | entity:HQ_B1_010_TRANSFORMER_SUBSTATION | B1.010 TRANSFORMER SUBSTATION | B.012 GENERATOR | HQ/Basment Floor/BF-1 | ok | YES | the dot is in a cell the screen does not name, so the ontology room cannot be confirmed from it; the BMS screen puts it in Unlabelled cell east of Transformer Substation B.010 and the ontology in B1.010 TRANSFORMER SUBSTATION; the top band of this plan is three cells and only the first two are named; the dot is in the third
HQ | DX_B0004 | para:DXUnit | entity:HQ_DX_B0004 | entity:HQ_B1_010_TRANSFORMER_SUBSTATION | B1.010 TRANSFORMER SUBSTATION
HQ | DX_B0005 | para:DXUnit | entity:HQ_DX_B0005 | entity:HQ_B1_010_TRANSFORMER_SUBSTATION | B1.010 TRANSFORMER SUBSTATION
HQ | DX_B0006 | para:DXUnit | entity:HQ_DX_B0006 | entity:HQ_B1_026_UPS_ROOM | B1.026 UPS ROOM
HQ | DX_B0007 | para:DXUnit | entity:HQ_DX_B0007 | entity:HQ_B1_026_UPS_ROOM | B1.026 UPS ROOM
HQ | DX_B0008 | para:DXUnit | entity:HQ_DX_B0008 | entity:HQ_B1_026_UPS_ROOM | B1.026 UPS ROOM
HQ | DX_B0009 | para:DXUnit | entity:HQ_DX_B0009 | entity:HQ_B1_023_CBS_ROOM | B1.023 CBS ROOM
HQ | DX_B0010 | para:DXUnit | entity:HQ_DX_B0010 | entity:HQ_B1_023_CBS_ROOM | B1.023 CBS ROOM
HQ | DX-B-0011 | para:DXUnit | entity:HQ_DX_B0011 | entity:HQ_B1_009_MV_SWITCH_ROOM | B1.009 MV SWITCH ROOM | UPS Room B.026 | HQ/Basment Floor/BF-1 | ok | YES | the BMS screen puts it in UPS Room B.26 and the ontology in B1.009 MV SWITCH ROOM
HQ | DX_B0012 | para:DXUnit | entity:HQ_DX_B0012 | entity:HQ_B1_009_MV_SWITCH_ROOM | B1.009 MV SWITCH ROOM
HQ | DX_B0013 | para:DXUnit | entity:HQ_DX_B0013 | entity:HQ_B1_002_SECURITY_UPS_ROOM | B1.002 SECURITY UPS ROOM
HQ | DX_B0014 | para:DXUnit | entity:HQ_DX_B0014 | entity:HQ_B1_002_SECURITY_UPS_ROOM | B1.002 SECURITY UPS ROOM
HQ | DX_B0015 | para:DXUnit | entity:HQ_DX_B0015 | entity:HQ_B1_002_SECURITY_UPS_ROOM | B1.002 SECURITY UPS ROOM
HQ | DX-B-0016 | para:DXUnit | entity:HQ_DX_B0016 | entity:HQ_B1_018_PA_ROOM | B1.018 PA ROOM | AHU - 3 B.022 | HQ/Basment Floor/BF-2 | ok | YES | the BMS screen puts it in AHU - 3 B.022 and the ontology in B1.018 PA ROOM
HQ | DX_CP | para:DXUnit | entity:HQ_DX_CP | None |  |  |  |  | YES | the rec:locatedIn row carries no room at all
HQ | DX_G0001 | para:DXUnit | entity:HQ_DX_G0001 | entity:HQ_G_008_CONTROL_ROOM | G.008 CONTROL ROOM
HQ | DX_G0002 | para:DXUnit | entity:HQ_DX_G0002 | entity:HQ_G_005_EMERGENCY_CONTROL_CENTER | G.005 EMERGENCY CONTROL CENTER
HQ | DX_G0003 | para:DXUnit | entity:HQ_DX_G0003 | entity:HQ_G_103_BMS | G.103 BMS
HQ | DX_ODSB0101 | para:DXUnit | entity:HQ_DX_ODSB0101 | None |  |  |  |  | YES | the rec:locatedIn row carries no room at all
HQ | DX_ODSB0102 | para:DXUnit | entity:HQ_DX_ODSB0102 | None |  |  |  |  | YES | the rec:locatedIn row carries no room at all
HQ | DX_ODSB0201 | para:DXUnit | entity:HQ_DX_ODSB0201 | None |  |  |  |  | YES | the rec:locatedIn row carries no room at all
HQ | DX_ODSB0202 | para:DXUnit | entity:HQ_DX_ODSB0202 | None |  |  |  |  | YES | the rec:locatedIn row carries no room at all
HQ | GEF12_0005 | para:General_Exhaust-Fan | entity:HQ_GEF12_0005 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | GEF12_0006 | para:General_Exhaust-Fan | entity:HQ_GEF12_0006 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | GEF12_0008 | para:General_Exhaust-Fan | entity:HQ_GEF12_0008 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | GEF12_0009 | para:General_Exhaust-Fan | entity:HQ_GEF12_0009 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | GEFB_0007 | para:General_Exhaust-Fan | entity:HQ_GEFB_0007 | entity:<Location> |  | B.016 AHU-2 |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | GEFB_0010 | para:General_Exhaust-Fan | entity:HQ_GEFB_0010 | entity:<Location> |  | B.105 SUPPORT SPACE LOADING |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | GEFB_0011 | para:General_Exhaust-Fan | entity:HQ_GEFB_0011 | entity:<Location> |  | B.016 AHU-2 |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | GEFB_0012 | para:General_Exhaust-Fan | entity:HQ_GEFB_0012 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | GEFB_0013 | para:General_Exhaust-Fan | entity:HQ_GEFB_0013 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | GEF_BF_CP0001 | para:General_Exhaust-Fan | entity:HQ_GEF_BF_CP0001 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | GEF_BF_CP0002 | para:General_Exhaust-Fan | entity:HQ_GEF_BF_CP0002 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | TEF12_0001 | para:T_Exhaust-Fan | entity:HQ_TEF12_0001 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | TEF12_0002 | para:T_Exhaust-Fan | entity:HQ_TEF12_0002 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | TEF12_0003 | para:T_Exhaust-Fan | entity:HQ_TEF12_0003 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | TEF12_0004 | para:T_Exhaust-Fan | entity:HQ_TEF12_0004 | entity:<Location> |  |  |  |  | YES | the ontology points at the placeholder entity:<Location> rather than a room
HQ | ELEC_Gen2 | para:Generator | entity:HQ_ELEC_Gen2 | [5 empty] | YES | the ontology gives this equipment no rec:locatedIn at all
HQ | ELEC_Gen3 | para:Generator | entity:HQ_ELEC_Gen3 | [5 empty] | YES | the ontology gives this equipment no rec:locatedIn at all
HQ | JF-B-0001 | Jet fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-1 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | JF-B-0002 | Jet fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-1 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | JF-B-0003 | Jet fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-1 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | JF-B-0004 | Jet fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-1 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | JF-B-0005 | Jet fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-1 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | JF-B-0006 | Jet fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-1 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | JF-B-0007 | Jet fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-2 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | JF-B-0008 | Jet fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-2 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | JF-B-0009 | Jet fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-2 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | JF-B-0010 | Jet fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-2 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | IF-B-0001 | Induction fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-1 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | IF-B-0002 | Induction fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-1 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | IF-B-0003 | Induction fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-1 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | IF-B-0004 | Induction fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-2 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | IF-B-0005 | Induction fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-2 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | IF-B-0006 | Induction fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-2 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | IF-B-0007 | Induction fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-2 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all
HQ | IF-B-0008 | Induction fan (BMS screen only) |  |  |  |  | HQ/Cark Park/CPF-2 | ok | YES | this unit is drawn on the BMS screen and the ontology has no entity for it at all

## Summary
Building | Equipment class | Rows | Needing revision
HQ | Induction fan (BMS screen only) | 8 | 8
HQ | Jet fan (BMS screen only) | 10 | 10
HQ | brick:CRAC | 11 | 2
HQ | brick:Chilled_Water_Booster_Pump | 4 | 4
HQ | brick:Heat_Exchanger | 6 | 6
HQ | para:Car-Parking_Exhaust-Fan | 27 | 27
HQ | para:DXUnit | 24 | 8
HQ | para:General_Exhaust-Fan | 11 | 11
HQ | para:Generator | 2 | 2
HQ | para:T_Exhaust-Fan | 4 | 4
SSC | brick:CRAC | 14 | 2
SSC | brick:Chilled_Water_Booster_Pump | 4 | 0
SSC | brick:Exhaust_Fan | 7 | 7
SSC | brick:Heat_Exchanger | 5 | 0
SSC | para:DXUnit | 10 | 8
SSC | para:Generator | 1 | 0