## START HERE
HQ and SSC equipment and the rooms they are in
One row per piece of equipment that is NOT an AHU, a VAV or an FCU - those three were covered by the earlier BMS screen pass and are left out here.
Two sources, side by side:
Room per BMS screen - the room the serving-area leader on the BMS floor-plan screen points at. Harvested from the earlier pass in projects/bms-room-allocation. It covers SSC only: the HQ pass recorded VAVs and FCUs and did not read the plant icons, and the HQ screen images are no longer in this session to re-read.
Room per ontology - the rec:locatedIn on the equipment entity in the delivered ontology, named by that room entity's own rdfs:label_en.
A row is filled GREEN where it needs revision, for one of three reasons, spelled out in the Why column:
1. the two sources name different rooms;
2. the ontology points at a placeholder rather than a room - entity:<Location> on HQ - or at a room entity that carries no readable name, or at nothing at all;
3. the equipment carries points but the ontology gives it no rec:locatedIn at all;
4. the class and the room do not go together - eight CRACs, which are computer-room units, are located in VVIP parking bays.
One pattern worth knowing about before you start. On SSC the four DX units DXB0001 to DXB0004 all sit in B1.005 UPS in the ontology while the screens spread them across three different rooms, and DXB0007 and DXB0008 share B1.019 FM STORAGE the same way. A block of units carrying one room where the screens disagree is the signature of a fill-down, not of a reading.
Where the Room per BMS screen column is empty there was no reading to compare against, so the row is judged on the ontology alone.

## Equipment and rooms
Building | Tag | Equipment class | Ontology entity | Ontology room entity | Room per ontology | Room per BMS screen | BMS screen | Screen reading | Needs revision | Why
SSC | CCU3F0301 | brick:CRAC | entity:SSC_CCU3F0301 | entity:SSC_B1_038_SER-2 | B1.038 SER-2
SSC | CCU3F0302 | brick:CRAC | entity:SSC_CCU3F0302 | entity:SSC_B1_038_SER-2 | B1.038 SER-2
SSC | CCUB0001A | brick:CRAC | entity:SSC_CCUB0001A | entity:SSC_B1_038_SER-2 | B1.038 SER-2
SSC | CCU-B-001B | brick:CRAC | entity:SSC_CCUB0001B | entity:SSC_B1_038_SER-2 | B1.038 SER-2 | B.038 SER-2 | BF-part1 | check
SSC | CCU-B-002A | brick:CRAC | entity:SSC_CCUB0002A | entity:SSC_B1_038_SER-2 | B1.038 SER-2 | B.038 SER-2 | BF-part1 | check
SSC | CCU-B-002B | brick:CRAC | entity:SSC_CCUB0002B | entity:SSC_B1_038_SER-2 | B1.038 SER-2 | B.038 SER-2 | BF-part1 | check
SSC | CCUB0003 | brick:CRAC | entity:SSC_CCUB0003 | entity:SSC_B1_023_Q_TEL | B1.023 QTEL
SSC | CCU-B-0004 | brick:CRAC | entity:SSC_CCUB0004 | entity:SSC_B1_023_Q_TEL | B1.023 QTEL | B.017 MDF-2 | BF-part1 | ok | YES | the BMS screen puts it in B.017 MDF-2 and the ontology in B1.023 QTEL
SSC | CCUB0005A | brick:CRAC | entity:SSC_CCUB0005A | entity:SSC_B1_023_Q_TEL | B1.023 QTEL
SSC | CCU-B-005B | brick:CRAC | entity:SSC_CCUB0005B | entity:SSC_B1_023_Q_TEL | B1.023 QTEL | B.023 Q TEL | BF-part1 | ok
SSC | CCU-B-006A | brick:CRAC | entity:SSC_CCUB0006A | entity:SSC_B1_023_Q_TEL | B1.023 QTEL | B.023 Q TEL | BF-part1 | check
SSC | CCU-B-006B | brick:CRAC | entity:SSC_CCUB0006B | entity:SSC_B1_023_Q_TEL | B1.023 QTEL | B.023 Q TEL | BF-part1 | ok
SSC | CCU-B-0007 | brick:CRAC | entity:SSC_CCUB0007 | entity:SSC_B1_017_MDF-2 | B1.017 MDF-2 | B.026 MDF-SER1 | BF-part1 | ok | YES | the BMS screen puts it in B.026 MDF/SER.1 and the ontology in B1.017 MDF-2
SSC | CCUB0008 | brick:CRAC | entity:SSC_CCUB0008 | entity:SSC_B1_017_MDF-2 | B1.017 MDF-2
SSC | CHW_CHWP01 | brick:Chilled_Water_Booster_Pump | entity:SSC_CHW_CHWP01 | entity:SSC_B1_014_VENT_PLANT | B1.014 VENT PLANT
SSC | CHW_CHWP02 | brick:Chilled_Water_Booster_Pump | entity:SSC_CHW_CHWP02 | entity:SSC_B1_014_VENT_PLANT | B1.014 VENT PLANT
SSC | CHW_CHWP03 | brick:Chilled_Water_Booster_Pump | entity:SSC_CHW_CHWP03 | entity:SSC_B1_014_VENT_PLANT | B1.014 VENT PLANT
SSC | CHW_CHWP04 | brick:Chilled_Water_Booster_Pump | entity:SSC_CHW_CHWP04 | entity:SSC_B1_014_VENT_PLANT | B1.014 VENT PLANT
SSC | GEFB0001 | brick:Exhaust_Fan | entity:SSC_GEFB0001 | entity:Level7_Office0367 |  | B.008 VENT PLANT |  |  | YES | the room entity entity:Level7_Office0367 carries no rdfs:label_en, so it has no readable name
SSC | KEF-1F-0103 | brick:Exhaust_Fan | entity:SSC_KEF0103 | entity:Level7_Office0367 |  | 01.005 KITCHEN | FF-part2 | ok | YES | the room entity entity:Level7_Office0367 carries no rdfs:label_en, so it has no readable name; the BMS screen puts it in 01.005 KITCHEN and the ontology in entity:Level7_Office0367
SSC | KEF0303 | brick:Exhaust_Fan | entity:SSC_KEF0303 | entity:Level7_Office0367 |  | 03.049 IT OFFICE |  |  | YES | the room entity entity:Level7_Office0367 carries no rdfs:label_en, so it has no readable name
SSC | TEF-1F-0101 | brick:Exhaust_Fan | entity:SSC_TEF0101 | entity:Level7_Office0367 |  | 01.028 CORRIDOR | FF-part2 | ok | YES | the room entity entity:Level7_Office0367 carries no rdfs:label_en, so it has no readable name; the BMS screen puts it in 01.028 CORRIDOR and the ontology in entity:Level7_Office0367
SSC | TEF0102 | brick:Exhaust_Fan | entity:SSC_TEF0102 | entity:Level7_Office0367 |  | 01.206 CORRIDOR |  |  | YES | the room entity entity:Level7_Office0367 carries no rdfs:label_en, so it has no readable name
SSC | TEF0301 | brick:Exhaust_Fan | entity:SSC_TEF0301 | entity:Level7_Office0367 |  | 03.038 IT SERVER ROOM |  |  | YES | the room entity entity:Level7_Office0367 carries no rdfs:label_en, so it has no readable name
SSC | TEF0302 | brick:Exhaust_Fan | entity:SSC_TEF0302 | entity:Level7_Office0367 |  | 03.045 JANITOR'S CLOSET |  |  | YES | the room entity entity:Level7_Office0367 carries no rdfs:label_en, so it has no readable name
SSC | CHW_HE01 | brick:Heat_Exchanger | entity:SSC_CHW_HE01 | entity:SSC_B1_014_VENT_PLANT | B1.014 VENT PLANT
SSC | CHW_HE02 | brick:Heat_Exchanger | entity:SSC_CHW_HE02 | entity:SSC_B1_014_VENT_PLANT | B1.014 VENT PLANT
SSC | CHW_HE03 | brick:Heat_Exchanger | entity:SSC_CHW_HE03 | entity:SSC_B1_014_VENT_PLANT | B1.014 VENT PLANT
SSC | CHW_HE04 | brick:Heat_Exchanger | entity:SSC_CHW_HE04 | entity:SSC_B1_014_VENT_PLANT | B1.014 VENT PLANT
SSC | CHW_HE05 | brick:Heat_Exchanger | entity:SSC_CHW_HE05 | entity:SSC_B1_014_VENT_PLANT | B1.014 VENT PLANT
SSC | DX-B-0001 | para:DXUnit | entity:SSC_DXB0001 | entity:SSC_B1_005_UPS | B1.005 UPS | B.022 SSP | BF-part1 | check | YES | the BMS screen puts it in B.022 SSP and the ontology in B1.005 UPS; and the screen reading was itself marked as wanting a second look when it was made
SSC | DX-B-0002 | para:DXUnit | entity:SSC_DXB0002 | entity:SSC_B1_005_UPS | B1.005 UPS | B.022 SSP | BF-part1 | check | YES | the BMS screen puts it in B.022 SSP and the ontology in B1.005 UPS; and the screen reading was itself marked as wanting a second look when it was made
SSC | DX-B-0003 | para:DXUnit | entity:SSC_DXB0003 | entity:SSC_B1_005_UPS | B1.005 UPS | B.005 UPS | BF-part2 | ok
SSC | DX-B-0004 | para:DXUnit | entity:SSC_DXB0004 | entity:SSC_B1_005_UPS | B1.005 UPS | B.005 UPS | BF-part2 | ok
SSC | DXB0005 | para:DXUnit | entity:SSC_DXB0005 | entity:SSC_B1_004_MV_SWITCH_ROOM | B1.004 MV SWITCH ROOM | B.004 MV SWITCH ROOM
SSC | DX-B-0006 | para:DXUnit | entity:SSC_DXB0006 | entity:SSC_B1_004_MV_SWITCH_ROOM | B1.004 MV SWITCH ROOM | B.033 CLOSET | BF-part2 | ok | YES | the BMS screen puts it in B.001 FM STORAGE and the ontology in B1.004 MV SWITCH ROOM
SSC | DX-B-0007 | para:DXUnit | entity:SSC_DXB0007 | entity:SSC_B1_019_FM_STORAGE | B1.019 FM STORAGE | B.003 TRANSFORMER | BF-part2 | ok | YES | the BMS screen puts it in B.006 SERVICE AREA and the ontology in B1.019 FM STORAGE
SSC | DX-B-0008 | para:DXUnit | entity:SSC_DXB0008 | entity:SSC_B1_019_FM_STORAGE | B1.019 FM STORAGE | B.003 TRANSFORMER | BF-part2 | ok | YES | the BMS screen puts it in B.008 VENT PLANT and the ontology in B1.019 FM STORAGE
SSC | DX-B-0009 | para:DXUnit | entity:SSC_DXB0009 | entity:SSC_B1_020_FM_STORAGE | B1.020 FM STORAGE | B.002 HV ROOM | BF-part2 | ok | YES | the BMS screen puts it in B.002 HV ROOM and the ontology in B1.020 FM STORAGE
SSC | DX-B-0010 | para:DXUnit | entity:SSC_DXB0010 | entity:SSC_B1_021_FM_STORAGE | B1.021 FM STORAGE | B.002 HV ROOM | BF-part2 | check | YES | the BMS screen puts it in B.033 CLOSET and the ontology in B1.021 FM STORAGE; and the screen reading was itself marked as wanting a second look when it was made
SSC | MV_Generator | para:Generator | entity:SSC_MV_Generator | entity:SSC_B1_012_GENERATOR | B1.012 GENERATOR

## Summary
Building | Equipment class | Rows | Needing revision
HQ | brick:CRAC | 11 | 9
HQ | brick:Chilled_Water_Booster_Pump | 4 | 4
HQ | brick:Heat_Exchanger | 6 | 6
HQ | para:Car-Parking_Exhaust-Fan | 27 | 27
HQ | para:DXUnit | 24 | 5
HQ | para:General_Exhaust-Fan | 11 | 11
HQ | para:Generator | 2 | 2
HQ | para:T_Exhaust-Fan | 4 | 4
SSC | brick:CRAC | 14 | 2
SSC | brick:Chilled_Water_Booster_Pump | 4 | 0
SSC | brick:Exhaust_Fan | 7 | 7
SSC | brick:Heat_Exchanger | 5 | 0
SSC | para:DXUnit | 10 | 8
SSC | para:Generator | 1 | 0