## SSC
ID | Date | Category | Layer | Entity / Scope | What the source says | What we did | Why / basis | Rows affected
(no entries yet)

## HQ
ID | Date | Category | Layer | Entity / Scope | What the source says | What we did | Why / basis | Rows affected
(no entries yet)

## QNL
ID | Date | Category | Layer | Entity / Scope | What the source says | What we did | Why / basis | Rows affected
QNL-007 | 2026-08-24 | Spelling | Rooms | 24 room names | Hand-typed schedule carries misspellings (CARRLES, VENTILATON, GREEM) | Corrected whole tokens only, on the name segment | Each settled against a sibling room that spells it correctly - never guessed. Names reach users through rdfs:label_en. | 24
QNL-008 | 2026-08-24 | Spelling | Rooms | 11 room names | Run-together words (REST_ROOMMEN, ABLUTIONMEN, INDIVISTUDY) | Restored the separator only; wording unchanged | Every sibling room writes the two tokens apart. No abbreviation was expanded. | 11
QNL-009 | 2026-08-24 | Spelling | Rooms | INDIVI_STUDY_ROOM (6 rooms), B046_ITT | INDIVI probably means INDIVIDUAL; ITT sits in the room-number segment | Left as-is | Expanding an abbreviation is a rewrite, not a correction; ITT may be a drawing code and a join key. Client's call. | 7
QNL-010 | 2026-08-24 | Spelling | Equipment | All asset tags | Register tags may contain errors | Left completely untouched | Asset tags are the BMS join key. Only room names were corrected. | 0
QNL-011 | 2026-08-24 | Units | Points | 20 brick:Electric_Power_Sensor points | IO list gives '%' on 20 of its 24 .kW tags, against a description reading 'Power' | Overrode to unit:KiloW | A power sensor cannot read a percentage. Dar Cairo uses unit:KiloW on all 559 of its Electric_Power_Sensor points. | 20
QNL-012 | 2026-08-24 | Units | Points | 22 AHU air-flow points | IO list gives 'm/s' (a velocity) on Supply_/Return_Air_Flow_Sensor | Overrode to unit:L-PER-SEC | Dar Cairo uses L-PER-SEC on all 51 air-flow sensors, SSC on all 118; unit:M-PER-SEC occurs 0 times in either model, and no point in the IO list is named 'velocity'. | 22
QNL-013 | 2026-08-24 | Units | Points | 30 analog rows in the Selected sheet | Humidity and temperature units transposed (AvgSpcHumd as degC, AvgSpcTemp as %rH) | Took units from the IO list instead | The IO list has both right. The Selected sheet is not used as the unit authority anywhere. | 30
QNL-014 | 2026-08-24 | Units | Points | 64 brick:Relative_Humidity_Sensor points | Dar Cairo uses unit:PERCENT on this class | Used unit:PERCENT_RH | Dar Cairo contradicts itself - its Return_ and Supply_Air_Humidity_Sensor both use PERCENT_RH. SSC and the IO list agree with PERCENT_RH. | 64
QNL-015 | 2026-08-24 | Units | Points | 22 brick:Speed_Sensor points | SSC uses unit:RPM on this class | Used unit:PERCENT | SSC's are Motor_Speed_Fbk (shaft RPM); QNL's are fan VFD SpeedFbk in % of max. Dar Cairo's Speed_Command is PERCENT on all 88. | 22
QNL-016 | 2026-08-24 | Units | Points | 295 brick:Air_Flow_Sensor points | Dar Cairo uses unit:UNITLESS on this class | Used unit:L-PER-SEC | A flow is not dimensionless - Dar Cairo's value is a missing unit, not a convention. Its own specific flow classes all use L-PER-SEC. | 295
QNL-017 | 2026-08-24 | Units | Points | 14 brick:Damper_Position_Command points | Dar Cairo is mixed: UNITLESS x28, PERCENT x1 | Used unit:PERCENT | Dar Cairo's unitless ones read as binary open/close. Its Speed_Command is PERCENT on all 88 and Damper_Position_Sensor PERCENT on all 74. | 14
QNL-018 | 2026-08-24 | Class | Points | 4 CHW temperature point signatures | brick:Chilled_Water_Supply/Return_Temperature_Sensor are deprecated in Brick 1.4 | Kept the deprecated Dar Cairo class; recorded the replacement in the ledger note | Client directed - the class is the established join key. Each raises an expected W-TYP-4 naming the entering/leaving replacement. | 64
QNL-019 | 2026-08-24 | Class | Points | 22 fan trip-alarm points | SSC types its own _TripAlm points as the bare brick:Alarm | Coined para:Trip_Alarm (subClassOf brick:Alarm), defined in row 3 | brick:Alarm is reserved for a literal general/summary alarm; SSC's bare typing makes trips indistinguishable from every other alarm. | 22
QNL-021 | 2026-08-24 | Location | Equipment | entity:QNL_CAV_1F_S15_001, entity:QNL_VAV_B_S13_005 | Named in the Selected points sheet but absent from the asset register - no room, no Fed By | Modelled both units and their 6 points WITHOUT rec:locatedIn, rec:feeds or rec:isFedBy | Rule 1: model the asset and its datapoints, assert nothing about position. Inventing a location would read as surveyed fact. Raises 2 E-FEED-1 and 2 W-GR-2, accepted here. | 10
QNL-022 | 2026-08-24 | Scope | Points | entity:QNL_VAV_1F_S15_039S | In the asset register and the historian, but the Selected sheet lists no points for it | Added the 3 points its 245 siblings carry, taken from the historian | Rule 1: points exist in the historian, so they are modelled. The family's own selected signature decides which, so the unit matches its siblings. Its other 5 historian points are not selected on any sibling either. | 6
QNL-023 | 2026-08-27 | Location | Equipment | entity:QNL_CCU_8081..8086 (6), entity:QNL_CHWPU_P02 | In the historian and Selected sheet but absent from the asset register - no room, no Fed By | Modelled each as its class (brick:CRAC / brick:Chilled_Water_Booster_Pump) with a label, an IFC reference and its datapoints, but no rec:locatedIn or rec:isFedBy. CHWPU_P02 feeds entity:QNL_CHWS-MAIN-LOOP (a pump feeds the loop by function); the CCUs' room-feeds are left unasserted. | Same basis as QNL-021: model the asset and its datapoints, assert nothing about position that the register does not give. Raises 6 E-FEED-1 and 7 W-GR-2 (with QNL_VAV_B_S13_005), accepted here. | 56
QNL-024 | 2026-08-27 | Scope | Points | 78 system/aggregate telemetry tags (CHW plant instrumentation 21, electrical metering 24, DX group/staging 11, CCU room sensors 10, misc 12) | In the historian and Selected sheet under a family prefix, but each is a single building- or system-level measurement, not an equipment unit (e.g. CHW_BldgAvgSupTemp, ELEC_MFM_MVP1, DX_RP21 staging, CCU_AVServerRmHumd) | NOT modelled this pass | These are points that need a parent entity - the chilled-water loop/system, the electrical system, or specific units - which the sources do not settle. Modelling them as standalone equipment would invent units that do not exist. Held for the client to direct where they attach. | 0

## RDC
ID | Date | Category | Layer | Entity / Scope | What the source says | What we did | Why / basis | Rows affected
(no entries yet)